## For Report - Comparison
Gas CT Recommend
CONE Area |  | Total Plant Capital Cost | Net Summer ICAP | Overnight Cost | Fixed O&M | After-Tax | Levelized Gross CONE |  | PJM 2014/15
[6 empty] | WACC | Level Real | Level Nominal | CT CONE
|  | ($M) | (MW) | ($/kW) | ($/kW-y) | (%) | ($/kW-y) | ($/kW-y) | ($/kW-y)
Brattle 2011 Estimate | [8 empty] | Escalated at CPI
June 1, 2015 Online Date (2015$) | [8 empty] | for 1 Year
1 | Eastern MAAC | 308.2522 | 389.608 | 791.1855 | 15.7338 | 8.468% | 111.9506 | 133.9955 | 142.1118
2 | Southwest MAAC | 281.5224 | 389.608 | 722.5786 | 15.8022 | 8.486% | 103.3876 | 123.7307 | 131.4313
3 | Rest of RTO | 287.2595 | 389.608 | 737.3039 | 15.1744 | 8.456% | 103.1404 | 123.4608 | 134.9727
4 | Western MAAC | 299.3021 | 389.608 | 768.2134 | 15.1086 | 8.444% | 108.6458 | 130.0615 | 131.4313
5 | Dominion | 254.721 | 392.008 | 649.7852 | 14.6586 | 8.541% | 92.8206 | 111.0425 | 131.5484
Power Project Management, LLC 2008 Update
June 1, 2008 Online Date (Escalated at CPI from 2008$ to 2015$)
1 | Eastern MAAC | 350.2643 | 336.066 | 1042.2485 | 17.2114 | 8.07% | n/a | 154.3872 | n/a
2 | Southwest MAAC | 322.0909 | 336.066 | 958.4156 | 17.5211 | 8.087% | n/a | 142.7843 | n/a
3 | Rest of RTO | 332.4995 | 336.066 | 989.3875 | 15.2827 | 8.109% | n/a | 146.0872 | n/a
Gas CC Recommend
CONE Area |  | Total Plant Capital Cost | Net Summer ICAP | Overnight Cost | Fixed O&M | After-Tax | Levelized Gross CONE |  | PJM 2014/15
[6 empty] | WACC | Level Real | Level Nominal | CC CONE
|  | ($M) | (MW) | ($/kW) | ($/kW-y) | (%) | ($/kW-y) | ($/kW-y) | ($/kW-y)
Brattle 2011 Estimate | [8 empty] | Escalated at CPI
June 1, 2015 Online Date (2015$) | [8 empty] | for 1 Year
1 | Eastern MAAC | 621.4333 | 655.638 | 947.8299 | 16.652 | 0.084681 | 140.5151 | 168.1848 | 179.6312
2 | Southwest MAAC | 537.3812 | 655.638 | 819.631 | 16.5826 | 0.084864 | 123.3174 | 147.582 | 158.7417
3 | Rest of RTO | 599.028 | 655.638 | 913.6566 | 16.0214 | 0.084559 | 135.4713 | 162.1614 | 168.4844
4 | Western MAAC | 597.4203 | 655.638 | 911.2045 | 15.7916 | 0.08444 | 135.1632 | 161.8059 | 158.7417
5 | Dominion | 532.9029 | 655.638 | 812.8005 | 15.4483 | 0.085413 | 120.2345 | 143.8382 | 158.7417
Pasteris 2011 Update
June 1, 2014 Online Date (Escalated at CPI from 2014$ to 2015$)
1 | Eastern MAAC | 710.9308 | 600.9 | 1183.11 | 18.5247 | 8.07% | n/a | 179.6312 | n/a
2 | Southwest MAAC | 618.6562 | 600.9 | 1029.5493 | 18.8215 | 8.087% | n/a | 158.7417 | n/a
3 | Rest of RTO | 677.9914 | 600.9 | 1128.2932 | 16.8821 | 8.109% | n/a | 168.4844 | n/a
Additional Options
Cone Area |  | Total Plant Capital Cost | Net Summer ICAP | Overnight Cost | Fixed O&M | After-Tax | Levelized Gross CONE
[6 empty] | WACC | Level Real | Level Nominal
|  | ($M) | (MW) | ($/kW) | ($/kW-y) | (%) | ($/kW-y) | ($/kW-y)
Gas CT - No SCR - Dual Fuel
1 | Eastern MAAC | 281.0672 | 392.008 | 716.9935 | 15.6375 | 8.468% | 102.9238 | 123.1911
2 | Southwest MAAC | 258.1083 | 392.008 | 658.4261 | 15.7106 | 8.486% | 95.5866 | 114.3946
3 | Rest of RTO | 279.1573 | 392.008 | 712.1214 | 15.0815 | 8.456% | 101.683 | 121.7162
4 | Western MAAC | 272.3761 | 392.008 | 694.8228 | 15.017 | 8.444% | 99.6873 | 119.3372
Gas CT - With SCR - Dual Fuel
3 | Rest of RTO | 306.2447 | 389.608 | 786.0329 | 15.1744 | 8.456% | 110.6874 | 132.4946
5 | Dominion | 278.9963 | 389.608 | 716.0949 | 14.7489 | 8.541% | 100.8225 | 120.6153
Gas CT - No SCR - Single Fuel
3 | Rest of RTO | 260.6341 | 392.008 | 664.8693 | 15.0815 | 8.456% | 94.5442 | 113.1709
Gas CC - With SCR - Dual Fuel
3 | Rest of RTO | 616.6773 | 655.638 | 940.5759 | 16.0214 | 8.456% | 138.9443 | 166.3185

## Levelization Summary
Levelized Revenue Requirements
| Cone Area |  | Tech | Fuel | SCR | Level-Real | Level-Nominal | Total Capital Costs
|  |  | (CT/CC) | (SF/DF) | (Y/N) | ($/kW-yr) | ($/kW-yr) | ($m)
1_CT_DF_Y | 1 | Middlesex, NJ | CT | DF | Y | 111.9506 | 133.9955 | 308.2522
2_CT_DF_Y | 2 | Charles County, MD | CT | DF | Y | 103.3876 | 123.7307 | 281.5224
3_CT_SF_Y | 3 | Will, IL | CT | SF | Y | 103.1404 | 123.4608 | 287.2595
4_CT_DF_Y | 4 | Northampton, PA | CT | DF | Y | 108.6458 | 130.0615 | 299.3021
5_CT_DF_N | 5 | Fauquier, VA | CT | DF | N | 92.8206 | 111.0425 | 254.721
Levelized Revenue Requirements
| Cone Area |  | Tech | Fuel | SCR | Level-Real | Level-Nominal | Total Capital Costs
|  |  | (CT/CC) | (SF/DF) | (Y/N) | ($/kW-yr) | ($/kW-yr) | ($m)
1_CC_DF_Y | 1 | Middlesex, NJ | CC | DF | Y | 140.5151 | 168.1848 | 621.4333
2_CC_DF_Y | 2 | Charles County, MD | CC | DF | Y | 123.3174 | 147.582 | 537.3812
3_CC_SF_Y | 3 | Will, IL | CC | SF | Y | 135.4713 | 162.1614 | 599.028
4_CC_DF_Y | 4 | Northampton, PA | CC | DF | Y | 135.1632 | 161.8059 | 597.4203
5_CC_DF_Y | 5 | Fauquier, VA | CC | DF | Y | 120.2345 | 143.8382 | 532.9029
|  |  | Tech | Fuel | SCR
| Gas CT - No SCR - Dual Fuel |  | (CT/CC) | (SF/DF) | (Y/N)
1_CT_DF_N | 1 | Middlesex, NJ | CT | DF | N | 102.9238 | 123.1911 | 281.0672
2_CT_DF_N | 2 | Charles County, MD | CT | DF | N | 95.5866 | 114.3946 | 258.1083
3_CT_DF_N | 3 | Will, IL | CT | DF | N | 101.683 | 121.7162 | 279.1573
4_CT_DF_N | 4 | Northampton, PA | CT | DF | N | 99.6873 | 119.3372 | 272.3761
___
Gas CT - With SCR - Dual Fuel___ | Gas CT - With SCR - Dual Fuel
3_CT_DF_Y | 3 | Will, IL | CT | DF | Y | 110.6874 | 132.4946 | 306.2447
5_CT_DF_Y | 5 | Fauquier, VA | CT | DF | Y | 100.8225 | 120.6153 | 278.9963
___
Gas CT - No SCR - Single Fuel___ | Gas CT - No SCR - Single Fuel
3_CT_SF_N | 3 | Will, IL | CT | SF | N | 94.5442 | 113.1709 | 260.6341
___
Gas CC - With SCR - Dual Fuel___ | Gas CC - With SCR - Dual Fuel
3_CC_DF_Y | 3 | Will, IL | CC | DF | Y | 138.9443 | 166.3185 | 616.6773
Levelized Revenue Requirements
| Cone Area |  | Tech | Fuel | SCR | Level-Real | Level-Nominal | Total Capital Costs
|  |  | (CT/CC) | (SF/DF) | (Y/N) | ($/kW-yr) | ($/kW-yr) | ($m)
1_CT_DF_N | 1 | Middlesex, NJ | CT | DF | N | 102.9238 | 123.1911 | 281.0672
2_CT_DF_N | 2 | Charles County, MD | CT | DF | N | 95.5866 | 114.3946 | 258.1083
3_CT_DF_N | 3 | Will, IL | CT | DF | N | 101.683 | 121.7162 | 279.1573
4_CT_DF_N | 4 | Northampton, PA | CT | DF | N | 99.6873 | 119.3372 | 272.3761
5_CT_DF_N | 5 | Fauquier, VA | CT | DF | N | 92.8206 | 111.0425 | 254.721
1_CT_DF_Y | 1 | Middlesex, NJ | CT | DF | Y | 111.9506 | 133.9955 | 308.2522
2_CT_DF_Y | 2 | Charles County, MD | CT | DF | Y | 103.3876 | 123.7307 | 281.5224
3_CT_DF_Y | 3 | Will, IL | CT | DF | Y | 110.6874 | 132.4946 | 306.2447
4_CT_DF_Y | 4 | Northampton, PA | CT | DF | Y | 108.6458 | 130.0615 | 299.3021
5_CT_DF_Y | 5 | Fauquier, VA | CT | DF | Y | 100.8225 | 120.6153 | 278.9963
1_CC_DF_Y | 1 | Middlesex, NJ | CC | DF | Y | 140.5151 | 168.1848 | 621.4333
2_CC_DF_Y | 2 | Charles County, MD | CC | DF | Y | 123.3174 | 147.582 | 537.3812
3_CC_DF_Y | 3 | Will, IL | CC | DF | Y | 138.9443 | 166.3185 | 616.6773
4_CC_DF_Y | 4 | Northampton, PA | CC | DF | Y | 135.1632 | 161.8059 | 597.4203
5_CC_DF_Y | 5 | Fauquier, VA | CC | DF | Y | 120.2345 | 143.8382 | 532.9029
___
3_CT_SF_N | 3 | Will, IL | CT | SF | N | 94.5442 | 113.1709 | 260.6341
3_CT_SF_Y | 3 | Will, IL | CT | SF | Y | 103.1404 | 123.4608 | 287.2595
3_CC_SF_Y | 3 | Will, IL | CC | SF | Y | 135.4713 | 162.1614 | 599.028

## CONE_Calculations
Assumptions
1 | Select Options
| Select Technology >>> | Combined Cycle | Single Cycle | Combined Cycle
| Select Region >>> | Area 3 | Area 1 | Area 2 | Area 3 | Area 4 | Area 5
| Select Single/Dual Fuel (Area 3 Only) >>> | Single | Dual | Single
| Select SCR >>> | Include SCR | Include SCR
| Levelization Method >>> | Level-Nominal | 0% | Level-Real | Level-Nominal
| Levelized Revenue Requirements ($/kW-yr) | 162.1614
| Levelized Revenue Requirements ($/MW-day) | 444.2777
| Plant Capacity (MW) | 655.638 | CC_SF_Y
| Installed Cost ($m) | 681.9996
| Depreciable Cost ($m) | 631.1942
| Installed Cost ($/kW) | 1040.2075
| Depreciable Cost ($/kW) | 962.7176
2 | Financial Assumptions
| Economic Life (years) | 20
| Debt Fraction (%) | 50%
| Debt Rate (%) | 7.5%
| Equity Rate (%) | 12.5%
| Federal Tax Rate (%) | 35%
| State Tax Rate (%) | 9.5%
| Total Income Tax Rate (%) | 41.17%
| Tax Depreciation Schedule | 20yr MACRS | 15yr MACRS | 20yr MACRS
| Annual Inflation Rate (%) | 2.5%
| ATWACC Nominal (%) | 8.456%
| ATWACC Real (%) | 5.811%
| Interest During Construction (%) | 7.5%
| Construction Debt Fraction (%) | 50%
Calculations
Note: All dollar numbers are in nominal $.
|  | (1+ATWACC)/(1+Price_Growth)-1 = | 8.456%
|  | Present Value | First Year Revenue Req. | First Year Revenue Req.
|  | EOY 0 | MOY 1 | MOY 1
|  | ($m) | ($m/yr) | ($/kW-yr)
| (+) Investment Costs | 681.9996 | 117.2618 | 178.8514
| (+) Operating Costs | 73.1296 | 12.5738 | 19.1779
| (-) Depreciation Tax Shield | -136.7722 | -23.5164 | -35.8679
| Total | 618.3569 | 106.3191 | 162.1614
13.75%
Summary of Cash Flows
| Project Year | EOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
| Revenue Requirement ($/kW-yr) |  | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 162.1614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Revenue Requirement ($m) |  | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 106.3191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M ($m) |  | 10.5043 | 10.7669 | 11.036 | 11.3119 | 11.5947 | 11.8846 | 12.1817 | 12.4863 | 12.7984 | 13.1184 | 13.4463 | 13.7825 | 14.1271 | 14.4802 | 14.8422 | 15.2133 | 15.5936 | 15.9835 | 16.3831 | 16.7926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Costs ($m) |  | 10.5043 | 10.7669 | 11.036 | 11.3119 | 11.5947 | 11.8846 | 12.1817 | 12.4863 | 12.7984 | 13.1184 | 13.4463 | 13.7825 | 14.1271 | 14.4802 | 14.8422 | 15.2133 | 15.5936 | 15.9835 | 16.3831 | 16.7926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Depreciation (%) |  | 6.563% | 7% | 6.482% | 5.996% | 5.546% | 5.13% | 4.746% | 4.459% | 4.459% | 4.459% | 4.459% | 4.46% | 4.459% | 4.46% | 4.459% | 4.46% | 4.459% | 4.46% | 4.459% | 4.46% | 0.565% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Tax Depreciation ($m) |  | 41.4253 | 44.1836 | 40.914 | 37.8464 | 35.006 | 32.3803 | 29.9565 | 28.145 | 28.145 | 28.145 | 28.145 | 28.1513 | 28.145 | 28.1513 | 28.145 | 28.1513 | 28.145 | 28.1513 | 28.145 | 28.1513 | 3.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Income Tax ($m) ALL-EQUITY |  | 22.3949 | 21.1511 | 22.3865 | 23.536 | 24.589 | 25.5509 | 26.4265 | 27.047 | 26.9185 | 26.7867 | 26.6517 | 26.5107 | 26.3714 | 26.2234 | 26.0769 | 25.9216 | 25.7676 | 25.6044 | 25.4425 | 25.2713 | -1.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All-Equity Cash Flow ($m) | -681.9996 | 73.42 | 74.4012 | 72.8966 | 71.4713 | 70.1354 | 68.8837 | 67.7109 | 66.7859 | 66.6023 | 66.414 | 66.2211 | 66.026 | 65.8207 | 65.6155 | 65.4 | 65.1843 | 64.958 | 64.7312 | 64.4936 | 64.2553 | 1.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at ATWACC ($m) | 0: 681.9996
TRUE
| Interest Payments ($m) |  | 12.5563 | 23.8744 | 23.1032 | 22.3231 | 21.5306 | 20.7211 | 19.8902 | 19.0329 | 18.1378 | 17.174 | 16.1357 | 15.0168 | 13.8106 | 12.5102 | 11.1075 | 9.5942 | 7.9611 | 6.1983 | 4.295 | 2.2397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Taxable Income ($m) |  | 41.8333 | 27.4943 | 31.2659 | 34.8377 | 38.1878 | 41.3332 | 44.2908 | 46.655 | 47.2379 | 47.8818 | 48.5922 | 49.3686 | 50.2365 | 51.1775 | 52.2245 | 53.3604 | 54.6195 | 55.9861 | 57.4961 | 59.1356 | -3.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Income Tax ($m) |  | 17.2249 | 11.3208 | 12.8738 | 14.3444 | 15.7238 | 17.0189 | 18.2367 | 19.2102 | 19.4502 | 19.7154 | 20.0078 | 20.3275 | 20.6849 | 21.0723 | 21.5034 | 21.9711 | 22.4896 | 23.0523 | 23.674 | 24.3491 | -1.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE Payments ($m) |  | 20.6851 | 39.7907 | 38.5053 | 37.2052 | 35.8843 | 34.5352 | 33.1503 | 31.7215 | 30.2297 | 28.6233 | 26.8928 | 25.028 | 23.0177 | 20.8503 | 18.5124 | 15.9903 | 13.2684 | 10.3305 | 7.1584 | 3.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discretionary Cash ($m) |  | 45.3486 | 20.5664 | 20.8009 | 21.1344 | 21.5857 | 22.1593 | 22.8603 | 23.8683 | 25.7029 | 27.6882 | 29.8365 | 32.1643 | 34.6788 | 37.4061 | 40.3536 | 43.5502 | 47.0064 | 50.7546 | 54.8087 | 59.2049 | 1.4684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Debt Balance ($m) |  | 340.9998 | 318.3255 | 308.0423 | 297.6418 | 287.0746 | 276.2817 | 265.2021 | 253.772 | 241.8378 | 228.9864 | 215.1423 | 200.224 | 184.1418 | 166.8024 | 148.0994 | 127.9226 | 106.1475 | 82.6442 | 57.267 | 29.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interest Payments ($m) |  | 12.5563 | 23.8744 | 23.1032 | 22.3231 | 21.5306 | 20.7211 | 19.8902 | 19.0329 | 18.1378 | 17.174 | 16.1357 | 15.0168 | 13.8106 | 12.5102 | 11.1075 | 9.5942 | 7.9611 | 6.1983 | 4.295 | 2.2397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Principal Repayment ($m) | -340.9998 | 22.6743 | 10.2832 | 10.4005 | 10.5672 | 10.7928 | 11.0796 | 11.4301 | 11.9341 | 12.8515 | 13.8441 | 14.9183 | 16.0822 | 17.3394 | 18.7031 | 20.1768 | 21.7751 | 23.5032 | 25.3773 | 27.4043 | 29.6025 | 0.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Payments to Debt Holders ($m) | -340.9998 | 35.2306 | 34.1576 | 33.5036 | 32.8904 | 32.3234 | 31.8008 | 31.3203 | 30.967 | 30.9893 | 31.0181 | 31.0539 | 31.099 | 31.1501 | 31.2132 | 31.2843 | 31.3693 | 31.4643 | 31.5756 | 31.6994 | 31.8422 | 0.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at Debt Rate ($m) | 0: 341.103
TRUE
| Equity Balance ($m) |  | 340.9998 | 318.3255 | 308.0423 | 297.6418 | 287.0746 | 276.2817 | 265.2021 | 253.772 | 241.8378 | 228.9864 | 215.1423 | 200.224 | 184.1418 | 166.8024 | 148.0994 | 127.9226 | 106.1475 | 82.6442 | 57.267 | 29.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ROE Payments ($m) |  | 20.6851 | 39.7907 | 38.5053 | 37.2052 | 35.8843 | 34.5352 | 33.1503 | 31.7215 | 30.2297 | 28.6233 | 26.8928 | 25.028 | 23.0177 | 20.8503 | 18.5124 | 15.9903 | 13.2684 | 10.3305 | 7.1584 | 3.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Dividend Payments ($m) | -340.9998 | 22.6743 | 10.2832 | 10.4005 | 10.5672 | 10.7928 | 11.0796 | 11.4301 | 11.9341 | 12.8515 | 13.8441 | 14.9183 | 16.0822 | 17.3394 | 18.7031 | 20.1768 | 21.7751 | 23.5032 | 25.3773 | 27.4043 | 29.6025 | 0.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Payments to Equity Holders ($m) | -340.9998 | 43.3594 | 50.0739 | 48.9057 | 47.7724 | 46.6772 | 45.6149 | 44.5804 | 43.6556 | 43.0812 | 42.4674 | 41.811 | 41.1102 | 40.3572 | 39.5534 | 38.6892 | 37.7654 | 36.7717 | 35.7078 | 34.5627 | 33.3353 | 0.7342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at Equity Rate ($m) | 0: 341.0393
TRUE
| Debt Fraction (%) |  | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -

## Construction Costs
| Months To |  |  |  | Construction Assumptions
| Completion |  |  |  | CONE Area >>> | 3
| 39 |  |  |  | Technology >>> | CC
[5 empty] | Single Fuel (Only in Area 3) >>> | Yes | SF
[5 empty] | SCR >> | Include SCR | Y
[5 empty] | Debt Ratio >>> | 50%
[5 empty] | Interest During Construction >>> | 7.5%
[5 empty] | ATWACC >>> | 8.456%
|  |  | EPC Total Cost ($m) = |  | 467.6318
|  |  | OFE and EPC Sales Taxes Passed Through ($m) = |  | 58.5574
|  |  | Month Of Construction = |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  |  | Date = |  | 2012-04-01 | 2012-05-01 | 2012-06-01 | 2012-07-01 | 2012-08-01 | 2012-09-01 | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01 | 2013-04-01 | 2013-05-01 | 2013-06-01 | 2013-07-01 | 2013-08-01 | 2013-09-01 | 2013-10-01 | 2013-11-01 | 2013-12-01 | 2014-01-01 | 2014-02-01 | 2014-03-01 | 2014-04-01 | 2014-05-01 | 2014-06-01 | 2014-07-01 | 2014-08-01 | 2014-09-01 | 2014-10-01 | 2014-11-01 | 2014-12-01 | 2015-01-01 | 2015-02-01 | 2015-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01
|  |  | EPC Cash Flow (%) |  | 0% | 0% | 0% | 0% | 0% | 0% | 4.414% | 3.287% | 1.684% | 1.949% | 3.535% | 2.802% | 2.993% | 3.116% | 4.778% | 3.458% | 4.375% | 3.917% | 6.917% | 4.743% | 2.675% | 3.715% | 3.822% | 3.158% | 3.711% | 4.003% | 4.003% | 3.49% | 3.309% | 3.218% | 2.735% | 2.131% | 1.557% | 1.315% | 1.013% | 0.983% | 0.741% | 0.228% | 2.226% | 0%
|  |  | Owner's Cash Flow (%) |  | 0% | 31.61% | 0% | 0% | 26.22% | 15.81% | 0.03% | 0.58% | 1.86% | 0.89% | 0.91% | 1.69% | 0.99% | 0.98% | 1.06% | 1.57% | 1.11% | 1.13% | 1.15% | 2.77% | 1.59% | 0.58% | 0.57% | 0.52% | 0.61% | 0.62% | 0.59% | 0.49% | 0.54% | 0.48% | 0.43% | 0.41% | 0.26% | 0.22% | 0.19% | 0.18% | 0.15% | 0.11% | 1.08% | 0%
Depreciable?
|  |  | EPC ($m) = | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6413 | 15.3711 | 7.8749 | 9.1141 | 16.5308 | 13.103 | 13.9962 | 14.5714 | 22.3434 | 16.1707 | 20.4589 | 18.3171 | 32.3461 | 22.1798 | 12.5092 | 17.3725 | 17.8729 | 14.7678 | 17.3538 | 18.7193 | 18.7193 | 16.3204 | 15.4739 | 15.0484 | 12.7897 | 9.9652 | 7.281 | 6.1494 | 4.7371 | 4.5968 | 3.4652 | 1.0662 | 10.4095 | 0
|  |  | Owner ($m) = | 1 | 0 | 18.51 | 0 | 0 | 15.3537 | 9.2579 | 0.017567 | 0.33963 | 1.0892 | 0.52116 | 0.53287 | 0.98962 | 0.57972 | 0.57386 | 0.62071 | 0.91935 | 0.64999 | 0.6617 | 0.67341 | 1.622 | 0.93106 | 0.33963 | 0.33378 | 0.3045 | 0.3572 | 0.36306 | 0.34549 | 0.28693 | 0.31621 | 0.28108 | 0.2518 | 0.24009 | 0.15225 | 0.12883 | 0.11126 | 0.1054 | 0.087836 | 0.064413 | 0.63242 | 0
Cost | Month
($m) | Incurred |  | Additional Owner Costs
15.5 | 32 | 7 | Electric Interconnection ($m) = | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 31 | 8 | Gas Interconnection ($m) = | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.2 | 1 |  | Land ($m) = | 0 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7762 | 27 | 12 | O&M Services Mobilization Costs ($m) = | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0.23135 | 0
8 | All |  | Project Development Costs ($m) = | 1 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0.20513 | 0
1.6485 | 15 |  | Emissions Reductions Credits ($m) = | 1 | 0 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0.042268 | 0
2.5559 | 33 | 6 | Startup Fuel ($m) = | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.42598 | 0.42598 | 0.42598 | 0.42598 | 0.42598 | 0.42598 | 0
5.7587 | All |  | Financing Fees ($m) = | 1 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0.14766 | 0
17.4489 | All |  | Owner's Contingency ($m) = | 1 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0.44741 | 0
1 |  |  | Depreciable Asset Total ($m) = |  | 0.80019 | 19.3524 | 0.84246 | 0.84246 | 16.1962 | 10.1004 | 21.5013 | 16.5532 | 9.8065 | 10.4778 | 17.9061 | 14.9351 | 15.4184 | 15.9877 | 23.8066 | 17.9325 | 21.9513 | 19.8213 | 33.862 | 24.6443 | 14.2827 | 18.5546 | 19.0491 | 15.9148 | 18.5535 | 19.9248 | 19.9073 | 17.6811 | 16.864 | 16.4033 | 30.1153 | 26.7791 | 8.5071 | 7.778 | 6.3482 | 6.202 | 5.0528 | 2.6304 | 12.5417 | 0
0 |  |  | Non-Depreciable Asset Total ($m) = |  | 3.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Total ($m) = |  | 4.0002 | 19.3524 | 0.84246 | 0.84246 | 16.1962 | 10.1004 | 21.5013 | 16.5532 | 9.8065 | 10.4778 | 17.9061 | 14.9351 | 15.4184 | 15.9877 | 23.8066 | 17.9325 | 21.9513 | 19.8213 | 33.862 | 24.6443 | 14.2827 | 18.5546 | 19.0491 | 15.9148 | 18.5535 | 19.9248 | 19.9073 | 17.6811 | 16.864 | 16.4033 | 30.1153 | 26.7791 | 8.5071 | 7.778 | 6.3482 | 6.202 | 5.0528 | 2.6304 | 12.5417 | 0
0.6045% |  |  | Interest During Construction ($m) = |  | 0 | 0.01209 | 0.070619 | 0.073379 | 0.076147 | 0.12533 | 0.15624 | 0.2217 | 0.2724 | 0.30286 | 0.33544 | 0.39058 | 0.4369 | 0.48482 | 0.53461 | 0.60818 | 0.66422 | 0.73257 | 0.7947 | 0.89944 | 0.97665 | 1.0228 | 1.0819 | 1.1428 | 1.1943 | 1.254 | 1.318 | 1.3822 | 1.4398 | 1.4951 | 1.5492 | 1.6449 | 1.7308 | 1.7618 | 1.7906 | 1.8152 | 1.8395 | 1.8603 | 1.8739 | 0
|  |  | IDC + Depreciable Assets ($m) = |  | 0.80019 | 19.3645 | 0.91308 | 0.91584 | 16.2724 | 10.2257 | 21.6575 | 16.7748 | 10.0789 | 10.7806 | 18.2416 | 15.3257 | 15.8553 | 16.4726 | 24.3412 | 18.5407 | 22.6156 | 20.5539 | 34.6567 | 25.5437 | 15.2593 | 19.5774 | 20.1311 | 17.0576 | 19.7478 | 21.1788 | 21.2253 | 19.0633 | 18.3038 | 17.8984 | 31.6646 | 28.4241 | 10.2379 | 9.5398 | 8.1388 | 8.0172 | 6.8922 | 4.4907 | 14.4156 | 0
|  |  | Cumulative Dollars Spent ($m) = |  | 4.0002 | 23.3647 | 24.2778 | 25.1937 | 41.466 | 51.6917 | 73.3492 | 90.1241 | 100.203 | 110.9837 | 129.2252 | 144.5509 | 160.4062 | 176.8788 | 201.22 | 219.7607 | 242.3763 | 262.9301 | 297.5868 | 323.1305 | 338.3898 | 357.9672 | 378.0983 | 395.1559 | 414.9037 | 436.0825 | 457.3078 | 476.3711 | 494.6749 | 512.5733 | 544.2379 | 572.662 | 582.8999 | 592.4397 | 600.5785 | 608.5957 | 615.488 | 619.9787 | 634.3942 | 634.3942
|  |  | Overnight Cost ($m) = |  | 2012-04-01: 599.028
0.6787% |  |  | Installed Cost ($m) = |  | 2012-04-01: 681.9996
|  |  | Depreciable Cost ($m) = |  | 2012-04-01: 631.1942

## FOM Estimates
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
|  | Plant Capacity (MW) = | 655.638
|  | Technology = | CC
|  | CONE Area = | 3
|  | SCR = | Y
|  | FOM Escalation Rate (Beyond Year 5) = | 2.5%
|  | Property Tax Escalation Rate (Beyond Year 1) = | 2.5%
|  | Insurance Escalation Rate (Beyond Year 1) = | 2.5%
|  | Asset Management Escalation Rate (Beyond Year 1) = | 2.5%
|  | Area | Tech | SCR | [7 empty] | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
[12 empty] | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m) | ($m)
| Total FOM Costs | 3 | CC | Y | [7 empty] | 10.5043 | 10.7669 | 11.036 | 11.3119 | 11.5947 | 11.8846 | 12.1817 | 12.4863 | 12.7984 | 13.1184 | 13.4463 | 13.7825 | 14.1271 | 14.4802 | 14.8422 | 15.2133 | 15.5936 | 15.9835 | 16.3831 | 16.7926 | 17.2124 | 17.6428 | 18.0838 | 18.5359 | 18.9993 | 19.4743 | 19.9612 | 20.4602 | 20.9717 | 21.496 | 22.0334 | 22.5842 | 23.1488 | 23.7275 | 24.3207 | 24.9288 | 25.552 | 26.1908 | 26.8455 | 27.5167 | 28.2046 | 28.9097 | 29.6325 | 30.3733 | 31.1326 | 31.9109 | 32.7087 | 33.5264 | 34.3646 | 35.2237
3_CC_Y | FOM | 3 | CC | Y | [7 empty] | 5.1994 | 5.3294 | 5.4626 | 5.5992 | 5.7391 | 5.8826 | 6.0297 | 6.1804 | 6.3349 | 6.4933 | 6.6556 | 6.822 | 6.9926 | 7.1674 | 7.3466 | 7.5302 | 7.7185 | 7.9115 | 8.1092 | 8.312 | 8.5198 | 8.7328 | 8.9511 | 9.1749 | 9.4042 | 9.6393 | 9.8803 | 10.1273 | 10.3805 | 10.64 | 10.906 | 11.1787 | 11.4581 | 11.7446 | 12.0382 | 12.3392 | 12.6477 | 12.9638 | 13.2879 | 13.6201 | 13.9606 | 14.3097 | 14.6674 | 15.0341 | 15.4099 | 15.7952 | 16.1901 | 16.5948 | 17.0097 | 17.4349
3_CC | Property Tax | 3 | CC | Y | [7 empty] | 0.054884 | 0.056256 | 0.057663 | 0.059104 | 0.060582 | 0.062097 | 0.063649 | 0.06524 | 0.066871 | 0.068543 | 0.070257 | 0.072013 | 0.073813 | 0.075659 | 0.07755 | 0.079489 | 0.081476 | 0.083513 | 0.085601 | 0.087741 | 0.089934 | 0.092183 | 0.094487 | 0.096849 | 0.099271 | 0.10175 | 0.1043 | 0.1069 | 0.10958 | 0.11232 | 0.11512 | 0.118 | 0.12095 | 0.12398 | 0.12707 | 0.13025 | 0.13351 | 0.13685 | 0.14027 | 0.14377 | 0.14737 | 0.15105 | 0.15483 | 0.1587 | 0.16267 | 0.16673 | 0.1709 | 0.17517 | 0.17955 | 0.18404
3_CC | Insurance | 3 | CC | Y | [7 empty] | 3.75 | 3.8437 | 3.9398 | 4.0383 | 4.1393 | 4.2428 | 4.3489 | 4.4576 | 4.569 | 4.6832 | 4.8003 | 4.9203 | 5.0433 | 5.1694 | 5.2987 | 5.4311 | 5.5669 | 5.7061 | 5.8487 | 5.9949 | 6.1448 | 6.2984 | 6.4559 | 6.6173 | 6.7827 | 6.9523 | 7.1261 | 7.3043 | 7.4869 | 7.674 | 7.8659 | 8.0625 | 8.2641 | 8.4707 | 8.6825 | 8.8995 | 9.122 | 9.3501 | 9.5838 | 9.8234 | 10.069 | 10.3207 | 10.5787 | 10.8432 | 11.1143 | 11.3921 | 11.6769 | 11.9689 | 12.2681 | 12.5748
3_CC | Asset Management | 3 | CC | Y | [7 empty] | 1.5 | 1.5375 | 1.5759 | 1.6153 | 1.6557 | 1.6971 | 1.7395 | 1.783 | 1.8276 | 1.8733 | 1.9201 | 1.9681 | 2.0173 | 2.0678 | 2.1195 | 2.1724 | 2.2268 | 2.2824 | 2.3395 | 2.398 | 2.4579 | 2.5194 | 2.5824 | 2.6469 | 2.7131 | 2.7809 | 2.8504 | 2.9217 | 2.9947 | 3.0696 | 3.1464 | 3.225 | 3.3056 | 3.3883 | 3.473 | 3.5598 | 3.6488 | 3.74 | 3.8335 | 3.9294 | 4.0276 | 4.1283 | 4.2315 | 4.3373 | 4.4457 | 4.5569 | 4.6708 | 4.7875 | 4.9072 | 5.0299
FOM Costs (Nominal $)
|  | Area | Tech | SCR | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | VOM | VOM | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
Lookup |  |  |  |  | (Total$) | (Total$) | (Total$) | (Total$) | (Total$) | (Total$) | (%) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$) | (FOM$)
1_CT_N | Middlesex, NJ | 1 | CT | N | 2862324 | 2933883 | 3007229 | 3082411 | 3159471 | 146792 | 5.128% | 2715532 | 2783421.1538 | 2853005.6628 | 2924332.014 | 2997440.0535 | 3072376.0548 | 3149185.4562 | 3227915.0926 | 3308612.9699 | 3391328.2941 | 3476111.5015 | 3563014.289 | 3652089.6462 | 3743391.8874 | 3836976.6846 | 3932901.1017 | 4031223.6292 | 4132004.22 | 4235304.3255 | 4341186.9336 | 4449716.607 | 4560959.5221 | 4674983.5102 | 4791858.0979 | 4911654.5504 | 5034445.9141 | 5160307.062 | 5289314.7385 | 5421547.607 | 5557086.2972 | 5696013.4546 | 5838413.791 | 5984374.1358 | 6133983.4891 | 6287333.0764 | 6444516.4033 | 6605629.3134 | 6770770.0462 | 6940039.2974 | 7113540.2798 | 7291378.7868 | 7473663.2565 | 7660504.8379 | 7852017.4588 | 8048317.8953 | 8249525.8427 | 8455763.9887 | 8667158.0884 | 8883837.0407 | 9105932.9667
2_CT_N | Charles County, MD | 2 | CT | N | 2688669 | 2755886 | 2824783 | 2895403 | 2967788 | 146792 | 5.46% | 2541877 | 2605424.185 | 2670559.6478 | 2737324.0408 | 2805757.0709 | 2875900.9977 | 2947798.5226 | 3021493.4857 | 3097030.8228 | 3174456.5934 | 3253818.0082 | 3335163.4584 | 3418542.5449 | 3504006.1085 | 3591606.2612 | 3681396.4178 | 3773431.3282 | 3867767.1114 | 3964461.2892 | 4063572.8214 | 4165162.142 | 4269291.1955 | 4376023.4754 | 4485424.0623 | 4597559.6638 | 4712498.6554 | 4830311.1218 | 4951068.8999 | 5074845.6224 | 5201716.7629 | 5331759.682 | 5465053.6741 | 5601680.0159 | 5741722.0163 | 5885265.0667 | 6032396.6934 | 6183206.6107 | 6337786.776 | 6496231.4454 | 6658637.2315 | 6825103.1623 | 6995730.7414 | 7170624.0099 | 7349889.6101 | 7533636.8504 | 7721977.7717 | 7915027.2159 | 8112902.8963 | 8315725.4688 | 8523618.6055
3_CT_N | Will, IL | 3 | CT | N | 2767682 | 2836874 | 2907795 | 2980491 | 3055003 | 146792 | 5.304% | 2620890 | 2686412.2027 | 2753571.7028 | 2822412.0607 | 2892972.1018 | 2965296.4044 | 3039428.8145 | 3115414.5348 | 3193299.8982 | 3273132.3956 | 3354960.7055 | 3438834.7232 | 3524805.5913 | 3612925.731 | 3703248.8743 | 3795830.0962 | 3890725.8486 | 3987993.9948 | 4087693.8447 | 4189886.1908 | 4294633.3455 | 4401999.1792 | 4512049.1587 | 4624850.3876 | 4740471.6473 | 4858983.4385 | 4980458.0245 | 5104969.4751 | 5232593.712 | 5363408.5548 | 5497493.7686 | 5634931.1128 | 5775804.3907 | 5920199.5004 | 6068204.4879 | 6219909.6001 | 6375407.3401 | 6534792.5236 | 6698162.3367 | 6865616.3952 | 7037256.805 | 7213188.2252 | 7393517.9308 | 7578355.8791 | 7767814.776 | 7962010.1454 | 8161060.3991 | 8365086.909 | 8574214.0818 | 8788569.4338
4_CT_N | Northampton, PA | 4 | CT | N | 2649101 | 2715329 | 2783211 | 2852792 | 2924112 | 146792 | 5.541% | 2502309 | 2564867.1737 | 2628987.6959 | 2694713.0731 | 2762081.0889 | 2831133.1161 | 2901911.444 | 2974459.2301 | 3048820.7108 | 3125041.2286 | 3203167.2593 | 3283246.4408 | 3365327.6018 | 3449460.7919 | 3535697.3117 | 3624089.7445 | 3714691.9881 | 3807559.2878 | 3902748.27 | 4000316.9767 | 4100324.9011 | 4202833.0237 | 4307903.8493 | 4415601.4455 | 4525991.4816 | 4639141.2687 | 4755119.8004 | 4873997.7954 | 4995847.7403 | 5120743.9338 | 5248762.5321 | 5379981.5954 | 5514481.1353 | 5652343.1637 | 5793651.7428 | 5938493.0364 | 6086955.3623 | 6239129.2463 | 6395107.4775 | 6554985.1644 | 6718859.7936 | 6886831.2884 | 7059002.0706 | 7235477.1224 | 7416364.0504 | 7601773.1517 | 7791817.4805 | 7986612.9175 | 8186278.2404 | 8390935.1964
5_CT_N | Fauquier, VA | 5 | CT | N | 2643078 | 2709156 | 2776884 | 2846306 | 2917464 | 146792 | 5.554% | 2496286 | 2558694.1417 | 2622660.6452 | 2688227.0669 | 2755433.0741 | 2824318.901 | 2894926.8735 | 2967300.0453 | 3041482.5465 | 3117519.6101 | 3195457.6004 | 3275344.0404 | 3357227.6414 | 3441158.3324 | 3527187.2908 | 3615366.973 | 3705751.1474 | 3798394.926 | 3893354.7992 | 3990688.6692 | 4090455.8859 | 4192717.283 | 4297535.2151 | 4404973.5955 | 4515097.9354 | 4627975.3838 | 4743674.7684 | 4862266.6376 | 4983823.3035 | 5108418.8861 | 5236129.3583 | 5367032.5922 | 5501208.407 | 5638738.6172 | 5779707.0826 | 5924199.7597 | 6072304.7537 | 6224112.3725 | 6379715.1818 | 6539208.0614 | 6702688.2629 | 6870255.4695 | 7042011.8562 | 7218062.1526 | 7398513.7064 | 7583476.5491 | 7773063.4628 | 7967390.0494 | 8166574.8006 | 8370739.1707
__
1_CT_Y | Middlesex, NJ | 1 | CT | Y | 2868587 | 2940302 | 3013809 | 3089155 | 3166383 | 153055 | 5.336% | 2715532 | 2783420.6077 | 2853005.6022 | 2924331.4759 | 2997438.9345 | 3072374.9078 | 3149184.2805 | 3227913.8876 | 3308611.7347 | 3391327.0281 | 3476110.2038 | 3563012.9589 | 3652088.2829 | 3743390.49 | 3836975.2522 | 3932899.6335 | 4031222.1243 | 4132002.6775 | 4235302.7444 | 4341185.313 | 4449714.9458 | 4560957.8195 | 4674981.765 | 4791856.3091 | 4911652.7168 | 5034444.0347 | 5160305.1356 | 5289312.764 | 5421545.5831 | 5557084.2227 | 5696011.3282 | 5838411.6114 | 5984371.9017 | 6133981.1993 | 6287330.7293 | 6444513.9975 | 6605626.8474 | 6770767.5186 | 6940036.7066 | 7113537.6242 | 7291376.0648 | 7473660.4665 | 7660501.9781 | 7852014.5276 | 8048314.8908 | 8249522.763 | 8455760.8321 | 8667154.8529 | 8883833.7242 | 9105929.5673
2_CT_Y | Charles County, MD | 2 | CT | Y | 2694932 | 2762306 | 2831363 | 2902147 | 2974701 | 153055 | 5.679% | 2541877 | 2605424.5852 | 2670559.5868 | 2737323.5057 | 2805756.8999 | 2875900.8224 | 2947798.343 | 3021493.3015 | 3097030.6341 | 3174456.3999 | 3253817.8099 | 3335163.2552 | 3418542.3366 | 3504005.895 | 3591606.0423 | 3681396.1934 | 3773431.0982 | 3867766.8757 | 3964461.0476 | 4063572.5738 | 4165161.8881 | 4269290.9353 | 4376023.2087 | 4485423.7889 | 4597559.3836 | 4712498.3682 | 4830310.8274 | 4951068.5981 | 5074845.3131 | 5201716.4459 | 5331759.3571 | 5465053.341 | 5601679.6745 | 5741721.6664 | 5885264.708 | 6032396.3257 | 6183206.2339 | 6337786.3897 | 6496231.0495 | 6658636.8257 | 6825102.7463 | 6995730.315 | 7170623.5729 | 7349889.1622 | 7533636.3913 | 7721977.301 | 7915026.7336 | 8112902.4019 | 8315724.9619 | 8523618.086
3_CT_Y | Will, IL | 3 | CT | Y | 2773944 | 2843294 | 2914375 | 2987235 | 3061915 | 153055 | 5.518% | 2620889 | 2686412.5478 | 2753571.5859 | 2822411.4661 | 2892970.926 | 2965295.1992 | 3039427.5792 | 3115413.2686 | 3193298.6004 | 3273131.0654 | 3354959.342 | 3438833.3255 | 3524804.1587 | 3612924.2627 | 3703247.3692 | 3795828.5535 | 3890724.2673 | 3987992.374 | 4087692.1833 | 4189884.4879 | 4294631.6001 | 4401997.3901 | 4512047.3249 | 4624848.508 | 4740469.7207 | 4858981.4637 | 4980456.0003 | 5104967.4003 | 5232591.5853 | 5363406.3749 | 5497491.5343 | 5634928.8227 | 5775802.0432 | 5920197.0943 | 6068202.0217 | 6219907.0722 | 6375404.749 | 6534789.8677 | 6698159.6144 | 6865613.6048 | 7037253.9449 | 7213185.2935 | 7393514.9259 | 7578352.799 | 7767811.619 | 7962006.9095 | 8161057.0822 | 8365083.5093 | 8574210.597 | 8788565.8619
4_CT_Y | Northampton, PA | 4 | CT | Y | 2655364 | 2721748 | 2789792 | 2859537 | 2931025 | 153055 | 5.764% | 2502309 | 2564866.6308 | 2628988.5792 | 2694713.4822 | 2762080.9187 | 2831132.9417 | 2901911.2653 | 2974459.0469 | 3048820.5231 | 3125041.0361 | 3203167.062 | 3283246.2386 | 3365327.3946 | 3449460.5794 | 3535697.0939 | 3624089.5213 | 3714691.7593 | 3807559.0533 | 3902748.0296 | 4000316.7303 | 4100324.6486 | 4202832.7648 | 4307903.5839 | 4415601.1735 | 4525991.2029 | 4639140.9829 | 4755119.5075 | 4873997.4952 | 4995847.4326 | 5120743.6184 | 5248762.2089 | 5379981.2641 | 5514480.7957 | 5652342.8156 | 5793651.386 | 5938492.6706 | 6086954.9874 | 6239128.8621 | 6395107.0836 | 6554984.7607 | 6718859.3797 | 6886830.8642 | 7059001.6358 | 7235476.6767 | 7416363.5936 | 7601772.6835 | 7791817.0006 | 7986612.4256 | 8186277.7362 | 8390934.6796
5_CT_Y | Fauquier, VA | 5 | CT | Y | 2649341 | 2715575 | 2783464 | 2853051 | 2924377 | 153055 | 5.777% | 2496286 | 2558693.5976 | 2622660.5842 | 2688227.4757 | 2755432.9034 | 2824318.726 | 2894926.6942 | 2967299.8615 | 3041482.3581 | 3117519.417 | 3195457.4024 | 3275343.8375 | 3357227.4334 | 3441158.1193 | 3527187.0723 | 3615366.7491 | 3705750.9178 | 3798394.6907 | 3893354.558 | 3990688.422 | 4090455.6325 | 4192717.0233 | 4297534.9489 | 4404973.3226 | 4515097.6557 | 4627975.0971 | 4743674.4745 | 4862266.3364 | 4983822.9948 | 5108418.5696 | 5236129.0339 | 5367032.2597 | 5501208.0662 | 5638738.2679 | 5779706.7246 | 5924199.3927 | 6072304.3775 | 6224111.987 | 6379714.7866 | 6539207.6563 | 6702687.8477 | 6870255.0439 | 7042011.42 | 7218061.7055 | 7398513.2481 | 7583476.0793 | 7773062.9813 | 7967389.5558 | 8166574.2947 | 8370738.6521
__
1_CC_Y | Middlesex, NJ | 1 | CC | Y | 6833182 | 7004010 | 7179110 | 7358589 | 7542555 | 1384799 | 20.27% | 5448383 | 5584591.3391 | 5724205.9233 | 5867312.068 | 6013995.8863 | 6164345.7835 | 6318454.4281 | 6476415.7888 | 6638326.1835 | 6804284.3381 | 6974391.4465 | 7148751.2327 | 7327470.0135 | 7510656.7639 | 7698423.183 | 7890883.7625 | 8088155.8566 | 8290359.753 | 8497618.7468 | 8710059.2155 | 8927810.6959 | 9151005.9633 | 9379781.1124 | 9614275.6402 | 9854632.5312 | 10100998.3445 | 10353523.3031 | 10612361.3857 | 10877670.4203 | 11149612.1808 | 11428352.4853 | 11714061.2975 | 12006912.8299 | 12307085.6506 | 12614762.7919 | 12930131.8617 | 13253385.1582 | 13584719.7872 | 13924337.7819 | 14272446.2264 | 14629257.3821 | 14994988.8166 | 15369863.5371 | 15754110.1255 | 16147962.8786 | 16551661.9506 | 16965453.4993 | 17389589.8368 | 17824329.5828 | 18269937.8223
2_CC_Y | Charles County, MD | 2 | CC | Y | 6407425 | 6567609 | 6731799 | 6900095 | 7072599 | 1384799 | 21.61% | 5022626 | 5148190.3762 | 5276894.9592 | 5408818.1367 | 5544039.8639 | 5682640.8605 | 5824706.882 | 5970324.5541 | 6119582.6679 | 6272572.2346 | 6429386.5405 | 6590121.204 | 6754874.2341 | 6923746.0899 | 7096839.7422 | 7274260.7357 | 7456117.2541 | 7642520.1855 | 7833583.1901 | 8029422.7699 | 8230158.3391 | 8435912.2976 | 8646810.105 | 8862980.3577 | 9084554.8666 | 9311668.7383 | 9544460.4567 | 9783071.9682 | 10027648.7674 | 10278339.9865 | 10535298.4862 | 10798680.9484 | 11068647.9721 | 11345364.1714 | 11628998.2757 | 11919723.2326 | 12217716.3134 | 12523159.2212 | 12836238.2017 | 13157144.1568 | 13486072.7607 | 13823224.5797 | 14168805.1942 | 14523025.3241 | 14886100.9572 | 15258253.4811 | 15639709.8181 | 16030702.5636 | 16431470.1277 | 16842256.8809
3_CC_Y | Will, IL | 3 | CC | Y | 6584169 | 6748771 | 6917491 | 7090428 | 7267691 | 1384799 | 21.03% | 5199370 | 5329352.493 | 5462586.8778 | 5599151.3326 | 5739131.9322 | 5882610.2305 | 6029675.4862 | 6180417.3734 | 6334927.8077 | 6493301.0029 | 6655633.528 | 6822024.3662 | 6992574.9753 | 7167389.3497 | 7346574.0835 | 7530238.4356 | 7718494.3964 | 7911456.7564 | 8109243.1753 | 8311974.2546 | 8519773.611 | 8732767.9513 | 8951087.1501 | 9174864.3288 | 9404235.937 | 9639341.8355 | 9880325.3814 | 10127333.5159 | 10380516.8538 | 10640029.7751 | 10906030.5195 | 11178681.2825 | 11458148.3146 | 11744602.0224 | 12038217.073 | 12339172.4998 | 12647651.8123 | 12963843.1076 | 13287939.1853 | 13620137.6649 | 13960641.1066 | 14309657.1342 | 14667398.5626 | 15034083.5266 | 15409935.6148 | 15795184.0052 | 16190063.6053 | 16594815.1954 | 17009685.5753 | 17434927.7147
4_CC_Y | Northampton, PA | 4 | CC | Y | 6291117 | 6448393 | 6609603 | 6774843 | 6944216 | 1384799 | 22.01% | 4906318 | 5028974.4487 | 5154698.9464 | 5283566.3616 | 5415657.0219 | 5551048.4475 | 5689824.6586 | 5832070.2751 | 5977872.032 | 6127318.8328 | 6280501.8036 | 6437514.3487 | 6598452.2074 | 6763413.5126 | 6932498.8504 | 7105811.3217 | 7283456.6047 | 7465543.0198 | 7652181.5953 | 7843486.1352 | 8039573.2886 | 8240562.6208 | 8446576.6863 | 8657741.1035 | 8874184.6311 | 9096039.2468 | 9323440.228 | 9556526.2337 | 9795439.3896 | 10040325.3743 | 10291333.5087 | 10548616.8464 | 10812332.2675 | 11082640.5742 | 11359706.5886 | 11643699.2533 | 11934791.7346 | 12233161.528 | 12538990.5662 | 12852465.3303 | 13173776.9636 | 13503121.3877 | 13840699.4224 | 14186716.9079 | 14541384.8306 | 14904919.4514 | 15277542.4377 | 15659480.9986 | 16050968.0236 | 16452242.2242
5_CC_Y | Fauquier, VA | 5 | CC | Y | 6263303 | 6419884 | 6580381 | 6744891 | 6913515 | 1384799 | 22.11% | 4878504 | 5000465.3732 | 5125476.9297 | 5253614.2229 | 5384955.9221 | 5519579.8201 | 5657569.3156 | 5799008.5485 | 5943983.7622 | 6092583.3563 | 6244897.9402 | 6401020.3887 | 6561045.8984 | 6725072.0459 | 6893198.847 | 7065528.8182 | 7242167.0386 | 7423221.2146 | 7608801.745 | 7799021.7886 | 7993997.3333 | 8193847.2667 | 8398693.4483 | 8608660.7845 | 8823877.3041 | 9044474.2367 | 9270586.0927 | 9502350.745 | 9739909.5136 | 9983407.2514 | 10232992.4327 | 10488817.2435 | 10751037.6746 | 11019813.6165 | 11295308.9569 | 11577691.6808 | 11867133.9729 | 12163812.3222 | 12467907.6302 | 12779605.321 | 13099095.454 | 13426572.8404 | 13762237.1614 | 14106293.0904 | 14458950.4177 | 14820424.1781 | 15190934.7826 | 15570708.1521 | 15959975.8559 | 16358975.2523
Property Taxes (Nominal $)
|  | Area | Tech | SCR | Land Value | Land Tax | Plant Tax |  |  |  |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
[5 empty] | ($m) | (%) | ($/MW-yr) |  |  |  |  | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($)
1_CT | Middlesex, NJ | 1 | CT | n/a | 3.87 | 4.25% | 0 |  |  |  |  | 164475 | 168586.875 | 172801.5469 | 177121.5855 | 181549.6252 | 186088.3658 | 190740.575 | 195509.0893 | 200396.8166 | 205406.737 | 210541.9054 | 215805.453 | 221200.5894 | 226730.6041 | 232398.8692 | 238208.8409 | 244164.062 | 250268.1635 | 256524.8676 | 262937.9893 | 269511.439 | 276249.225 | 283155.4556 | 290234.342 | 297490.2006 | 304927.4556 | 312550.642 | 320364.408 | 328373.5182 | 336582.8562 | 344997.4276 | 353622.3633 | 362462.9223 | 371524.4954 | 380812.6078 | 390332.923 | 400091.2461 | 410093.5272 | 420345.8654 | 430854.512 | 441625.8748 | 452666.5217 | 463983.1847 | 475582.7644 | 487472.3335 | 499659.1418 | 512150.6203 | 524954.3858 | 538078.2455 | 551530.2016
2_CT | Charles County, MD | 2 | CT | n/a | 3.6 | 1.14% | 831 |  |  |  |  | 585875.178 | 600522.0575 | 615535.1089 | 630923.4866 | 646696.5738 | 662863.9881 | 679435.5878 | 696421.4775 | 713832.0145 | 731677.8148 | 749969.7602 | 768719.0042 | 787936.9793 | 807635.4038 | 827826.2889 | 848521.9461 | 869734.9947 | 891478.3696 | 913765.3289 | 936609.4621 | 960024.6986 | 984025.3161 | 1008625.949 | 1033841.5977 | 1059687.6377 | 1086179.8286 | 1113334.3243 | 1141167.6824 | 1169696.8745 | 1198939.2964 | 1228912.7788 | 1259635.5982 | 1291126.4882 | 1323404.6504 | 1356489.7667 | 1390402.0108 | 1425162.0611 | 1460791.1126 | 1497310.8904 | 1534743.6627 | 1573112.2543 | 1612440.0606 | 1652751.0621 | 1694069.8387 | 1736421.5847 | 1779832.1243 | 1824327.9274 | 1869936.1256 | 1916684.5287 | 1964601.6419
3_CT | Will, IL | 3 | CT | n/a | 2.4 | 1.715% | 0 |  |  |  |  | 41163.227 | 42192.3077 | 43247.1154 | 44328.2933 | 45436.5006 | 46572.4131 | 47736.7234 | 48930.1415 | 50153.3951 | 51407.2299 | 52692.4107 | 54009.721 | 55359.964 | 56743.9631 | 58162.5622 | 59616.6262 | 61107.0419 | 62634.7179 | 64200.5859 | 65805.6005 | 67450.7405 | 69137.009 | 70865.4343 | 72637.0701 | 74452.9969 | 76314.3218 | 78222.1798 | 80177.7343 | 82182.1777 | 84236.7321 | 86342.6504 | 88501.2167 | 90713.7471 | 92981.5908 | 95306.1306 | 97688.7838 | 100131.0034 | 102634.2785 | 105200.1355 | 107830.1389 | 110525.8923 | 113289.0396 | 116121.2656 | 119024.2973 | 121999.9047 | 125049.9023 | 128176.1499 | 131380.5536 | 134665.0675 | 138031.6942
4_CT | Northampton, PA | 4 | CT | n/a | 2.7 | 3.02% | 135 |  |  |  |  | 170051.13 | 174302.4082 | 178659.9685 | 183126.4677 | 187704.6294 | 192397.2451 | 197207.1762 | 202137.3556 | 207190.7895 | 212370.5593 | 217679.8232 | 223121.8188 | 228699.8643 | 234417.3609 | 240277.7949 | 246284.7398 | 252441.8583 | 258752.9047 | 265221.7274 | 271852.2705 | 278648.5773 | 285614.7917 | 292755.1615 | 300074.0406 | 307575.8916 | 315265.2889 | 323146.9211 | 331225.5941 | 339506.234 | 347993.8898 | 356693.7371 | 365611.0805 | 374751.3575 | 384120.1415 | 393723.145 | 403566.2236 | 413655.3792 | 423996.7637 | 434596.6828 | 445461.5998 | 456598.1398 | 468013.0933 | 479713.4207 | 491706.2562 | 503998.9126 | 516598.8854 | 529513.8575 | 542751.704 | 556320.4966 | 570228.509
5_CT | Fauquier, VA | 5 | CT | n/a | 3.54 | 0% | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
_
1_CC | Middlesex, NJ | 1 | CC | n/a | 5.16 | 4.25% | 0 |  |  |  |  | 219300 | 224782.5 | 230402.0625 | 236162.1141 | 242066.1669 | 248117.8211 | 254320.7666 | 260678.7858 | 267195.7554 | 273875.6493 | 280722.5405 | 287740.6041 | 294934.1192 | 302307.4721 | 309865.1589 | 317611.7879 | 325552.0826 | 333690.8847 | 342033.1568 | 350583.9857 | 359348.5854 | 368332.3 | 377540.6075 | 386979.1227 | 396653.6007 | 406569.9408 | 416734.1893 | 427152.544 | 437831.3576 | 448777.1416 | 459996.5701 | 471496.4843 | 483283.8965 | 495365.9939 | 507750.1437 | 520443.8973 | 533454.9947 | 546791.3696 | 560461.1538 | 574472.6827 | 588834.4998 | 603555.3623 | 618644.2463 | 634110.3525 | 649963.1113 | 666212.1891 | 682867.4938 | 699939.1811 | 717437.6607 | 735373.6022
2_CC | Charles County, MD | 2 | CC | n/a | 4.8 | 1.14% | 831 |  |  |  |  | 599555.178 | 614544.0574 | 629907.6589 | 645655.3504 | 661796.7341 | 678341.6525 | 695300.1938 | 712682.6986 | 730499.7661 | 748762.2602 | 767481.3168 | 786668.3497 | 806335.0584 | 826493.4349 | 847155.7707 | 868334.665 | 890043.0316 | 912294.1074 | 935101.4601 | 958478.9966 | 982440.9715 | 1007001.9958 | 1032177.0457 | 1057981.4719 | 1084431.0087 | 1111541.7839 | 1139330.3285 | 1167813.5867 | 1197008.9263 | 1226934.1495 | 1257607.5032 | 1289047.6908 | 1321273.8831 | 1354305.7302 | 1388163.3734 | 1422867.4578 | 1458439.1442 | 1494900.1228 | 1532272.6259 | 1570579.4415 | 1609843.9276 | 1650090.0258 | 1691342.2764 | 1733625.8333 | 1776966.4791 | 1821390.6411 | 1866925.4071 | 1913598.5423 | 1961438.5059 | 2010474.4685
3_CC | Will, IL | 3 | CC | n/a | 3.2 | 1.715% | 0 |  |  |  |  | 54884.3027 | 56256.4103 | 57662.8205 | 59104.391 | 60582.0008 | 62096.5508 | 63648.9646 | 65240.1887 | 66871.1934 | 68542.9733 | 70256.5476 | 72012.9613 | 73813.2853 | 75658.6174 | 77550.0829 | 79488.835 | 81476.0558 | 83512.9572 | 85600.7812 | 87740.8007 | 89934.3207 | 92182.6787 | 94487.2457 | 96849.4268 | 99270.6625 | 101752.4291 | 104296.2398 | 106903.6458 | 109576.2369 | 112315.6429 | 115123.5339 | 118001.6223 | 120951.6628 | 123975.4544 | 127074.8408 | 130251.7118 | 133508.0046 | 136845.7047 | 140266.8473 | 143773.5185 | 147367.8564 | 151052.0529 | 154828.3542 | 158699.063 | 162666.5396 | 166733.2031 | 170901.5332 | 175174.0715 | 179553.4233 | 184042.2589
4_CC | Northampton, PA | 4 | CC | n/a | 3.6 | 3.02% | 135 |  |  |  |  | 197231.13 | 202161.9082 | 207215.956 | 212396.3549 | 217706.2637 | 223148.9203 | 228727.6433 | 234445.8344 | 240306.9803 | 246314.6548 | 252472.5211 | 258784.3342 | 265253.9425 | 271885.2911 | 278682.4234 | 285649.484 | 292790.7211 | 300110.4891 | 307613.2513 | 315303.5826 | 323186.1722 | 331265.8265 | 339547.4721 | 348036.1589 | 356737.0629 | 365655.4895 | 374796.8767 | 384166.7986 | 393770.9686 | 403615.2428 | 413705.6239 | 424048.2645 | 434649.4711 | 445515.7079 | 456653.6006 | 468069.9406 | 479771.6891 | 491765.9813 | 504060.1308 | 516661.6341 | 529578.175 | 542817.6293 | 556388.0701 | 570297.7718 | 584555.2161 | 599169.0965 | 614148.3239 | 629502.032 | 645239.5828 | 661370.5724
5_CC | Fauquier, VA | 5 | CC | n/a | 4.72 | 0% | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Insurance (Nominal $)
|  | Area | Tech | SCR | [7 empty] | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
[12 empty] | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($)
1_CT | Middlesex, NJ | 1 | CT | n/a | [7 empty] | 1750000 | 1793750 | 1838593.75 | 1884558.5937 | 1931672.5586 | 1979964.3726 | 2029463.4819 | 2080200.0689 | 2132205.0706 | 2185510.1974 | 2240147.9523 | 2296151.6512 | 2353555.4424 | 2412394.3285 | 2472704.1867 | 2534521.7914 | 2597884.8362 | 2662831.9571 | 2729402.756 | 2797637.8249 | 2867578.7705 | 2939268.2398 | 3012749.9458 | 3088068.6944 | 3165270.4118 | 3244402.1721 | 3325512.2264 | 3408650.032 | 3493866.2828 | 3581212.9399 | 3670743.2634 | 3762511.845 | 3856574.6411 | 3952989.0071 | 4051813.7323 | 4153109.0756 | 4256936.8025 | 4363360.2226 | 4472444.2281 | 4584255.3338 | 4698861.7172 | 4816333.2601 | 4936741.5916 | 5060160.1314 | 5186664.1347 | 5316330.7381 | 5449239.0065 | 5585469.9817 | 5725106.7312 | 5868234.3995
2_CT | Charles County, MD | 2 | CT | n/a | [7 empty] | 1750000 | 1793750 | 1838593.75 | 1884558.5937 | 1931672.5586 | 1979964.3726 | 2029463.4819 | 2080200.0689 | 2132205.0706 | 2185510.1974 | 2240147.9523 | 2296151.6512 | 2353555.4424 | 2412394.3285 | 2472704.1867 | 2534521.7914 | 2597884.8362 | 2662831.9571 | 2729402.756 | 2797637.8249 | 2867578.7705 | 2939268.2398 | 3012749.9458 | 3088068.6944 | 3165270.4118 | 3244402.1721 | 3325512.2264 | 3408650.032 | 3493866.2828 | 3581212.9399 | 3670743.2634 | 3762511.845 | 3856574.6411 | 3952989.0071 | 4051813.7323 | 4153109.0756 | 4256936.8025 | 4363360.2226 | 4472444.2281 | 4584255.3338 | 4698861.7172 | 4816333.2601 | 4936741.5916 | 5060160.1314 | 5186664.1347 | 5316330.7381 | 5449239.0065 | 5585469.9817 | 5725106.7312 | 5868234.3995
3_CT | Will, IL | 3 | CT | n/a | [7 empty] | 1750000 | 1793750 | 1838593.75 | 1884558.5937 | 1931672.5586 | 1979964.3726 | 2029463.4819 | 2080200.0689 | 2132205.0706 | 2185510.1974 | 2240147.9523 | 2296151.6512 | 2353555.4424 | 2412394.3285 | 2472704.1867 | 2534521.7914 | 2597884.8362 | 2662831.9571 | 2729402.756 | 2797637.8249 | 2867578.7705 | 2939268.2398 | 3012749.9458 | 3088068.6944 | 3165270.4118 | 3244402.1721 | 3325512.2264 | 3408650.032 | 3493866.2828 | 3581212.9399 | 3670743.2634 | 3762511.845 | 3856574.6411 | 3952989.0071 | 4051813.7323 | 4153109.0756 | 4256936.8025 | 4363360.2226 | 4472444.2281 | 4584255.3338 | 4698861.7172 | 4816333.2601 | 4936741.5916 | 5060160.1314 | 5186664.1347 | 5316330.7381 | 5449239.0065 | 5585469.9817 | 5725106.7312 | 5868234.3995
4_CT | Northampton, PA | 4 | CT | n/a | [7 empty] | 1750000 | 1793750 | 1838593.75 | 1884558.5937 | 1931672.5586 | 1979964.3726 | 2029463.4819 | 2080200.0689 | 2132205.0706 | 2185510.1974 | 2240147.9523 | 2296151.6512 | 2353555.4424 | 2412394.3285 | 2472704.1867 | 2534521.7914 | 2597884.8362 | 2662831.9571 | 2729402.756 | 2797637.8249 | 2867578.7705 | 2939268.2398 | 3012749.9458 | 3088068.6944 | 3165270.4118 | 3244402.1721 | 3325512.2264 | 3408650.032 | 3493866.2828 | 3581212.9399 | 3670743.2634 | 3762511.845 | 3856574.6411 | 3952989.0071 | 4051813.7323 | 4153109.0756 | 4256936.8025 | 4363360.2226 | 4472444.2281 | 4584255.3338 | 4698861.7172 | 4816333.2601 | 4936741.5916 | 5060160.1314 | 5186664.1347 | 5316330.7381 | 5449239.0065 | 5585469.9817 | 5725106.7312 | 5868234.3995
5_CT | Fauquier, VA | 5 | CT | n/a | [7 empty] | 1750000 | 1793750 | 1838593.75 | 1884558.5937 | 1931672.5586 | 1979964.3726 | 2029463.4819 | 2080200.0689 | 2132205.0706 | 2185510.1974 | 2240147.9523 | 2296151.6512 | 2353555.4424 | 2412394.3285 | 2472704.1867 | 2534521.7914 | 2597884.8362 | 2662831.9571 | 2729402.756 | 2797637.8249 | 2867578.7705 | 2939268.2398 | 3012749.9458 | 3088068.6944 | 3165270.4118 | 3244402.1721 | 3325512.2264 | 3408650.032 | 3493866.2828 | 3581212.9399 | 3670743.2634 | 3762511.845 | 3856574.6411 | 3952989.0071 | 4051813.7323 | 4153109.0756 | 4256936.8025 | 4363360.2226 | 4472444.2281 | 4584255.3338 | 4698861.7172 | 4816333.2601 | 4936741.5916 | 5060160.1314 | 5186664.1347 | 5316330.7381 | 5449239.0065 | 5585469.9817 | 5725106.7312 | 5868234.3995
_
1_CC | Middlesex, NJ | 1 | CC | n/a | [7 empty] | 3750000 | 3843750 | 3939843.75 | 4038339.8437 | 4139298.3398 | 4242780.7983 | 4348850.3183 | 4457571.5763 | 4569010.8657 | 4683236.1373 | 4800317.0407 | 4920324.9668 | 5043333.0909 | 5169416.4182 | 5298651.8287 | 5431118.1244 | 5566896.0775 | 5706068.4794 | 5848720.1914 | 5994938.1962 | 6144811.6511 | 6298431.9424 | 6455892.7409 | 6617290.0594 | 6782722.3109 | 6952290.3687 | 7126097.6279 | 7304250.0686 | 7486856.3203 | 7674027.7283 | 7865878.4216 | 8062525.3821 | 8264088.5166 | 8470690.7296 | 8682457.9978 | 8899519.4477 | 9122007.4339 | 9350057.6198 | 9583809.0603 | 9823404.2868 | 10068989.394 | 10320714.1288 | 10578731.982 | 10843200.2816 | 11114280.2886 | 11392137.2958 | 11676940.7282 | 11968864.2464 | 12268085.8526 | 12574787.9989
2_CC | Charles County, MD | 2 | CC | n/a | [7 empty] | 3750000 | 3843750 | 3939843.75 | 4038339.8437 | 4139298.3398 | 4242780.7983 | 4348850.3183 | 4457571.5763 | 4569010.8657 | 4683236.1373 | 4800317.0407 | 4920324.9668 | 5043333.0909 | 5169416.4182 | 5298651.8287 | 5431118.1244 | 5566896.0775 | 5706068.4794 | 5848720.1914 | 5994938.1962 | 6144811.6511 | 6298431.9424 | 6455892.7409 | 6617290.0594 | 6782722.3109 | 6952290.3687 | 7126097.6279 | 7304250.0686 | 7486856.3203 | 7674027.7283 | 7865878.4216 | 8062525.3821 | 8264088.5166 | 8470690.7296 | 8682457.9978 | 8899519.4477 | 9122007.4339 | 9350057.6198 | 9583809.0603 | 9823404.2868 | 10068989.394 | 10320714.1288 | 10578731.982 | 10843200.2816 | 11114280.2886 | 11392137.2958 | 11676940.7282 | 11968864.2464 | 12268085.8526 | 12574787.9989
3_CC | Will, IL | 3 | CC | n/a | [7 empty] | 3750000 | 3843750 | 3939843.75 | 4038339.8437 | 4139298.3398 | 4242780.7983 | 4348850.3183 | 4457571.5763 | 4569010.8657 | 4683236.1373 | 4800317.0407 | 4920324.9668 | 5043333.0909 | 5169416.4182 | 5298651.8287 | 5431118.1244 | 5566896.0775 | 5706068.4794 | 5848720.1914 | 5994938.1962 | 6144811.6511 | 6298431.9424 | 6455892.7409 | 6617290.0594 | 6782722.3109 | 6952290.3687 | 7126097.6279 | 7304250.0686 | 7486856.3203 | 7674027.7283 | 7865878.4216 | 8062525.3821 | 8264088.5166 | 8470690.7296 | 8682457.9978 | 8899519.4477 | 9122007.4339 | 9350057.6198 | 9583809.0603 | 9823404.2868 | 10068989.394 | 10320714.1288 | 10578731.982 | 10843200.2816 | 11114280.2886 | 11392137.2958 | 11676940.7282 | 11968864.2464 | 12268085.8526 | 12574787.9989
4_CC | Northampton, PA | 4 | CC | n/a | [7 empty] | 3750000 | 3843750 | 3939843.75 | 4038339.8437 | 4139298.3398 | 4242780.7983 | 4348850.3183 | 4457571.5763 | 4569010.8657 | 4683236.1373 | 4800317.0407 | 4920324.9668 | 5043333.0909 | 5169416.4182 | 5298651.8287 | 5431118.1244 | 5566896.0775 | 5706068.4794 | 5848720.1914 | 5994938.1962 | 6144811.6511 | 6298431.9424 | 6455892.7409 | 6617290.0594 | 6782722.3109 | 6952290.3687 | 7126097.6279 | 7304250.0686 | 7486856.3203 | 7674027.7283 | 7865878.4216 | 8062525.3821 | 8264088.5166 | 8470690.7296 | 8682457.9978 | 8899519.4477 | 9122007.4339 | 9350057.6198 | 9583809.0603 | 9823404.2868 | 10068989.394 | 10320714.1288 | 10578731.982 | 10843200.2816 | 11114280.2886 | 11392137.2958 | 11676940.7282 | 11968864.2464 | 12268085.8526 | 12574787.9989
5_CC | Fauquier, VA | 5 | CC | n/a | [7 empty] | 3750000 | 3843750 | 3939843.75 | 4038339.8437 | 4139298.3398 | 4242780.7983 | 4348850.3183 | 4457571.5763 | 4569010.8657 | 4683236.1373 | 4800317.0407 | 4920324.9668 | 5043333.0909 | 5169416.4182 | 5298651.8287 | 5431118.1244 | 5566896.0775 | 5706068.4794 | 5848720.1914 | 5994938.1962 | 6144811.6511 | 6298431.9424 | 6455892.7409 | 6617290.0594 | 6782722.3109 | 6952290.3687 | 7126097.6279 | 7304250.0686 | 7486856.3203 | 7674027.7283 | 7865878.4216 | 8062525.3821 | 8264088.5166 | 8470690.7296 | 8682457.9978 | 8899519.4477 | 9122007.4339 | 9350057.6198 | 9583809.0603 | 9823404.2868 | 10068989.394 | 10320714.1288 | 10578731.982 | 10843200.2816 | 11114280.2886 | 11392137.2958 | 11676940.7282 | 11968864.2464 | 12268085.8526 | 12574787.9989
Asset Management (Nominal $)
|  | Area | Tech | SCR | [7 empty] | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50
[12 empty] | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($) | ($)
1_CT | Middlesex, NJ | 1 | CT | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
2_CT | Charles County, MD | 2 | CT | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
3_CT | Will, IL | 3 | CT | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
4_CT | Northampton, PA | 4 | CT | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
5_CT | Fauquier, VA | 5 | CT | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
_
1_CC | Middlesex, NJ | 1 | CC | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
2_CC | Charles County, MD | 2 | CC | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
3_CC | Will, IL | 3 | CC | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
4_CC | Northampton, PA | 4 | CC | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996
5_CC | Fauquier, VA | 5 | CC | n/a | [7 empty] | 1500000 | 1537500 | 1575937.5 | 1615335.9375 | 1655719.3359 | 1697112.3193 | 1739540.1273 | 1783028.6305 | 1827604.3463 | 1873294.4549 | 1920126.8163 | 1968129.9867 | 2017333.2364 | 2067766.5673 | 2119460.7315 | 2172447.2497 | 2226758.431 | 2282427.3918 | 2339488.0766 | 2397975.2785 | 2457924.6604 | 2519372.7769 | 2582357.0964 | 2646916.0238 | 2713088.9244 | 2780916.1475 | 2850439.0512 | 2921700.0274 | 2994742.5281 | 3069611.0913 | 3146351.3686 | 3225010.1528 | 3305635.4067 | 3388276.2918 | 3472983.1991 | 3559807.7791 | 3648802.9736 | 3740023.0479 | 3833523.6241 | 3929361.7147 | 4027595.7576 | 4128285.6515 | 4231492.7928 | 4337280.1126 | 4445712.1154 | 4556854.9183 | 4670776.2913 | 4787545.6986 | 4907234.341 | 5029915.1996

## EPC Estimates
Construction Assumptions
[13 empty] | CONE Area >>> | 3
[13 empty] | Technology >>> | CC
[13 empty] | Single Fuel (Only in Area 3) >>> | Yes
[13 empty] | SCR >> | Include SCR
3_CC_SF_Y | [8 empty] | EPC Total Cost ($m) = | 467.6318
3_CC_SF_Y | [8 empty] | Owner's Total Cost ($m) = | 58.5574
EPC Costs
[10 empty] | Area | Technology | Single/Dual Fuel | SCR | EPC Cost | EPC Cost | OFE (EPC Share)
[5 empty] | Tab | Line Item | Index | Match | [5 empty] | ($m) | ($m) | ($m)
1_CT_DF_N | 2x0 | DF | 1 |  | '2x0 DF 1'! | PROJECT TOTAL REVENUE | U:U | C:C | Middlesex, NJ | 1 | CT | DF | N | 205.0621 | 126.0121 | 79.05
2_CT_DF_N | 2x0 | DF | 2 |  | '2x0 DF 2'! | PROJECT TOTAL REVENUE | U:U | C:C | Charles County, MD | 2 | CT | DF | N | 183.2036 | 104.1536 | 79.05
3_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CT | DF | N | 202.7598 | 123.7098 | 79.05
3_CT_SF_N | 2x0 | SF | 3 |  | '2x0 SF 3'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CT | SF | N | 185.9376 | 109.4376 | 76.5
4_CT_DF_N | 2x0 | DF | 4 |  | '2x0 DF 4'! | PROJECT TOTAL REVENUE | U:U | C:C | Northampton, PA | 4 | CT | DF | N | 197.7669 | 118.7169 | 79.05
5_CT_DF_N | 2x0 | DF | 5 |  | '2x0 DF 5'! | PROJECT TOTAL REVENUE | U:U | C:C | Fauquier, VA | 5 | CT | DF | N | 183.0393 | 103.9893 | 79.05
' '!
1_CT_DF_Y | 2x0 | DF | 1 | SCR | '2x0 DF 1 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Middlesex, NJ | 1 | CT | DF | Y | 226.8021 | 130.5521 | 96.25
2_CT_DF_Y | 2x0 | DF | 2 | SCR | '2x0 DF 2 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Charles County, MD | 2 | CT | DF | Y | 201.2411 | 104.9911 | 96.25
3_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CT | DF | Y | 224.526 | 128.276 | 96.25
3_CT_SF_Y | 2x0 | SF | 3 | SCR | '2x0 SF 3 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CT | SF | Y | 207.2722 | 113.5722 | 93.7
4_CT_DF_Y | 2x0 | DF | 4 | SCR | '2x0 DF 4 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Northampton, PA | 4 | CT | DF | Y | 219.2953 | 123.0453 | 96.25
5_CT_DF_Y | 2x0 | DF | 5 | SCR | '2x0 DF 5 SCR'! | PROJECT TOTAL REVENUE | U:U | C:C | Fauquier, VA | 5 | CT | DF | Y | 201.0102 | 104.7602 | 96.25
' '!
1_CC_DF_Y | 2x1 | DF | 1 | SCR | '2x1 DF 1'! | PROJECT TOTAL REVENUE | U:U | C:C | Middlesex, NJ | 1 | CC | DF | Y | 491.4369 | 356.1869 | 135.25
2_CC_DF_Y | 2x1 | DF | 2 | SCR | '2x1 DF 2'! | PROJECT TOTAL REVENUE | U:U | C:C | Charles County, MD | 2 | CC | DF | Y | 409.816 | 274.566 | 135.25
3_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CC | DF | Y | 483.6275 | 348.3775 | 135.25
3_CC_SF_Y | 2x1 | SF | 3 | SCR | '2x1 SF 3'! | PROJECT TOTAL REVENUE | U:U | C:C | Will, IL | 3 | CC | SF | Y | 467.6318 | 334.9318 | 132.7
4_CC_DF_Y | 2x1 | DF | 4 | SCR | '2x1 DF 4'! | PROJECT TOTAL REVENUE | U:U | C:C | Northampton, PA | 4 | CC | DF | Y | 468.6976 | 333.4476 | 135.25
5_CC_DF_Y | 2x1 | DF | 5 | SCR | '2x1 DF 5'! | PROJECT TOTAL REVENUE | U:U | C:C | Fauquier, VA | 5 | CC | DF | Y | 409.6239 | 274.3739 | 135.25
Owner's Costs
[10 empty] | Area | Technology | Single/Dual Fuel | SCR | Owner's Cost | EPC Estimate
[14 empty] | ($m) | ($)
1_CT_DF_N | [8 empty] | Middlesex, NJ | 1 | CT | DF | N | 22.9934 | 22993367
2_CT_DF_N | [8 empty] | Charles County, MD | 2 | CT | DF | N | 21.6927 | 21692702
3_CT_DF_N | [8 empty] | Will, IL | 3 | CT | DF | N | 22.993 | 22992993
3_CT_SF_N | [8 empty] | Will, IL | 3 | CT | SF | N | 22.0137 | 22013712
4_CT_DF_N | [8 empty] | Northampton, PA | 4 | CT | DF | N | 21.7029 | 21702855
5_CT_DF_N | [8 empty] | Fauquier, VA | 5 | CT | DF | N | 20.4023 | 20402320
1_CT_DF_Y | [8 empty] | Middlesex, NJ | 1 | CT | DF | Y | 28.6141 | 28614072
2_CT_DF_Y | [8 empty] | Charles County, MD | 2 | CT | DF | Y | 27.1215 | 27121532
3_CT_DF_Y | [8 empty] | Will, IL | 3 | CT | DF | Y | 28.6137 | 28613686
3_CT_SF_Y | [8 empty] | Will, IL | 3 | CT | SF | Y | 27.6231 | 27623142
4_CT_DF_Y | [8 empty] | Northampton, PA | 4 | CT | DF | Y | 27.1349 | 27134930
5_CT_DF_Y | [8 empty] | Fauquier, VA | 5 | CT | DF | Y | 25.643 | 25643014
1_CC_DF_Y | [8 empty] | Middlesex, NJ | 1 | CC | DF | Y | 59.5356 | 59535565
2_CC_DF_Y | [8 empty] | Charles County, MD | 2 | CC | DF | Y | 56.8116 | 56811631
3_CC_DF_Y | [8 empty] | Will, IL | 3 | CC | DF | Y | 59.5345 | 59534480
3_CC_SF_Y | [8 empty] | Will, IL | 3 | CC | SF | Y | 58.5574 | 58557369
4_CC_DF_Y | [8 empty] | Northampton, PA | 4 | CC | DF | Y | 56.8561 | 56856147
5_CC_DF_Y | [8 empty] | Fauquier, VA | 5 | CC | DF | Y | 54.1347 | 54134692

## Cash Flow
B10:B100
Construction Assumptions
[11 empty] | CONE Area >>> | 3
[11 empty] | Technology >>> | CC
[11 empty] | Single Fuel (Only in Area 3) >>> | Yes
[11 empty] | SCR >> | Include SCR
Month
[14 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
3_CC_SF_Y | [12 empty] | EPC Cash Flow = | 0% | 0% | 0% | 0% | 0% | 0% | 4.414% | 3.287% | 1.684% | 1.949% | 3.535% | 2.802% | 2.993% | 3.116% | 4.778% | 3.458% | 4.375% | 3.917% | 6.917% | 4.743% | 2.675% | 3.715% | 3.822% | 3.158% | 3.711% | 4.003% | 4.003% | 3.49% | 3.309% | 3.218% | 2.735% | 2.131% | 1.557% | 1.315% | 1.013% | 0.983% | 0.741% | 0.228% | 2.226% | 0%
3_CC_SF_Y | [12 empty] | OFE and EPC Sales Taxes Passed Through Cash Flow = | 0% | 31.61% | 0% | 0% | 26.22% | 15.81% | 0.03% | 0.58% | 1.86% | 0.89% | 0.91% | 1.69% | 0.99% | 0.98% | 1.06% | 1.57% | 1.11% | 1.13% | 1.15% | 2.77% | 1.59% | 0.58% | 0.57% | 0.52% | 0.61% | 0.62% | 0.59% | 0.49% | 0.54% | 0.48% | 0.43% | 0.41% | 0.26% | 0.22% | 0.19% | 0.18% | 0.15% | 0.11% | 1.08% | 0%
3_CC_SF_Y | [12 empty] | Months to Completion = | Month 1: 39
EPC Cash Flow
[9 empty] | Area | Technology | Single/Dual Fuel | SCR | Mon. Until | Month 1: Month
[5 empty] | Tab | Index | Match | [5 empty] | Completion | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
1_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | D:D | B:B | Middlesex, NJ | 1 | CT | DF | N | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.336% | 2.675% | 2.967% | 3.154% | 3.137% | 2.936% | 3.132% | 3.785% | 3.941% | 4.617% | 4.481% | 4.739% | 12.72% | 2.903% | 3.69% | 4.824% | 4.165% | 5.054% | 4.313% | 3.869% | 3.706% | 2.489% | 1.725% | 1.429% | 1.01% | 0.419% | 2.782% | 0% | 0% | 0% | 0% | 0% | 0%
2_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | D:D | B:B | Charles County, MD | 2 | CT | DF | N | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.336% | 2.675% | 2.967% | 3.154% | 3.137% | 2.936% | 3.132% | 3.785% | 3.941% | 4.617% | 4.481% | 4.739% | 12.72% | 2.903% | 3.69% | 4.824% | 4.165% | 5.054% | 4.313% | 3.869% | 3.706% | 2.489% | 1.725% | 1.429% | 1.01% | 0.419% | 2.782% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | D:D | B:B | Will, IL | 3 | CT | DF | N | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.336% | 2.675% | 2.967% | 3.154% | 3.137% | 2.936% | 3.132% | 3.785% | 3.941% | 4.617% | 4.481% | 4.739% | 12.72% | 2.903% | 3.69% | 4.824% | 4.165% | 5.054% | 4.313% | 3.869% | 3.706% | 2.489% | 1.725% | 1.429% | 1.01% | 0.419% | 2.782% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_SF_N | 2x0 | SF | 3 |  | '2x0 SF 3 CF'! | D:D | B:B | Will, IL | 3 | CT | SF | N | 30 | 0% | 0% | 0% | 0% | 0% | 0% | 2.935% | 2.701% | 3.045% | 3.295% | 3.256% | 3.138% | 3.678% | 4.213% | 4.511% | 5.785% | 5.301% | 5.632% | 6.031% | 14.29% | 5.256% | 5.111% | 4.622% | 4.593% | 3.758% | 2.475% | 1.519% | 1.356% | 0.563% | 2.934% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
4_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | D:D | B:B | Northampton, PA | 4 | CT | DF | N | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.336% | 2.675% | 2.967% | 3.154% | 3.137% | 2.936% | 3.132% | 3.785% | 3.941% | 4.617% | 4.481% | 4.739% | 12.72% | 2.903% | 3.69% | 4.824% | 4.165% | 5.054% | 4.313% | 3.869% | 3.706% | 2.489% | 1.725% | 1.429% | 1.01% | 0.419% | 2.782% | 0% | 0% | 0% | 0% | 0% | 0%
5_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | D:D | B:B | Fauquier, VA | 5 | CT | DF | N | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.336% | 2.675% | 2.967% | 3.154% | 3.137% | 2.936% | 3.132% | 3.785% | 3.941% | 4.617% | 4.481% | 4.739% | 12.72% | 2.903% | 3.69% | 4.824% | 4.165% | 5.054% | 4.313% | 3.869% | 3.706% | 2.489% | 1.725% | 1.429% | 1.01% | 0.419% | 2.782% | 0% | 0% | 0% | 0% | 0% | 0%
1_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | D:D | B:B | Middlesex, NJ | 1 | CT | DF | Y | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.92% | 2.419% | 2.691% | 2.863% | 2.79% | 2.572% | 4.619% | 3.2% | 5.383% | 3.846% | 5.933% | 3.936% | 12.46% | 3.404% | 3.07% | 4.088% | 3.708% | 4.499% | 4.568% | 3.422% | 4.06% | 2.8% | 2.275% | 1.367% | 1.391% | 0.866% | 2.852% | 0% | 0% | 0% | 0% | 0% | 0%
2_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | D:D | B:B | Charles County, MD | 2 | CT | DF | Y | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.92% | 2.419% | 2.691% | 2.863% | 2.79% | 2.572% | 4.619% | 3.2% | 5.383% | 3.846% | 5.933% | 3.936% | 12.46% | 3.404% | 3.07% | 4.088% | 3.708% | 4.499% | 4.568% | 3.422% | 4.06% | 2.8% | 2.275% | 1.367% | 1.391% | 0.866% | 2.852% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | D:D | B:B | Will, IL | 3 | CT | DF | Y | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.92% | 2.419% | 2.691% | 2.863% | 2.79% | 2.572% | 4.619% | 3.2% | 5.383% | 3.846% | 5.933% | 3.936% | 12.46% | 3.404% | 3.07% | 4.088% | 3.708% | 4.499% | 4.568% | 3.422% | 4.06% | 2.8% | 2.275% | 1.367% | 1.391% | 0.866% | 2.852% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_SF_Y | 2x0 | SF | 3 | SCR | '2x0 SF 3 SCR CF'! | D:D | B:B | Will, IL | 3 | CT | SF | Y | 30 | 0% | 0% | 0% | 0% | 0% | 0% | 2.732% | 2.441% | 2.742% | 2.946% | 2.793% | 2.664% | 3.012% | 5.503% | 3.714% | 7.167% | 4.464% | 7.019% | 5.549% | 13.32% | 5.818% | 4.218% | 4.761% | 4.308% | 4.264% | 3.019% | 1.956% | 1.435% | 1.141% | 3.013% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
4_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | D:D | B:B | Northampton, PA | 4 | CT | DF | Y | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.92% | 2.419% | 2.691% | 2.863% | 2.79% | 2.572% | 4.619% | 3.2% | 5.383% | 3.846% | 5.933% | 3.936% | 12.46% | 3.404% | 3.07% | 4.088% | 3.708% | 4.499% | 4.568% | 3.422% | 4.06% | 2.8% | 2.275% | 1.367% | 1.391% | 0.866% | 2.852% | 0% | 0% | 0% | 0% | 0% | 0%
5_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | D:D | B:B | Fauquier, VA | 5 | CT | DF | Y | 34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.92% | 2.419% | 2.691% | 2.863% | 2.79% | 2.572% | 4.619% | 3.2% | 5.383% | 3.846% | 5.933% | 3.936% | 12.46% | 3.404% | 3.07% | 4.088% | 3.708% | 4.499% | 4.568% | 3.422% | 4.06% | 2.8% | 2.275% | 1.367% | 1.391% | 0.866% | 2.852% | 0% | 0% | 0% | 0% | 0% | 0%
1_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | D:D | B:B | Middlesex, NJ | 1 | CC | DF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.434% | 3.212% | 1.666% | 1.931% | 3.474% | 2.785% | 2.975% | 3.1% | 4.729% | 3.447% | 4.344% | 3.914% | 6.914% | 4.689% | 2.696% | 3.734% | 3.856% | 3.186% | 3.736% | 4.039% | 4.039% | 3.521% | 3.339% | 3.247% | 2.759% | 2.15% | 1.571% | 1.327% | 1.022% | 0.992% | 0.748% | 0.23% | 2.191% | 0%
2_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | D:D | B:B | Charles County, MD | 2 | CC | DF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.434% | 3.212% | 1.666% | 1.931% | 3.474% | 2.785% | 2.975% | 3.1% | 4.729% | 3.447% | 4.344% | 3.914% | 6.914% | 4.689% | 2.696% | 3.734% | 3.856% | 3.186% | 3.736% | 4.039% | 4.039% | 3.521% | 3.339% | 3.247% | 2.759% | 2.15% | 1.571% | 1.327% | 1.022% | 0.992% | 0.748% | 0.23% | 2.191% | 0%
3_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | D:D | B:B | Will, IL | 3 | CC | DF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.434% | 3.212% | 1.666% | 1.931% | 3.474% | 2.785% | 2.975% | 3.1% | 4.729% | 3.447% | 4.344% | 3.914% | 6.914% | 4.689% | 2.696% | 3.734% | 3.856% | 3.186% | 3.736% | 4.039% | 4.039% | 3.521% | 3.339% | 3.247% | 2.759% | 2.15% | 1.571% | 1.327% | 1.022% | 0.992% | 0.748% | 0.23% | 2.191% | 0%
3_CC_SF_Y | 2x1 | SF | 3 | SCR | '2x1 SF 3 CF'! | D:D | B:B | Will, IL | 3 | CC | SF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.414% | 3.287% | 1.684% | 1.949% | 3.535% | 2.802% | 2.993% | 3.116% | 4.778% | 3.458% | 4.375% | 3.917% | 6.917% | 4.743% | 2.675% | 3.715% | 3.822% | 3.158% | 3.711% | 4.003% | 4.003% | 3.49% | 3.309% | 3.218% | 2.735% | 2.131% | 1.557% | 1.315% | 1.013% | 0.983% | 0.741% | 0.228% | 2.226% | 0%
4_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | D:D | B:B | Northampton, PA | 4 | CC | DF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.434% | 3.212% | 1.666% | 1.931% | 3.474% | 2.785% | 2.975% | 3.1% | 4.729% | 3.447% | 4.344% | 3.914% | 6.914% | 4.689% | 2.696% | 3.734% | 3.856% | 3.186% | 3.736% | 4.039% | 4.039% | 3.521% | 3.339% | 3.247% | 2.759% | 2.15% | 1.571% | 1.327% | 1.022% | 0.992% | 0.748% | 0.23% | 2.191% | 0%
5_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | D:D | B:B | Fauquier, VA | 5 | CC | DF | Y | 39 | 0% | 0% | 0% | 0% | 0% | 0% | 4.434% | 3.212% | 1.666% | 1.931% | 3.474% | 2.785% | 2.975% | 3.1% | 4.729% | 3.447% | 4.344% | 3.914% | 6.914% | 4.689% | 2.696% | 3.734% | 3.856% | 3.186% | 3.736% | 4.039% | 4.039% | 3.521% | 3.339% | 3.247% | 2.759% | 2.15% | 1.571% | 1.327% | 1.022% | 0.992% | 0.748% | 0.23% | 2.191% | 0%
OFE and EPC Sales Taxes Passed Through Cash Flow
[9 empty] | Area | Technology | Single/Dual Fuel | SCR |  | Month 1: Month
[5 empty] | Tab | Index | Match | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
1_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | H:H | B:B | Middlesex, NJ | 1 | CT | DF | N | 34 | 0% | 0% | 43.28% | 0% | 21.64% | 0% | 0% | 1.45% | 1.5% | 1.54% | 1.58% | 1.62% | 1.67% | 1.69% | 1.75% | 1.86% | 1.83% | 1.86% | 2.09% | 6.35% | 0.8% | 0.66% | 0.76% | 0.84% | 0.62% | 0.73% | 0.58% | 0.47% | 0.41% | 0.27% | 0.27% | 0.21% | 0.15% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0%
2_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | H:H | B:B | Charles County, MD | 2 | CT | DF | N | 34 | 0% | 0% | 43.28% | 0% | 21.64% | 0% | 0% | 1.45% | 1.5% | 1.54% | 1.58% | 1.62% | 1.67% | 1.69% | 1.75% | 1.86% | 1.83% | 1.86% | 2.09% | 6.35% | 0.8% | 0.66% | 0.76% | 0.84% | 0.62% | 0.73% | 0.58% | 0.47% | 0.41% | 0.27% | 0.27% | 0.21% | 0.15% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | H:H | B:B | Will, IL | 3 | CT | DF | N | 34 | 0% | 0% | 43.28% | 0% | 21.64% | 0% | 0% | 1.45% | 1.5% | 1.54% | 1.58% | 1.62% | 1.67% | 1.69% | 1.75% | 1.86% | 1.83% | 1.86% | 2.09% | 6.35% | 0.8% | 0.66% | 0.76% | 0.84% | 0.62% | 0.73% | 0.58% | 0.47% | 0.41% | 0.27% | 0.27% | 0.21% | 0.15% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_SF_N | 2x0 | SF | 3 |  | '2x0 SF 3 CF'! | H:H | B:B | Will, IL | 3 | CT | SF | N | 30 | 0% | 0% | 43.75% | 0% | 21.87% | 0% | 0.04% | 1.54% | 1.56% | 1.61% | 1.7% | 1.68% | 1.75% | 1.89% | 1.88% | 1.91% | 2.18% | 2.17% | 2.12% | 6.59% | 0.77% | 0.65% | 0.74% | 0.58% | 0.45% | 0.36% | 0.26% | 0.24% | 0.19% | 1.51% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
4_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | H:H | B:B | Northampton, PA | 4 | CT | DF | N | 34 | 0% | 0% | 43.28% | 0% | 21.64% | 0% | 0% | 1.45% | 1.5% | 1.54% | 1.58% | 1.62% | 1.67% | 1.69% | 1.75% | 1.86% | 1.83% | 1.86% | 2.09% | 6.35% | 0.8% | 0.66% | 0.76% | 0.84% | 0.62% | 0.73% | 0.58% | 0.47% | 0.41% | 0.27% | 0.27% | 0.21% | 0.15% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0%
5_CT_DF_N | 2x0 | DF | 3 |  | '2x0 DF 3 CF'! | H:H | B:B | Fauquier, VA | 5 | CT | DF | N | 34 | 0% | 0% | 43.28% | 0% | 21.64% | 0% | 0% | 1.45% | 1.5% | 1.54% | 1.58% | 1.62% | 1.67% | 1.69% | 1.75% | 1.86% | 1.83% | 1.86% | 2.09% | 6.35% | 0.8% | 0.66% | 0.76% | 0.84% | 0.62% | 0.73% | 0.58% | 0.47% | 0.41% | 0.27% | 0.27% | 0.21% | 0.15% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0%
1_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | H:H | B:B | Middlesex, NJ | 1 | CT | DF | Y | 34 | 0% | 0% | 34.78% | 0% | 17.39% | 0% | 0% | 1.17% | 1.2% | 1.23% | 1.26% | 1.29% | 17.41% | 2.39% | 1.38% | 2.52% | 1.45% | 2.52% | 1.64% | 5.59% | 1.13% | 0.49% | 0.57% | 0.62% | 0.46% | 0.54% | 0.43% | 0.35% | 0.3% | 0.2% | 0.2% | 0.16% | 0.11% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0%
2_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | H:H | B:B | Charles County, MD | 2 | CT | DF | Y | 34 | 0% | 0% | 34.78% | 0% | 17.39% | 0% | 0% | 1.17% | 1.2% | 1.23% | 1.26% | 1.29% | 17.41% | 2.39% | 1.38% | 2.52% | 1.45% | 2.52% | 1.64% | 5.59% | 1.13% | 0.49% | 0.57% | 0.62% | 0.46% | 0.54% | 0.43% | 0.35% | 0.3% | 0.2% | 0.2% | 0.16% | 0.11% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | H:H | B:B | Will, IL | 3 | CT | DF | Y | 34 | 0% | 0% | 34.78% | 0% | 17.39% | 0% | 0% | 1.17% | 1.2% | 1.23% | 1.26% | 1.29% | 17.41% | 2.39% | 1.38% | 2.52% | 1.45% | 2.52% | 1.64% | 5.59% | 1.13% | 0.49% | 0.57% | 0.62% | 0.46% | 0.54% | 0.43% | 0.35% | 0.3% | 0.2% | 0.2% | 0.16% | 0.11% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0%
3_CT_SF_Y | 2x0 | SF | 3 | SCR | '2x0 SF 3 SCR CF'! | H:H | B:B | Will, IL | 3 | CT | SF | Y | 30 | 0% | 0% | 34.86% | 0% | 17.43% | 0% | 0.03% | 1.22% | 1.24% | 1.27% | 1.34% | 1.32% | 18.03% | 2.56% | 1.47% | 2.58% | 1.68% | 2.76% | 1.64% | 5.74% | 1.11% | 0.47% | 0.54% | 0.42% | 0.33% | 0.26% | 0.19% | 0.17% | 0.14% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
4_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | H:H | B:B | Northampton, PA | 4 | CT | DF | Y | 34 | 0% | 0% | 34.78% | 0% | 17.39% | 0% | 0% | 1.17% | 1.2% | 1.23% | 1.26% | 1.29% | 17.41% | 2.39% | 1.38% | 2.52% | 1.45% | 2.52% | 1.64% | 5.59% | 1.13% | 0.49% | 0.57% | 0.62% | 0.46% | 0.54% | 0.43% | 0.35% | 0.3% | 0.2% | 0.2% | 0.16% | 0.11% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0%
5_CT_DF_Y | 2x0 | DF | 3 | SCR | '2x0 DF 3 SCR CF'! | H:H | B:B | Fauquier, VA | 5 | CT | DF | Y | 34 | 0% | 0% | 34.78% | 0% | 17.39% | 0% | 0% | 1.17% | 1.2% | 1.23% | 1.26% | 1.29% | 17.41% | 2.39% | 1.38% | 2.52% | 1.45% | 2.52% | 1.64% | 5.59% | 1.13% | 0.49% | 0.57% | 0.62% | 0.46% | 0.54% | 0.43% | 0.35% | 0.3% | 0.2% | 0.2% | 0.16% | 0.11% | 1.2% | 0% | 0% | 0% | 0% | 0% | 0%
1_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | H:H | B:B | Middlesex, NJ | 1 | CC | DF | Y | 39 | 0% | 31.63% | 0% | 0% | 25.79% | 15.82% | 0.03% | 0.59% | 1.86% | 0.9% | 0.92% | 1.69% | 1% | 0.99% | 1.07% | 1.58% | 1.12% | 1.15% | 1.17% | 2.81% | 1.59% | 0.6% | 0.59% | 0.54% | 0.64% | 0.64% | 0.61% | 0.51% | 0.55% | 0.5% | 0.45% | 0.42% | 0.27% | 0.23% | 0.2% | 0.19% | 0.16% | 0.11% | 1.08% | 0%
2_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | H:H | B:B | Charles County, MD | 2 | CC | DF | Y | 39 | 0% | 31.63% | 0% | 0% | 25.79% | 15.82% | 0.03% | 0.59% | 1.86% | 0.9% | 0.92% | 1.69% | 1% | 0.99% | 1.07% | 1.58% | 1.12% | 1.15% | 1.17% | 2.81% | 1.59% | 0.6% | 0.59% | 0.54% | 0.64% | 0.64% | 0.61% | 0.51% | 0.55% | 0.5% | 0.45% | 0.42% | 0.27% | 0.23% | 0.2% | 0.19% | 0.16% | 0.11% | 1.08% | 0%
3_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | H:H | B:B | Will, IL | 3 | CC | DF | Y | 39 | 0% | 31.63% | 0% | 0% | 25.79% | 15.82% | 0.03% | 0.59% | 1.86% | 0.9% | 0.92% | 1.69% | 1% | 0.99% | 1.07% | 1.58% | 1.12% | 1.15% | 1.17% | 2.81% | 1.59% | 0.6% | 0.59% | 0.54% | 0.64% | 0.64% | 0.61% | 0.51% | 0.55% | 0.5% | 0.45% | 0.42% | 0.27% | 0.23% | 0.2% | 0.19% | 0.16% | 0.11% | 1.08% | 0%
3_CC_SF_Y | 2x1 | SF | 3 | SCR | '2x1 SF 3 CF'! | H:H | B:B | Will, IL | 3 | CC | SF | Y | 39 | 0% | 31.61% | 0% | 0% | 26.22% | 15.81% | 0.03% | 0.58% | 1.86% | 0.89% | 0.91% | 1.69% | 0.99% | 0.98% | 1.06% | 1.57% | 1.11% | 1.13% | 1.15% | 2.77% | 1.59% | 0.58% | 0.57% | 0.52% | 0.61% | 0.62% | 0.59% | 0.49% | 0.54% | 0.48% | 0.43% | 0.41% | 0.26% | 0.22% | 0.19% | 0.18% | 0.15% | 0.11% | 1.08% | 0%
4_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | H:H | B:B | Northampton, PA | 4 | CC | DF | Y | 39 | 0% | 31.63% | 0% | 0% | 25.79% | 15.82% | 0.03% | 0.59% | 1.86% | 0.9% | 0.92% | 1.69% | 1% | 0.99% | 1.07% | 1.58% | 1.12% | 1.15% | 1.17% | 2.81% | 1.59% | 0.6% | 0.59% | 0.54% | 0.64% | 0.64% | 0.61% | 0.51% | 0.55% | 0.5% | 0.45% | 0.42% | 0.27% | 0.23% | 0.2% | 0.19% | 0.16% | 0.11% | 1.08% | 0%
5_CC_DF_Y | 2x1 | DF | 3 | SCR | '2x1 DF 3 CF'! | H:H | B:B | Fauquier, VA | 5 | CC | DF | Y | 39 | 0% | 31.63% | 0% | 0% | 25.79% | 15.82% | 0.03% | 0.59% | 1.86% | 0.9% | 0.92% | 1.69% | 1% | 0.99% | 1.07% | 1.58% | 1.12% | 1.15% | 1.17% | 2.81% | 1.59% | 0.6% | 0.59% | 0.54% | 0.64% | 0.64% | 0.61% | 0.51% | 0.55% | 0.5% | 0.45% | 0.42% | 0.27% | 0.23% | 0.2% | 0.19% | 0.16% | 0.11% | 1.08% | 0%

## Additional Estimates
|  | Technology >> | CC
|  | CONE Area >> | 3
|  | SCR >> | Y
State Tax Rates
| State | Cone Area | Rate
| IL | 3 | 9.5%
| MD | 2 | 8.25%
| NJ | 1 | 9%
| PA | 4 | 9.99%
| VA | 5 | 6%
Land Costs
[6 empty] | CT | CC
|  | Cone Area | Land Price ($/acre) | CT Acreage | CC Acreage | CT Land Cost ($m) | CC Land Cost ($m)
|  |  | [1] | [2] | [3] | [4] | [5]
| Middlesex, NJ | 1 | 129000 | 30 | 40 | 3.87 | 5.16
| Charles County, MD | 2 | 120000 | 30 | 40 | 3.6 | 4.8
| Will, IL | 3 | 80000 | 30 | 40 | 2.4 | 3.2
| Northampton, PA | 4 | 90000 | 30 | 40 | 2.7 | 3.6
| Fauquier, VA | 5 | 118000 | 30 | 40 | 3.54 | 4.72
Property Taxes
[5 empty] | CT | CC
|  | Cone Area | Property Tax on Land | Property Tax on Plant | CT Property Tax | CC Property Tax
|  |  | (%) | ($/MW-yr) | ($/yr) | ($/yr)
| Middlesex, NJ | 1 | 4.25% | 0 | 164475 | 219300
| Charles County, MD | 2 | 1.14% | 831 | 390060 | 637251
| Will, IL | 3 | 1.715% | 0 | 41163.227 | 54884.3027
| Northampton, PA | 4 | 3.02% | 135 | 138240 | 203355
| Fauquier, VA | 5 | 0% | 0 | 0 | 0
Electric Interconnection
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | ($m) | ($m)
| Middlesex, NJ | 1 | 11 | 15.5
| Charles County, MD | 2 | 11 | 15.5
| Will, IL | 3 | 11 | 15.5
| Northampton, PA | 4 | 11 | 15.5
| Fauquier, VA | 5 | 11 | 15.5
Gas Interconnection
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | ($m) | ($m)
| Middlesex, NJ | 1 | 16 | 16
| Charles County, MD | 2 | 16 | 16
| Will, IL | 3 | 16 | 16
| Northampton, PA | 4 | 16 | 16
| Fauquier, VA | 5 | 16 | 16
O&M Mobilization Costs
|  |  | CT_Y | CT_N | CC_
|  | Cone Area | Gas CT w/ SCR | Gas CT w/o SCR | Gas CC
|  |  | ($m) | ($m) | ($m)
| Middlesex, NJ | 1 | 1.1606 | 1.0223 | 2.8892
| Charles County, MD | 2 | 1.1083 | 0.98259 | 2.7066 |  |  | `
| Will, IL | 3 | 1.1313 | 0.99465 | 2.7762
| Northampton, PA | 4 | 1.093 | 0.96149 | 2.638
| Fauquier, VA | 5 | 1.0931 | 0.9726 | 2.6335
Plant Size
| Technology | Fuel | SCR | Plant Size
(MW)
CT_DF_Y | CT | DF | Y | 389.608
CT_DF_N | CT | DF | N | 392.008
CT_SF_Y | CT | SF | Y | 389.608
CT_SF_N | CT | SF | N | 392.008
CC_DF_Y | CC | DF | Y | 655.638
CC_SF_Y | CC | SF | Y | 655.638
Project Development Costs
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | ($m) | ($m)
| Middlesex, NJ | 1 | 6 | 8
| Charles County, MD | 2 | 6 | 8
| Will, IL | 3 | 6 | 8
| Northampton, PA | 4 | 6 | 8
| Fauquier, VA | 5 | 6 | 8
Owner's Contingency
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | (% Total Plant) | (% Total Plant)
| Middlesex, NJ | 1 | 3% | 3%
| Charles County, MD | 2 | 3% | 3%
| Will, IL | 3 | 3% | 3%
| Northampton, PA | 4 | 3% | 3%
| Fauquier, VA | 5 | 3% | 3%
Financing Fees
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | (% of Overnight Borrowed) | (% of Overnight Borrowed)
| Middlesex, NJ | 1 | 2% | 2%
| Charles County, MD | 2 | 2% | 2%
| Will, IL | 3 | 2% | 2%
| Northampton, PA | 4 | 2% | 2%
| Fauquier, VA | 5 | 2% | 2%
Emissions Reduction Credits
|  |  | CT_Y | CT_N | CC_
|  | Cone Area | Gas CT w/ SCR | Gas CT w/o SCR | Gas CC
|  |  | ($m) | ($m) | ($m)
| Middlesex, NJ | 1 | 0.67727 | 2.0875 | 1.545
| Charles County, MD | 2 | 0.66261 | 1.782 | 1.315
| Will, IL | 3 | 0.68051 | 2.2126 | 1.6485
| Northampton, PA | 4 | 0.59913 | 1.8467 | 1.3739
| Fauquier, VA | 5 | 0 | 0 | 0
Startup Fuel Costs
|  |  | CT | CC
|  | Cone Area | Gas CT | Gas CC
|  |  | ($m) | ($m)
| Middlesex, NJ | 1 | 2.2071 | -2.6547
| Charles County, MD | 2 | 3.9031 | 1.6587
| Will, IL | 3 | 4.05 | 2.5559
| Northampton, PA | 4 | 3.9031 | 1.6587
| Fauquier, VA | 5 | 3.9031 | 1.6587

## Tax_depreciation
Source: | MACRS from IRS website
http://www.irs.gov/publications/p946/ar02.html
Year | 5yr MACRS | 10yr MACRS | 15yr MACRS | 20yr MACRS | 5yr SLD | 10yr SLD | 20yr SLD | 30yr SLD | 40yr SLD | 50yr SLD
1 | 35% | 17.5% | 8.75% | 6.563% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
2 | 26% | 16.5% | 9.13% | 7% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
3 | 15.6% | 13.2% | 8.21% | 6.482% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
4 | 11.01% | 10.56% | 7.39% | 5.996% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
5 | 11.01% | 8.45% | 6.65% | 5.546% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
6 | 1.38% | 6.76% | 5.99% | 5.13% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
7 | 0% | 6.55% | 5.9% | 4.746% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
8 | 0% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
9 | 0% | 6.56% | 5.9% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
10 | 0% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
11 | 0% | 0.82% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
12 | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
13 | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
14 | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
15 | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
16 | 0% | 0% | 0.74% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
17 | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
18 | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
19 | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
20 | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
21 | 0% | 0% | 0% | 0.565% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
32 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
33 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
35 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
36 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
37 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
38 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
39 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
40 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
41 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
42 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
43 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
44 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
45 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
46 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
47 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
48 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
49 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
50 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
TOTAL | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%