## 2021-2022 Parameters
2021-2022 RPM Base Residual Auction Planning Parameters |  |  | 2018-05-03
| RTO | Notes:
Installed Reserve Margin (IRM) | 15.8% | 2017 IRM Study
Pool-Wide Average EFORd | 5.89% | 2017 IRM Study
Forecast Pool Requirement (FPR) | 1.0898 | 2017 IRM Study
Preliminary Forecast Peak Load | 152647.4 | Load data: from 2018 Load Report with adjustments due to load served outside PJM.
Locational Deliverability Area
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL | DAYTON | DEOK
CETO | NA | -8870 | 2500 | 2870 | 5620 | 2410 | 1080 | 1550 | 6020 | 4100 | -640 | 4470 | -850 | 2480 | 3110
CETL | NA | 4019 | 9000 | 9082 | 6902 | 3180 | 1624 | 6915 | 8439 | 5256 | 5574 | 6005 | 6609 | 3502 | 4959
Reliability Requirement | 166355.1 | 64919 | 35994 | 15259 | 11501 | 5810 | 2907 | 8073 | 15598 | 5258 | 26112 | 7910 | 9974 | 3979 | 7557
Total Peak Load of FRR Entities | 12107.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 878.5
Preliminary FRR Obligation | 13194.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 957.4
Reliability Requirement adjusted for FRR | 153160.8 | 64919 | 35994 | 15259 | 11501 | 5810 | 2907 | 8073 | 15598 | 5258 | 26112 | 7910 | 9974 | 3979 | 7129.0422
Gross CONE, $/MW-Day (UCAP Price) | 393.91 | 392.52 | 387.61 | 410.34 | 387.61 | 387.61 | 387.61 | 410.34 | 387.24 | 387.24 | 387.24 | 410.34 | 390.46 | 387.24 | 387.24
Net CONE, $/MW-Day (UCAP Price) | 321.57 | 292.69 | 313.77 | 264.88 | 330.61 | 330.61 | 300.18 | 285.42 | 306.87 | 306.87 | 344.36 | 244.33 | 300.72 | 312.56 | 312.8
EE Addback (UCAP) | 3912.9 | 1341.9 | 932.4 | 231.2 | 377.4 | 83.8 | 17.2 | 119.1 | 254.6 | 49.9 | 843.1 | 112.1 | 104 | 110.7 | 123.4
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 482.36 | 439.04 | 470.66 | 410.34 | 495.92 | 495.92 | 450.27 | 428.13 | 460.31 | 460.31 | 516.54 | 410.34 | 451.08 | 468.84 | 469.2
Point (b) UCAP Price, $/MW-Day | 241.18 | 219.52 | 235.33 | 198.66 | 247.96 | 247.96 | 225.14 | 214.07 | 230.15 | 230.15 | 258.27 | 183.25 | 225.54 | 234.42 | 234.6
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 156809.2 | 66148.8 | 36864.2 | 15463.8 | 11858.5 | 5883.8 | 2919.2 | 8178.2 | 15825.7 | 5298.8 | 26910 | 8008.4 | 10060.8 | 4082.8 | 7240.1
Point (b) UCAP Level, MW | 160909.3 | 67886.7 | 37827.8 | 15872.3 | 12166.4 | 6039.3 | 2997 | 8394.3 | 16243.2 | 5439.6 | 27609 | 8220.2 | 10327.8 | 4189.3 | 7431
Point (c) UCAP Level, MW | 168712.9 | 71194.3 | 39661.7 | 16649.8 | 12752.4 | 6335.3 | 3145.1 | 8805.6 | 17037.9 | 5707.5 | 28939.4 | 8623.2 | 10836 | 4392.1 | 7794.2
Nominated PRD Value, MW | 510 | 510 | 75 | 435 | 0 | 0 | 35.7 | 195 | 0 | 0 | 0 | 240 | 0 | 0 | 0
VRR Curve adjusted for PRD:
Point (a1) UCAP Price, $/MW-Day | 482.36 | 439.04 | 470.66 | 410.34 |  |  | 450.27 | 428.13 |  |  |  | 410.34
Point (b1) UCAP Price, $/MW-Day | 241.18 | 219.52 | 235.33 | 198.66 |  |  | 225.14 | 214.07 |  |  |  | 183.25
Point (prd1) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (prd2) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01 |  |  |  | 0.01
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
Point (a1) UCAP Level, MW | 156253.4 | 65593 | 36782.5 | 14989.7 |  |  | 2880.3 | 7965.7 |  |  |  | 7746.8
Point (b1) UCAP Level, MW | 160353.5 | 67330.9 | 37746.1 | 15398.2 |  |  | 2958.1 | 8181.8 |  |  |  | 7958.6
Point (prd1) UCAP Level, MW | 168156.8 | 70638.3 | 39579.9 | 16175.7 |  |  | 3106.2 | 8593.1 |  |  |  | 8361.6
Point (prd2) UCAP Level, MW | 168712.6 | 71194.1 | 39661.6 | 16649.8 |  |  | 3145.1 | 8805.6 |  |  |  | 8623.2
Point (c) UCAP Level, MW | 168712.9 | 71194.3 | 39661.7 | 16649.8 |  |  | 3145.1 | 8805.6 |  |  |  | 8623.2
Pre-Auction Credit Rate, $/MW | 58686.53 | 53415.93 | 57263.03 | 48340.6 | 60336.33 | 60336.33 | 54782.85 | 52089.15 | 56003.78 | 56003.78 | 62845.7 | 44590.23 | 54881.4 | 57042.2 | 57086
Participant-Funded ICTRs Awarded | NA | 1557 | 40 | NA | 41 | 21 | 72 | NA | NA | NA | 1097 | 65.7 | NA | NA | 155
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 100% | 83.2% | 45.4% | NA | NA | NA | NA | NA | NA | 87.8% | 27.4% | NA | NA | 44.7%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO | CETL | CETL to CETO Ratio % | 2017 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load
RTO | NA | NA | NA | 146876.5 | 152647.4 | NA | 12107.1 | 140540.3
AE | 800 | >920 | > 115% | 2350 | 2308 | 0.98213 | 0 | 2308
AEP | -580 | * | * | 21940 | 22124 | 1.0084 | 11209.3 | 10914.7
APS | 2410 | >2772 | > 115% | 8260 | 8862 | 1.0729 | 0 | 8862
ATSI | 6020 | 8439 | 140.2% | 12070 | 12424 | 1.0293 | 0 | 12424
ATSI-CLEVELAND | 4100 | 5256 | 128.2% | NA | 4200.6 | NA | 0 | 4200.6
BGE | 4470 | 6005 | 134.3% | 6100 | 6386 | 1.0469 | 0 | 6386
COMED | -640 | 5574 | * | 19640 | 21458 | 1.0926 | 0 | 21458
DAYTON | 2480 | 3502 | 141.2% | 3210 | 3252 | 1.0131 | 0 | 3252
DEOK | 3110 | 4959 | 159.5% | 4970 | 5336 | 1.0736 | 878.5 | 4457.5
DLCO | 2610 | >3002 | > 115% | 2620 | 2744 | 1.0473 | 0 | 2744
DOM | -1780 | * | * | 18330 | 19330 | 1.0546 | 0 | 19330
DPL | 700 | >805 | > 115% | 3650 | 3756 | 1.029 | 0 | 3756
DPL SOUTH | 1080 | 1624 | 150.4% | NA | 2213.4 | NA | 0 | 2213.4
EKPC | 530 | >610 | > 115% | 2181.5 | 2196.4 | 1.0068 | 19.3 | 2177.1
JCPL | 3400 | >3910 | > 115% | 5570 | 5616 | 1.0083 | 0 | 5616
METED | 1210 | >1392 | > 115% | 2810 | 2867 | 1.0203 | 0 | 2867
PECO | 2460 | >2829 | > 115% | 7950 | 8351 | 1.0504 | 0 | 8351
PENLC | -330 | * | * | 2760 | 2754 | 0.99783 | 0 | 2754
PEPCO | 1550 | 6915 | 446.1% | 5850 | 6112 | 1.0448 | 0 | 6112
PL (incl. UGI) | -850 | 6609 | * | 6785 | 7029 | 1.036 | 0 | 7029
PS | 5620 | 6902 | 122.8% | 9450 | 9363 | 0.99079 | 0 | 9363
PS NORTH | 2410 | 3180 | 132% | NA | 4583.2 | NA | 0 | 4583.2
RECO | NA | NA | NA | 380 | 379 | 0.99737 | 0 | 379
EMAAC | 2500 | 9000 | 360% | NA | 29773 | NA | 0
SWMAAC | 2870 | 9082 | 316.4% | NA | 12498 | NA | 0
Western MAAC | -10440 | * | * | NA | 12650 | NA | 0
MAAC | -8870 | 4019 | * | NA | 54921 | NA | 0
Western PJM | 3860 | >4439 | * | NA | 78396.4 | NA | 12107.1
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation/Limiting Facility
MAAC | Thermal / High Ridge - Sandy Springs 230 kV for the loss of the parallel High Ridge - Sandy Springs - Burtonsville 230 kV circuit
EMAAC | Voltage / Voltage drop at Cochranville 230 kV for loss of Keeney - Rock Springs 500 kV circuit
SWMAAC | Voltage / Voltage drop at multiple BES buses for the loss of the Burchess Hill - Possum Point 500 kV circuit
PS | Thermal / Roseland - Cedar Grove 230 kV for the loss of the Roseland - Williams Pipeline 230 kV circuit; McCarter - Essex 230 kV pre- contingency
PSNORTH | Thermal / Roseland - Cedar Grove 230 kV for the loss of the Roseland - Williams Pipeline 230 kV circuit; McCarter - Essex 230 kV pre- contingency
DPLSOUTH | Thermal / Cedar Creek - Sliver Run 230 kV for loss of Cartanza - Milford 230 kV circuit
PEPCO | Voltage / Voltage drop at multiple BES buses for the loss of the Burchess Hill - Possum Point 500 kV circuit
ATSI | Thermal / South Canton - Harmon 345 kV for loss of the Sammis - Star 345 kV circuit
ATSI-CLEVELAND | Thermal / South Canton - Harmon 345 kV for loss of the Sammis - Star 345 kV circuit
COMED | Thermal / Dumont - Stillwell 345kV line for the loss of Dumont - Wilton 765 kV circuit
BGE | Voltage / Voltage drop at multiple BES buses for the loss of the Waugh Chapel 230 kV capacitor
PL | Thermal / Wescosville 500/138 kV transformer pre-contingency
DAYTON | Thermal / O.H. Hutchings - Sugarcreek 138 kV line for the loss of Sugarcreek - Centerville and Sugarcreek - Normandy 138 kV line
DEOK | Thermal / Pierce 345/138 kV transformer for loss of the Pierce - Foster 345 kV circuit; Greendale - Miami Forte 138 kV for loss of the Tanners Creek - Miami Forte 345 kV circuit
Original 2/1/2018: Reliability Requirement not adjusted for FRR load.
Revision 4/13/2018: Reliability Requirement adjusted for FRR load. Revisions made in CETO, CETL, and Reliability Requirement values as shown in red.
Revision 4/18/2018: Corrected DEOK Reliability Requirement adjusted for FRR load. OVEC zone removed as its integration is delayed. EMAAC CETO, CETL changes shown in red.
Revision 5/3/2018: VRR Curve updated to reflect adjustments for total quantity of EE Resources for which PJM accepted an EE M&V Plan submitted for the auction.

## Net CONE
RPM CONE and E&AS Values for 2021/2022 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / (1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2021/2022 |  |  |  | 5.89%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC
CONE Area 4: MetEd, Penelec, PPL
Zone/LDA | 2020/2021 BRA CONE: Levelized Revenue Requirement, $/MW-Year | BLS Composite Index: 2016/2015 Escalation | 2021/2022 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Historic (2015-2017) Net Energy Revenue Offset, $/MW-Year | Ancillary Services Offset, $/MW-Year per Tariff | Net E&AS Revenue Offset, $/MW-Year | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | LDA Modeled with VRR Curve
CONE Area 1 | 134309.8704 | 0.99132 | 133143.971 | 387.61
AE |  |  |  | 387.61 | 17585.6541 | 2199 | 19784.6541 | 310.5735 | 330.01
DPL |  |  |  | 387.61 | 27833.0118 | 2199 | 30032.0118 | 282.4985 | 300.18 | DPL SOUTH
JCPL |  |  |  | 387.61 | 29867.4724 | 2199 | 32066.4724 | 276.9247 | 294.26
PE |  |  |  | 387.61 | 27967.2596 | 2199 | 30166.2596 | 282.1307 | 299.79
PSEG |  |  |  | 387.61 | 17381.3296 | 2199 | 19580.3296 | 311.1333 | 330.61 | PS, PSEG NORTH
RECO |  |  |  | 387.61 | 18358.947 | 2199 | 20557.947 | 308.4549 | 327.76
EMAAC |  |  |  | 387.61 |  |  |  | 295.29 | 313.77 | EMAAC
CONE Area 2 | 136733.0664 | 1.0309 | 140953.3657 | 410.34
BGE |  |  |  | 410.34 | 54826.5296 | 2199 | 57025.5296 | 229.9393 | 244.33 | BGE
PEPCO |  |  |  | 410.34 | 40711.5122 | 2199 | 42910.5122 | 268.6106 | 285.42 | PEPCO
SWMAAC |  |  |  | 410.34 |  |  |  | 249.28 | 264.88 | SWMAAC
CONE Area 4 | 133464.6641 | 1.0049 | 134124.0692 | 390.46
METED |  |  |  | 390.46 | 31615.6053 | 2199 | 33814.6053 | 274.8204 | 292.02
PENELEC |  |  |  | 390.46 | 58259.9771 | 2199 | 60458.9771 | 201.8222 | 214.45
PPL |  |  |  | 390.46 | 28626.958 | 2199 | 30825.958 | 283.0085 | 300.72 | PPL
MAAC |  |  |  | 392.52 |  |  |  | 275.45 | 292.69 | MAAC
CONE Area 3 | 133413.296 | 0.99702 | 133016.3724 | 387.24
AEP |  |  |  | 387.24 | 22058.5783 | 2199 | 24257.5783 | 297.9693 | 316.62
APS |  |  |  | 387.24 | 29311.6327 | 2199 | 31510.6327 | 278.0979 | 295.5
ATSI |  |  |  | 387.24 | 25407.9788 | 2199 | 27606.9788 | 288.7929 | 306.87 | ATSI, ATSI CLEVELAND
COMED |  |  |  | 387.24 | 12528.6551 | 2199 | 14727.6551 | 324.0787 | 344.36 | COMED
DAYTON |  |  |  | 387.24 | 23450.948 | 2199 | 25649.948 | 294.1546 | 312.56 | DAYTON
DEOK |  |  |  | 387.24 | 23368.4472 | 2199 | 25567.4472 | 294.3806 | 312.8 | DEOK
DLCO |  |  |  | 387.24 | 21705.073 | 2199 | 23904.073 | 298.9378 | 317.65
DOM |  |  |  | 387.24 | 21951.2004 | 2199 | 24150.2004 | 298.2635 | 316.93
EKPC |  |  |  | 387.24 | 18097.4124 | 2199 | 20296.4124 | 308.8218 | 328.15
RTO | 134480.2242 |  | 135309.4446 | 393.91 | 22651.5644 | 2199 | 24850.5644 | 302.6271 | 321.57 | RTO

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2021/2022 model
Upgrade ID | Description | Transmission Owner
b2766.1 | Upgrade substation equipment at Conastone 500 kV (on the Peach Bottom – Conastone 500 kV circuit) to increase facility rating to 2826 MVA normal and 3525 MVA emergency | BGE
b2766.2 | Upgrade substation equipment at Peach Bottom 500 kV (on the Peach Bottom – Conastone 500 kV circuit) to increase facility rating to 2826 MVA normal and 3525 MVA emergency | PECO
b2777 | Reconductor the entire Dequine - Eugene 345 kV circuit #1 | AEP
b2828 | Install 10% reactors at Miami Fort 138 kV to limit current | DEOK
b2831.1 | Upgrade the Tanner Creek - Miami Fort 345 kV circuit (AEP portion) | AEP
b2831.2 | Upgrade the Tanner Creek - Miami Fort 345 kV circuit (DEOK portion) | DEOK
b2832 | Six wire the Kyger Creek - Sporn 345 kV circuits #1 and #2 and convert them to one circuit | AEP
b2879.1 | Replace wavetrap at the Stuart 345 kV substation | Dayton
b2930 | Upgrade capacity on E. Frankfort-University Park 345kV | ComEd
b2931 | Upgrade substation equipment at Pontiac Midpoint station to increase capacity on Pontiac-Brokaw 345 kV line. | ComEd
b2976 | Upgrade terminal equipment at Tanners Creek 345kV station. Upgrade 345kV Bus and Risers at Tanners Creek for the Dearborn circuit. | AEP
b2977.5 | Replace breaker 822 at Beckjord 138kV substation to increase the rating from Pierce to Beckjord 138kV to 603MVA. | DEOK
Y3-064 | upgrade the Pierce – Beckjord 138kV circuit (Duke Feeder 1887), conductor and/or associated equipment as required to increase the emergency rating from the existing 440MVA to 600MVA (160MW increase). | DEOK
b2972 | Reconductor limiting span of Lallendorf - Monroe 345kV (crossing of Maumee river) | ATSI
b2921 | New TVA 161kV Interconnection to TVA's East Glasgow Tap-East Glasgow 161 KV line section (~1 mile due West of Fox Hollow). Add Fox Hollow 161/69 KV 150 MVA transformer. Construct new Fox Hollow-Fox Hollow Jct 161 KV line section using 795 MCM ACSR (~1 m | EKPC
b2879.2 | Reconductor EKPC portion of the Stuart - Spurlock 345 kV line | EKPC
b2878 | Upgrade the Clifty Creek 345 kV risers | AEP
b2830 | Expand Garver 345 kV sub to include 138 kV. Install 1-345 kV breaker, 1-345/138 kV 400 MVA transformer, 6-138 kV Breakers and bus work. Connect local 138 kV circuits from Todhunter, Rockies Express, and Union. | DEOK
b2778 | Add 2nd 345/138 kV transformer at Chamberlin substation | ATSI
b2776 | Reconductor the entire Dequine - Meadow Lake 345 kV circuit #2 | AEP
b2633.1 | Build a new 230 kV transmission line between Hope Creek and Silver Run | LS POWER
b2633.5 | Add a new 500/230 kV autotransformer at Hope Creek and a new Hope Creek 230 kV substation | PSEG
b2633.10 | Interconnect the new Silver Run 230 kV substation with existing Red Lion - Cartanza and Red Lion - Cedar Creek 230 kV lines | DPL
b2633.2 | Construct a new Silver Run 230 kV substation | LS POWER
b2633.4 | Add a new 500 kV bay at Hope Creek (Expansion of Hope Creek substation) | PSEG
b2835 | Convert the R-1318 and Q1317 (Edison – Metuchen) 138 kV circuits to one 230 kV circuit | PSEG
s1455 | Rebuild line 23070 circuit between Cool Spring and Indian River 230 kV substations. All structures, conductor, and static wire will be replaced with new steel poles, conductor, and OPGW | DPL
Key Transmission Upgrades included for 2020/2021 model but not included for 2021/2022 model
Upgrade ID | Description | Transmission Owner
b2443 | Construct new underground 230kV line from Gelebe to Station C. | Dominion
b2443.3 | New 230kV Potomac River Substation Project (include PARs) | PEPCO
b2443.4 | Rebuild Glebe substation | Dominion
n4301 | Construct new bay at Deans substation and install 2 500 kV breakers for a new position to connect the X1-078 converter station. | PSEG
b2414 | Build the 2nd Summer Shade EKPC - Summer Shade TVA 161 kV circuit | EKPC
| 320 MW Firm Transmission Withdrawal Rights for HVDC line connecting Bergen (PJM) to West 49th Street (NYISO) | HTP