## Sheet1
PJM 2016 RTEP Proposal Window #2 Tracking Spreadsheet
Proposal Window: | 2016 RTEP Proposal Window 2
Window Opening Date: | 2016-06-29
Window Closing Date: | 2016-07-29
Current Spreadsheet Version | V2 |  | V2 - 2/9/2017 - Updated to include previously redacted information that was subject to a subsequent window
Project ID | Upgrade/Greenfield | Proposing Entity | Final Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2016_2-1A | Upgrade | DEO&K | 18.7 | DEO&K | 138 | N-1-1 Thermal | N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Expand Garver 345kV sub to include 138kV
2016_2-1B | Upgrade | DEO&K | 1 | DEO&K | 138 | Gen Deliv | 897, 1137 | Install 5% reactors at Miami Fort to limit current.
2016_2-1C | Upgrade | DEO&K | 10.5 | DEO&K | 138 | Gen Deliv | 907 | Reconductor circuit from Nickel to Warren. Replace wooden structures with steel poles.
2016_2-1D | Upgrade | DEO&K | 2.2 | DEO&K | 138 | N-1-1 Thermal | N2-T4, N2-T5 | Reconductor Feeder from Port Union to East Provident for 300MVA
2016_2-2A | Upgrade | ComEd | 4.59 | ComEd | 138 | Gen Deliv | 1123 | Rebuild 138 kV line 11323 for 1.6 miles from Haumesser to West Dekalb Tap with double circuit towers and install 2 twisted 556.5 ACSR conductors per phase in both circuit positions, to be operated tied together as a single circuit. Upgrade line switch and revise relay settings.
2016_2-3A | Greenfield | Transource | 58 | ATSI, AEP | 345 | Gen Deliv | 915 | Construct a new double circuit 345 kV line between ATSI's Carlisle Station and a new station, Rocky River West, along the Avon Lake-Juniper 345 kV line.
2016_2-3B | Greenfield | Transource | 36 | Penelec | 345, 500 | Gen Deliv | 1026 | Establish a 500/345kV greenfield station by cutting into the existing Keystone - Conemaugh 500kV circuit. Construct a 345kV tie line between the new station and the existing Homer City 345kV yard.
2016_2-3C | Greenfield | Transource | 19 | DEO&K, EKPC, LGEE, OVEC | 138, 345 | Gen Deliv; N-1-1 Thermal | 897, 905, 906, 907, 1137; N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Build a new 345/138 kV Station (Russ Station) which taps the Stuart (DAY) – Clinton (DAY) 345 kV line and connects to both the Hillsboro (AEP) – Clinton County (DEOK) 138 kV and Middleboro (DAY) – Hillsboro (AEP) 138 kV lines
2016_2-3D | Greenfield | Transource | 12 | ATSI, AEP | 138 | N-1 Thermal; Gen Deliv | 109; 916 | Establish a new 138kV switch station near Seneca by cutting into the Markwest - Seneca 138kV line section. Construct a new 138kV line from the new station to McCalmont station.
2016_2-3E | Greenfield | Transource | 10 | Meted, PPL | 115 | N-1-1 Thermal | N2-T1, N2-T3 | Establish 230/115kV transformation at PPL Williams Grove station. Construct double circuit 115kV line to cut into existing METED Allen - Round Top 115kV circuit.
2016_2-3F | Greenfield | Transource | 63 | DEO&K, EKPC, LGEE, OVEC | 138, 345 | Gen Deliv; N-1-1 Thermal | 897, 905, 906, 907, 1137; N2-T4, N2-T5, N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Tap the Tanners Creek – Losantville 345 kV line and build a single circuit line approximately 13.5 miles to a new 345/138 station (Coyote) next to Wiley.
2016_2-4A | Upgrade | BGE/PECO | 2 | BGE, PECO | 500 | Gen Deliv | 294, 295, 296 | Upgrade Substation Equipment at Conastone and Peach Bottom to increase facility rating to 2598 MVA normal and 2863 MVA emergency
2016_2-4B | Upgrade | BGE/PECO | 7 | BGE, PECO | 500 | Gen Deliv | 294, 295, 296 | Upgrade Substation Equipment at Conastone and Peach Bottom to increase facility rating to 2826 MVA normal and 3525 MVA emergency
2016_2-5A | Upgrade | EKPC | 2.5 | EKPC | 138 | Gen Deliv | 905, 906 | The current 5% impedance 1200A line reactor, which connects the 4SPURLOCK - 4SPUR-KENT-R and 4SPUR-KENT-R - 4KENTON 138kV line sections, will be upgraded to a 6.5% impedance 1600A line reactor. This upgrade will mitigate the 104% post-contingent overload of these line sections for the loss of the 345kV lines from Spurlock - Stuart and from Spurlock - Meldahl Dam which share a common tower. The reactor will lower the post-contingent flow to 90% LTE, providing a sufficient buffer for operations. The new limiting element is the Spurlock - Kenton 138kV line conductor.
2016_2-6A | Greenfield | Nextera | 17.1 | DEO&K | 345 | Gen Deliv; N-1-1 Thermal | 907; N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | New 345/138 kV Substation Looping in Foster - Bath 345 kV, Foster - Sugar 345 kV, and Warren - Clinton 138 kV lines
2016_2-6B | Greenfield | Nextera | 32.5 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 128, 130, 131, 134 | New 345 kV line from Eugene - Dequine
2016_2-7A | Upgrade | AEP | 2.3 | AEP | 138, 161 | Gen Deliv | 874, 875, 901, 902 | Replace Hazard XF / Sag Study Hazard - Wooton
2016_2-7B | Upgrade | AEP | 10.45 | AEP | 138, 161 | Gen Deliv | 874, 875, 901, 902 | Replace Hazard XF / Rebuild Hazard - Wooton
2016_2-7C | Upgrade | AEP | 10.1 | AEP | 138, 500 | Gen Deliv | 307, 1109, 1110 | Install second 500/138 kV transformer at Nagel station
2016_2-7D | Upgrade | AEP | 0.1 | AEP | 138 | Gen Deliv | 1152 | Sag Study of Nagel to West Kingsport 138 kV line
2016_2-7E | Upgrade | AEP | 0.1 | AEP | 138 | Gen Deliv | 150 | Sag Study of Saltville to Tazewell 138 kV line
2016_2-7F | Upgrade | AEP | 1.2 | AEP | 138 | Gen Deliv | 307, 1109, 1110 | This project proposes the installation of a 4% series reactor at Sullivan Gardens towards the Walters line.
2016_2-7G | Upgrade | AEP | 2.6 | AEP | 138 | Gen Deliv | 307, 1109, 1110 | Loop existing West Kingsport - North Bristol 138kV line into Holston 138kV bus. Presently, the subject line deadends at the Holston bus but is not electrically connected to Holston. This project proposes to establish the connection of this line effectively creating line exits to West Kingsport and North Bristol from Holston. Additionally, this proposal also includes the installation of a 4% series reactor at Sullivan Gardens towards the Walters line.
2016_2-7H | Upgrade | AEP | 33.7 | AEP | 345 | Gen Deliv | 64 | Rebuild the Dequine - Meadow Lake 345kV double circuit corridor using AEP BOLD Lattice Tower Configuration.
2016_2-7I | Greenfield | AEP | 29.1 | AEP | 345 | Gen Deliv | 64 | Construct a greenfield Dequine - Meadow Lake 345kV Circuit #3 as a single circuit line.
2016_2-7J | Upgrade | AEP | 6.6 | AEP | 345 | Gen Deliv | 64 | Reconductor the enitre Dequine - Meadow Lake 345kV circuit #2.
2016_2-7K | Upgrade | AEP | 28.1 | AEP | 345 | Gen Deliv | 64 | Rebuild the Dequine - Meadow Lake 345kV double circuit corridor using AEP Traditional Tower Configuration.
2016_2-7L | Upgrade | AEP | 113.7 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 128, 130, 131, 134 | Rebuild the Dequine - Eugene 345kV double circuit corridor using AEP BOLD Lattice Tower Configuration.
2016_2-7M | Greenfield | AEP | 99.1 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 128, 130, 131, 134 | Construct a greenfield Dequine - Eugene 345kV Circuit #2 as a single circuit line.
2016_2-7N | Upgrade | AEP | 22.19 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 128, 130, 131, 134 | Reconductor the enitre Dequine - Eugene 345kV circuit.
2016_2-7O | Upgrade | AEP | 99.3 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 128, 130, 131, 134 | Rebuild the Dequine - Eugene 345kV double circuit corridor using AEP Traditional Tower Configuration.
2016_2-7P | Greenfield | AEP | 127.6 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 64, 128, 130, 131, 134 | Construct a greenfield Eugene – Meadow Lake 345kV Circuit single circuit line ~60 miles.
2016_2-7Q | Upgrade | AEP | 0.6 | AEP | 138 | Gen Deliv | 1141 | Reconfigure New Carlisle station and install an additional 138kV bus tie breaker.
2016_2-7R | Greenfield | AEP | 24.2 | AEP | 138 | Gen Deliv | 1141 | Rebuild sections of the 34.5 kV line b/w New Carlisle and Silver Lake as double ckt 138 kV, operating one ckt as 34.5 kV while the other as 138 kV. Extend the 138 kV ckt to Liquid Carbonics by constructing a green field single ckt line.
2016_2-7S | Upgrade | AEP | 0.82 | AEP | 138 | Gen Deliv | 897, 1137 | Replace the existing reactor at Clifty Creek 138 kV with a larger one (19 Ohms).
2016_2-8A | Upgrade | First Energy | 16.1 | ATSI | 138 | Gen Deliv | 915 | Reconductor the Beaver-Black River 138kV line 336Kcmil ACSR 6wire section (~7.0miles) with 954Kcmil ACSS conductor. Upgrade the wavetrap at Black River to 2000A. New ratings SN 459MVA/SE459MVA
2016_2-8B | Upgrade | First Energy | 1.8 | ATSI | 138 | N-1-1 Voltage Magnitude | N2-VM5, N2-VM6 | Install one 138kV 50MVAR Capacitor Bank, one Capacitor switcher,one MOAB's, three CCVT, one Standard Relay panel, tap on Valley-Theiss 138 kV Line, fiber communication and assocated relay revisions at Valley & Theiss Substations.
2016_2-8C | Upgrade | First Energy | 3.8 | ATSI | 138 | N-1-1 Voltage Magnitude | N2-VM5, N2-VM6 | Add 2nd 345/138kV transformer at Chamberlin substation
2016_2-8D | Upgrade | First Energy | 0.1 | Penelec, Meted | 115 | N-1-1 Thermal | N2-T1, N2-T3 | Upgrade bus conductor Gardners substation. Upgrade bus conductor and adjust CT ratios at Carlisle Pike
2016_2-8E | Upgrade | First Energy | 0.03 | APS | 138 | N-1-1 Thermal | N2-T2 | Upgrade breaker risers and disconnect leads; Replace 500 CU breaker risers and 556 ACSR disconnect leads with 795 ACSR.
2016_2-8F | Upgrade | First Energy | 3.9 | Penelec | 115, 230 | Gen Deliv | 25, 29 | North Meshoppen 230/115kV #3 Transformer: -Replace the existing transformer with a new 168/224 MVA transformer. -Remove the existing reactor.
2016_2-8G | Upgrade | First Energy | 6.6 | Penelec | 115, 230 | Gen Deliv | 1026 | At Homer City: -Construct a new 345kV breaker string with three (3) 345kV breakers. -Move the North autotransformer connection to this new breaker string.
2016_2-8H | Upgrade | First Energy | 3.9 | Penelec | 115 | Gen Deliv | 1059 | Erie South - Four Mile 115 kV -Reconductor 4.62 miles of 636 ACSR with 636 ACSS high temperature conductor. -Replace the 636 ACSR substation conductor with new conductor exceeding the conductor rating -Replace the 795 SCCIR bus conductor
2016_2-8I | Upgrade | First Energy | 12.1 | Penelec | 230 | Gen Deliv | 90, 91, 92 | East Towanda – Canyon 230kV, Reconductor ~12.18 miles of 1033 ACSR line with 1033 ACSS high temp conductor, Upgrade 230kV disconnect switch and line drop to East Towanda at Canyon Substation, Upgrade 230kV line drop to Canyon line at East Towanda Substation
2016_2-8J | Upgrade | First Energy | 2.4 | Penelec | 230 | Gen Deliv | 1132 | At North Meshoppen: Convert the 230kV yard to a ring bus.
2016_2-8K | Upgrade | First Energy | 0.97 | APS | 138 | N-1 Thermal; Gen Deliv | 109; 916 | Replace the Breaker Risers and Wavetrap at Bredinville Substation on the Cabrey Junction terminal
2016_2-9A | Greenfield | Northeast Transmission Development | 12.5 | PECO | 500 | Gen Deliv | 294, 295, 296 | Build a 230 kV switching station ("Bookers Run") interconnecting the Muddy Run to Peach Bottom 230 kV line and the Peach Bottom Tap to Cooper 230 kV line with a series reactor
2016_2-9B | Greenfield | Northeast Transmission Development | 19.2 | PECO | 500 | Gen Deliv | 294, 295, 296 | Build a 230 kV line from the existing Graceton substation to the new 230 kV switching station ("Bookers Run") interconnecting the Muddy Run to Peach Bottom 230 kV line
2016_2-9C | Greenfield | Northeast Transmission Development | 7.4 | APS | 138 | N-1 Thermal; Gen Deliv | 109; 916 | Build a 138 kV switching station ("Butchers Run") interconnecting the Cabrey Junction to Butler 138 kV line, the Cabrey Junction to Bredinville 138 kV line, the Cabrey Junction to Cabot 138 kV line, and the Lawson to MC Calmont 138 kV line
2016_2-9D | Greenfield | Northeast Transmission Development | 23 | Penelec | 345 | Gen Deliv | 1026 | Build a 500/345 kV substation ("Chestnut Ridge") interconnecting the Keystone to Conemaugh 500 kV line to the existing Homer City 345 kV substation
2016_2-9E | Greenfield | Northeast Transmission Development | 15.8 | AEP | 138 | Gen Deliv | 1141 | Build a 345/138 kV substation ("Coffee Creek") interconnecting the Green Acres to Olive 345 kV line and the Flint Lake to Luchtman Road 138 kV line
2016_2-9F | Greenfield | Northeast Transmission Development | 13.3 | Penelec, Meted | 115 | N-1-1 Thermal | N2-T1, N2-T3 | Build a 230/115 kV substation ("Dogwood Run") interconnecting the Allen to Roundtop 115 kV line and the existing William Grove 230 kV substation
2016_2-9G | Greenfield | Northeast Transmission Development | 18.7 | Penelec, Meted | 115 | N-1-1 Thermal | N2-T1, N2-T3 | Build a 500/115 kV substation ("Dogwood Run") interconnecting the Juniata to Three Mile Island 500 kV line and the Allen to Roundtop 115 kV line
2016_2-9H | Greenfield | Northeast Transmission Development | 32.1 | Penelec | 115, 230 | Gen Deliv | 25, 29, 90, 91, 92, 1132 | Build a 230 kV line from the existing 230 kV East Towanda substation to the existing 230 kV North Meshoppen substation
2016_2-9I | Greenfield | Northeast Transmission Development | 80.5 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 64, 128, 130, 131, 134 | Build a 345 kV line from the existing 345 kV Eugene switching station to the existing 345 kV Meadow Lake switching station
2016_2-9J | Greenfield | Northeast Transmission Development | 17 | DEO&K | 138, 345 | Gen Deliv; N-1-1 Thermal | 907; N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Build a 345 kV line from the existing Garver substation to a new 345/138 kV substation ("Greentree"). Interconnect Greentree with the existing 138 kV Rockies Express substation with a new 138 kV connection.
2016_2-9K | Greenfield | Northeast Transmission Development | 19.4 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Build a 500/230 kV substation (Hubbard) interconnecting the 230 kV line from the existing 230 kV Oxbow substation that currently goes to the existing Lackawanna substation. Remove the existing 230 kV line from Hubbard-Lackawanna from service. Build a new 500 kV line from the new Hubbard substation to the Lackawanna 500 kV substation
2016_2-9L | Greenfield | Northeast Transmission Development | 29.9 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Build a 500/230 kV substation (Laurel Run) interconnecting the Lackawanna-Hopatcong 500 kV line and a new 230 kV line to a point of interconnection outside the Lackawanna Energy Center. The existing 230 kV line from the Lackawanna 230 kV substation to the point of interconnection outside the Lackawanna Energy Center will be removed from service.
2016_2-9M | Greenfield | Northeast Transmission Development | 38.2 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Build a 500/230 kV substation (Laurel Run) interconnecting the existing Lackawanna-Hopatcong 500 kV line and the existing Lackawanna-Lackawanna Energy Center 230 kV line.
2016_2-9N | Greenfield | Northeast Transmission Development | 11.5 | Penelec | 115 | Gen Deliv | 1059 | Build a 230/115 kV substation ("LeBoeuf") interconnecting the Erie South-Warren 230 kV line and the Erie South-Union City 115 kV line
2016_2-9O | Greenfield | Northeast Transmission Development | 9.3 | APS | 138 | N-1-1 Thermal | N2-T2 | Construct a double circuit 138 kV line to loop the existing 138 kV Richwood Hill to Metz transmission line into the existing 138 kV Dents Run substation
2016_2-9P | Greenfield | Northeast Transmission Development | 26.8 | PECO | 500 | Gen Deliv | 294, 295, 296 | Build a 230 kV line from the existing Muddy Run to Peach Bottom 230 kV line to a new switching station ("Orson Run") interconnecting the existing Safe Harbor to Graceton 230 kV line. Reconfigure the Muddy Run to Peach Bottom 230 kV line to have a Muddy Run to Orson Run 230 kV line and retire the remaining 230 kV line to Peach Bottom. Build a 230 kV line from the existing Peach Bottom 230 kV substation to the existing Graceton 230 kV substation
2016_2-9Q | Greenfield | Northeast Transmission Development | 13.4 | PECO | 500 | Gen Deliv | 294, 295, 296 | Build a 230 kV line from the existing Muddy Run to Peach Bottom 230 kV line to a new switching station ("Orson Run") interconnecting the existing Safe Harbor to Graceton 230 kV line. Reconfigure the Muddy Run to Peach Bottom 230 kV line to have a Muddy Run to Orson Run 230 kV line and retire the remaining 230 kV line to Peach Bottom
2016_2-9R | Greenfield | Northeast Transmission Development | 18.7 | DEO&K | 138, 345 | Gen Deliv; N-1-1 Thermal | 897, 1137; N2-T4, N2-T5, N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Build a 345/138 kV substation ("Paddys Run") interconnecting the Miami Fort to West Milton 345 kV line, the Morgan to Fairfield 138 kV line and the Willey to Fairfield 138 kV line
2016_2-9S | Greenfield | Northeast Transmission Development | 12.1 | APS | 138 | N-1 Thermal; Gen Deliv | 109; 916 | Build a 138 kV switching station ("Patterson Run") interconnecting the Bull Creek to Cabot 138 kV line, the Bull Creek to Houseville 138 kV line, the Bull Creek to Mountain Gathering 138 kV line, the Lawson to Cabot 138 kV line, the Lawson to Fawn 138 kV line, and the Lawson to MC Calmont 138 kV line
2016_2-9T | Greenfield | Northeast Transmission Development | 6.1 | DEO&K | 138 | Gen Deliv | 897, 1137 | Build a 138 kV switching station ("Ramsey") interconnecting the Clifty Creek-Northwest 138 kV line and the Madison-Madison West 138 kV line
2016_2-9U | Greenfield | Northeast Transmission Development | 12.2 | ATSI | 138 | Gen Deliv | 915 | Build a 138 kV switching station ("Middle Ridge") interconnecting the Carlisle to Concast 138 kV line and the Beaver to Johnson 138 kV line. Build a 138 kV switching station ("West Ridge") interconnecting the Carlisle to Concast 138 kV line and the Murray to Gates 138 kV line.
2016_2-9V | Greenfield | Northeast Transmission Development | 12.1 | AEP | 138 | Gen Deliv | 307, 1109, 1110, 1152 | Build a 138 kV switching station ("Sougan") interconnecting the Orebank to Holston 138 kV line, the Orebank to Wolf Hills 138 kV line, and the Indian Springs to North Bristol 138 kV line
2016_2-10A | Greenfield | Mid-Atlantic MCN | 33.5 | Penelec | 115, 230 | Gen Deliv | 25, 29, 90, 91, 92 | Build second 230 kV circuit from East Towanda to North Meshopppen.
2016_2-10B | Greenfield | Mid-Atlantic MCN | 29.5 | DEO&K | 138, 345 | Gen Deliv; N-1-1 Thermal | 907; N2-T6, N2-T7, N2-T8, N2-T9, N2-T10 | Build a new station adjacent to the existing Shaker Run substation. Split the Warren to Nickell 138 kV line to bring in and out of new station. Split the Todhunter to Foster 345 kV line to bring in and out of new station. Install a 345/138 kV transformer in the new station. Build 138 kV between existing Shaker Run and new station.
2016_2-11A | Upgrade | PSEG | 124.9 | PSEG | 230 | N-1-1 Voltage Drop | N-2-VD1, N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD8, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14, N2-VD15, N2-VD16, N2-VD17, N2-VD18, N2-VD19, N2-VD20 | Convert existing 138kV circuits between Brunswick and Metuchen to 230kV.
2016_2-11B | Upgrade | PSEG | 1.68 | PSEG | 230 | N-1-1 Voltage Drop | N-2-VD1, N2-VD2, N2-VD3, N2-VD4, N2-VD5, N2-VD6, N2-VD7, N2-VD8, N2-VD9, N2-VD10, N2-VD11, N2-VD12, N2-VD13, N2-VD14, N2-VD15, N2-VD16, N2-VD17, N2-VD18, N2-VD19, N2-VD20 | Eliminate the overhead line crossing of Fanwood-Metuchen and Deans-Linden circuits. Reconfigured circuits become Fanwood-Linden and Deans-Metuchen.
2016_2-11C | Greenfield | PSEG | 102.4 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 64, 128, 130, 131, 134 | Build a new 345kV circuit from Eugene to Meadow Lake
2016_2-11D | Greenfield | PSEG | 44.3 | DEO&K, OVEC | 138 | Gen Deliv | 897, 1137 | Build a new 345kV circuit from Ghent to East Bend
2016_2-11E | Greenfield | PSEG | 85.7 | DEO&K, OVEC | 138 | Gen Deliv | 897, 1137 | Build a new 345kV circuit from Clifty Creek to East Bend
2016_2-12A | Greenfield/Upgrade | Nipsco | 5 | AEP/NIPSCO | 138 | Gen Deliv | 1141 | Reconductor existing NIPSCO line section between AEP Bosserman and Olive substations at approximately 12 miles with 397 ACSS
2016_2-12B | Greenfield | Nipsco | 95 | AEP/NIPSCO | 345 | Gen Deliv | 1141 | New 345 kV Circuit from Michigan City to Olive at approximately 26 miles using 2-954 ACSR
2016_2-13A | Upgrade | PPL | 20.73 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Move Lackawanna Energy generation termination point from 230 kV bus to 500 kV bus at Lackawanna: Expand Lackawanna 500 kV yard to the east of the East 500 kV bus.
2016_2-13B | Upgrade | PPL | 19 | PPL, Penelec | 115, 230, 500 | Gen Deliv | 25, 29, 90,91, 92, 1042,1044 | Lackawanna 230 kV Phase Angle Regulators: Add two (2) new 230 kV 450 MVA phase angle regulators (PARs) at Lackawanna in series with the Lackawanna - Oxbow 230 kV line and a new normally open motor-operated disconnect switch in parallel with the PARs to allow for the PARs to be bypassed when necessary. The new Lackawanna PARs would have an angle range of +/- 30 degrees with 64 tap steps
2016_2-13C | Upgrade | PPL | 2.59 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Lackawanna 230 kV Series Reactors: Add two (2) new 10 ohm series reactors on the low side of the T3 and T4 500/230 kV transformers respectively. The new reactors will be in service under all normal operating conditions. Each reactor would be purchased as three single phase units.
2016_2-13D | Upgrade | PPL | 11.26 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Lackawanna 500/230 kV Transformer T3 Retermination: Substation Component: Expand Lackawanna 500 kV bus to have a third bay that includes three (3) breakers (4 MODs). Add a third breaker to bay 1 at Lackawanna 500 kV. Move the Lackawanna 500/230 kV transformer T3 to bay position on bay 1 (between existing CB-1W and new CB-1T breakers) Transmission Line Component: Move Susquehanna – FRPO - Lackawanna 500 kV line termination to the new bay 3 (between CB-3W and CB-3T breakers) and make necessary protections upgrades at both substations
2016_2-13E | Upgrade | PPL | 19.17 | PPL | 230, 500 | Gen Deliv | 1042, 1044 | Lackawanna 500/230 kV Transformer T3 & T4 Replacement: Replace the existing Lackawanna 500/230 kV T3 and T4 transformers with two new 1050 MVA transformers.
2016_2-13F | Greenfield | PPL | 12.4 | OVEC, DEI | 138 | Gen Deliv | 897, 1137 | New 4.8 mile 138kV line from Clifty Creek (OVEC) to Madison (DEI) 138kV stations.
2016_2-13G | Greenfield | PPL | 136.9 | AEP | 345 | N-1 Thermal; Gen Deliv | 101, 102; 64, 128, 130, 131, 134 | Build a new 13.7 mile 345kV line from Meadow Lake to Dequine and a new 48 mile 345kV line from Dequine to Eugene.
2016_2-13H | Greenfield | PPL | 47.9 | Penelec | 115, 230 | Gen Deliv | 25, 29, 90, 91, 92 | Build 23 mile new 230kV ckt from East Towanda to N. Meshoppen.
2016_2-13I | Greenfield | PPL | 11.19 | DEO&K | 138 | Gen Deliv | 907 | New 3.2 mile 138kV ckt from Tod hunter to Rockies Express.
2016_2-13J | Greenfield | PPL | 14.27 | DEO&K | 138 | Gen Deliv | 907 | New 6mi 138kV ckt from Nickel to Warren. New 138kV substation. Remove existing switch at Nickel.