## Setup
Enter Stakeholder Group Name in cell A2:
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Fuel Requirements for Black Start Resources

## 1. Interest Identification
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OC Interest Identification
1 | Sufficient black start capabilities be available regardless of situation
2 | Improve fuel assurance for black start resources
3 | Support all fuel type eligibility for black start resources
4 | Avoid creating stringent requirements that eliminate existing black start resources
5 | Clearly define performance standards for operating hours during a restoration event for each fuel type
6 | Clearly define testing requirements related to fuel security
7 | Explore options for fuel assurance/storage requirements
8 | Determine if fuel requirements for black start resources have to be defined in the Manuals and/or the OATT
9 | In the transiton or implementation phase for existing units, include an RFP type procurement process.
10 | Ensure storage resources are included in proper compliance with order 841.
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OPTIONS MATRIX
Solution Options
# | Design Components | Priority | Status Quo | A | B | C | D | E
A | Fuel Evaluation Criteria /Attributes
1 | Primary Fuel : Natural Gas
1a | Fuel transportation contracts for Natural Gas | Medium - High | None
1b | Fuel supply contracts for Natural Gas | Medium - High | None
1c | Emissions permit limitations | Medium | Different states and black start units have various limitations for emission waivers.PJM currently does not track.
1d | Run hour requirements | High | 16hrs
1e | on-site fuel storage | High | None
1f | Multiple gas pipeline connections | Low-Medium | None
1g | Back up oil | High
1h | Ability to start with back up oil without gas | Low
1i | Replenishment of dual fuel | Medium
2 | Primary Fuel :Oil
2a | Oil Storage | High | 16 hours of on-site fuel storage
2b | Oil transportation contracts | Medium | None
2c | Water Inventories | High | None
2d | Emissions permit limitations | Medium | Different states and black start units have various limitations for emission waivers. PJM currently does not track.
3 | Primary Fuel : Hydro
3a | Hydro - Pumped storage | High | 16 hours of operations for black start
3b | Hydro - Run of River | High | 16 hours of operations for black start
4 | Energy storage | High | 16 hours
5 | Intermittent resources | Low | n/a
6 | Hybrid resources | Low | n/a
7 | DER/DR with on-site generator | Medium | n/a
8 | Non fuel consumables (Water, Ammonia) | High | None
B | Fuel Assurance Testing & Verification Requirements
1 | Dual fuel unit testing | High | None | Separate test on each fuel
2 | Concurrent unit testing | High | None
3 | Online fuel transition testing | Medium | None | One test switching between fuels
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry.
5 | Black start MW capability verification | High | None
6 | Black start MW capability determination | High | None
C | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | [5 empty] | Medium
1 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG black start units are compensated for carrying cost of the full MTSL volume. For black start units that share tanks only one unit gets compensated. | [5 empty] | Low
2 | Water inventory/ secondary fuel assurance compensation | Medium | None
D | Implementation |  | N/A | [5 empty] | Medium - High
1 | Existing Black Start Units | Medium - High | None
2 | New Black Start Units | High | None
3 | 2018 RTO wide RFP awarded Black Start units | High | None
4 | Procuring additional black start units because of immediate deficiencies created by the new rules, as needed | High | None | [5 empty] | High

## 2a. Design Component Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3