## Setup
Enter Stakeholder Group Name in cell A2:
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Fuel Requirements for Black Start Resources

## 1. Interest Identification
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OC Interest Identification
1 | Sufficient black start capabilities be available regardless of situation
2 | Improve fuel assurance for black start resources
3 | Support all fuel type eligibility for black start resources
4 | Avoid creating stringent requirements that eliminate existing black start resources
5 | Clearly define performance standards for operating hours during a restoration event for each fuel type
6 | Clearly define testing requirements related to fuel security
7 | Explore options for fuel assurance/storage requirements
8 | Determine if fuel requirements for black start resources have to be defined in the Manuals and/or the OATT
9 | In the transiton or implementation phase for existing units, include an RFP type procurement process.
10 | Ensure storage resources are included in proper compliance with order 841.
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
OPTIONS MATRIX
Solution Options
# | Design Components | Priority | Status Quo | A | B | C | D | E
A | Level of Fuel Assurance for Black Start resources |  | N/A | All Black Start resources allocated to a TO zone must be fuel assured. | Determine the number of Black Start resources that have to be fuel assured allocated to each TO zone based on an analysis. | X% of Black Start resources allocated to a TO zone must be fuel assured. | Minimum of two Black Start resources allocated to the TO zone at separate sites must be fuel assured. Determine the Black Start resources that have to be fuel assured based on an analysis.
B | Universal Black Start Fuel Assurance Requirements
1 | Duration / Run Hour requirements | High | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16+ Hours per blackstart resource | 24 Hours per blackstart resource
2 | Emissions Permit Limitations | Medium | Different states and Black Start resources have various limitations for emission waivers. PJM currently does not track. | Requirements for the fuel assured Black Start resources to obtain emission permit waivers to accommodate operations during a restoration situation (operating below normal economic min values), if required. | No requirement but higher weighting will be applied during the Black Start RFP process to resources with emission permit waivers. | PJM will provide education and awareness to states and coordinate/develop waiver process. PJM will create a template for emission waivers. | Requirements for the fuel assured Black Start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required.
3 | Non-Fuel Consumables (eg. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement.
4 | Bilateral Compensated Black Start Unit Requirements |  | NERC Requirements | Must meet all fuel assurance requirements
5 | Starting System Requirements |  | N/A | Capability to provide 3 starts with a minimum 16 hours idle time
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Limitations based on the number of resources within the same pipeline segment | Not allowed to be a fuel assured Black Start without on-site fuel capability. | non-fuel assured Black Start must have firm gas transport
1a | Dual Fuel Capability | High | n/a | Resources must be able to start solely on on-site fuel | Secondary fuel must be stored on-site for each Black Start resource (if they share a common fuel source) to meet the run hour requirements.
1b | Pipeline requirements | High | n/a | Primary firm gas transportation contract with an annual availability period | Primary firm gas transportation contract with a winter availability period | Physically independent connections to more than one interstate natural gas pipeline
2 | Oil | High | 16 hours of run hour requirements | oil storage on-site at all times for each Black Start resource in a site to meet minimum run time requirements (if resources shares the same fuel source) | Firm refueling contracts | Firm oil pipeline connections
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Analysis with X % of confidence of most restrictive seasonal flow to support the assigned Black Start MW. | Performance verification will be based on the most limiting season of the past X years of performance history. | Single site simultaneous verification test
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | The pond level must be maintained to satisfy run hour requirements to meet the Black Start commitment. | Pond level must be maintained to satisfy run hour requirements and telemetry. | Use the 24 Hour Capacity factor rather than ICAP. If wish to use as non-assured fuel resources, then use the traditional ICAP value and have a 16 hour run requirement.
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | Stored energy must always be kept on-site for each Black Start resource to meet minimum run time requirements
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Use the 24 Hour Capacity factor rather than ICAP. | A combination of on-site fuel inventory, water level, stored energy, etc. must always be kept on-site for each Black Start resource to meet minimum run time requirements
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Analysis with X % of confidence of most restrictive season to support the assigned Black Start MW.
8 | DER/DR with on-site generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Must meet min run time duration requirements. | Not allowed to be a fuel assured Black Start resource without on-site fuel capability able to meet the minimum run requirements
D | Fuel Assurance Testing & Verification Requirements
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel on alternate years
2 | Concurrent fuel testing | High | None | All Black Start resources connected to the same fuel source test concurrently
3 | Online fuel transition testing | Medium | None | One test per year to demonstrate the ability to switch between fuels. | Provide data on fuel switching restritctions/limitations that unit may have.
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Fuel verification atleast at X frequency or upon PJM request | Telemetry of fuel inventory | Black start units report to PJM dispatch and units are placed in max-emergency when they carry fuel less than the minumum run hour requirement | Fuel verification on Black Start test forms. | Based on resource unit and fuel type, on-site fuel inventory, water level, stored energy, etc. must be confirmed to PJM on a monthly basis via eDART or telemetry if preferred.
5 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability must take into account unit limitations i.e Steam bypass, if applicable
6 | Black start MW capability verification | High | The annual capacity test | All Black Start resources connected to the same fuel source test concurrently
7 | Emission permit limitation verification |  | n/a | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable.
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours | Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance. | Develop a methodology to determine which portion of the incremental capital costs are solely necessary for Black Start fuel assurance. | PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for Black Start by netting energy revenues that are a direct result of the capital expenditures during the capital recovery period
1 | Fuel Assurance Compensation Capital Recovery Period. |  |  | The greater of the schedule 6A recovery period based on the age of the unit or 10 years.
2 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG Black Start resources are compensated for carrying cost of the full MTSL volume. For Black Start resource that share tanks only one resource gets compensated. | Oil , propane and LNG tanks shared between resources will proportionally share compensation of the MTSL value. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL.
3 | Onsite fuel, water level, stored energy, etc. compensation | Medium | None | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM dispatch must be notified within 24 hours. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. If the fuel inventory, water level, stored energy falls below the run hour requirement as the result of a regulatory requirement for approved planned outage (full derate), monthly Black Start revenues will not be withheld. | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient. | Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy, or non-fuel consumables falls below the run hour requirement as the result of a regulatory requirement for an approved planned outage (full derate) or restoration events, monthly Black Start revenues will not be withheld. If fuel inventories fall below 16 hrs due to PAI event, monthly Black Start revenues will be foregone.
4 | Fuel Assurance Testing Compensation |  | None | Units will be compensated for fuel assurance testing on both fuels. | Compensation to be similar to current Black start testing. Compensation for both tests on both fuels for dual fuel units.
5 | Compensation for non-CRF Black Start resources and non Black Start resources that do not require capital projects to provide fuel assured Black Start. |  | Base formula rate
F | Implementation |  | N/A
1 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service Existing Black Start resources that do not clear the RFP may be terminated and if terminated will recover their investment in accordance with Section 6 of Schedule 6A of the OATT
2 | New Black Start resources | High | None | Add the requirement that any submission to a future RFP must meet the fuel assurance requirements. RFP process would not change beyond that.
3 | 2018 RTO wide RFP awarded Black Start resources | High | None | To be handled as Existing Black Start Resources. Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements. Existing Black Start resources that do not clear the RFP may be terminated and if terminated will recover their investment in accordance with Section 6 of Schedule 6A of the OATT
4 | Procuring additional Black Start resources because of deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements.

## 2a. Design Component Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D
A | Level of Fuel Assurance for Black Start resources |  | N/A | All Black Start resources allocated to a TO zone must be fuel assured (Only fuel assured Black Start resources may be used to meet M36 Attachment A requirements) | All Black Start resources within each TO zone must be fuel assured. Fuel Assurance needs to be clearly defined. | All Black Start resources must be fuel assured.
B | Universal Black Start Fuel Assurance Requirements
1 | Duration / Run Hour requirements | High | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16 hours per blackstart resource (even if resources on the same site share a common fuel source) | 16 Hours | 24 hours per blackstart resource (even if resources on the same site share a common fuel source)
2 | Emissions Permit Limitations | Medium | Different states and Black Start resources have various limitations on operations of Black Start resources. PJM currently does not track. | Requirements for the fuel assured Black Start resources to obtain operating permit conditions to accommodate operations during a restoration situation (operating below normal economic min values), if required. | Requirements for the Black Start resources to obtain emission permit waivers to accommodate operations during a restoration situation, if required. | Same as PJM
3 | Non-Fuel Consumables (eg. water, ammonia) | High | None | Capable of supporting the duration of the run hour requirement. | Capable of supporting the duration of the run hour requirement. | Same as PJM
4 | Bilateral Compensated Black Start resource Requirements |  | NERC Requirements | Must meet all fuel assurance requirements. Must enter PJM Black Start service through RFP process. |  | Must enter PJM's market RFP and be shown to be more economic than alternatives.
5 | Starting System Requirements |  | N/A | Capability to provide 3 starts and a minimum 16 hours idle time. | Time frame for 3 starts needs to be defined
C | Black Start Fuel Assurance Solutions by Primary Fuel Type
1 | Natural Gas | High | 16 hours of run hour requirements | Not allowed to be a fuel assured Black Start without on-site fuel capability, or interconnection to multiple interstate pipelines. | Options in addition to on-site fuel should be considered including multiple pipeline interconnections, nature of gas contracts, location of gas supply. | Same as PJM
1a | Dual Fuel Capability | High | N/A | Resources must be able to start solely on on-site fuel AND Secondary fuel must be stored on-site for each Black Start resource (if they share a common fuel source) to meet the run hour requirements. | Options in addition to on-site fuel should be considered including multiple pipeline interconnections, nature of gas contracts, location of gas supply. | Same as PJM
1b | Pipeline requirements | High | N/A | N/A | Options in addition to on-site fuel should be considered including multiple pipeline interconnections, nature of gas contracts, location of gas supply. | N/A |  | Low
2 | Oil | High | 16 hours of run hour requirements | oil storage on-site at all times for each Black Start resource at a site to meet minimum run time requirements (if resources share the same fuel source) | oil storage on-site at all times for each Black Start resource at a site to meet minimum run time requirements (if resources share the same fuel source) | Same as PJM
3 | Hydro (Run of River) | High | 16 hours of run hour requirements | Analysis with X% of confidence of most restrictive seasonal flow to support the assigned Black Start MW. | Analysis with X% of confidence of most restrictive seasonal flow to support the assigned Black Start MW. Confidence level needs to be defined and comparable to other resources. | 24 hours of run hours requirements |  | Low - High
4 | Hydro (Pumped Storage) | High | 16 hours of run hour requirements | The pond level must be maintained to satisfy run hour requirements to meet the Black Start commitment. | The pond level must satisfy run hour requirements to meet the Black Start commitment. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) |  | Medium
5 | Energy Storage Resources | High | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Stored energy must always be kept on-site for each Black Start resource to meet minimum run time requirements | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) Stored energy must always be kept on-site for each Black Start resource to meet minimum run time requirements. |  | Medium - High
6 | Hybrid Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | A combination of on-site fuel inventory, water level, stored energy, etc. must always be kept on-site for each Black Start resource to meet minimum run time requirements | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September) A combination of on-site fuel inventory, water level, stored energy, etc. must always be kept on-site for each Black Start resource to meet minimum run time requirements |  | High
7 | Intermittent Resources | Low | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Analysis with X% of confidence of most restrictive season to support the assigned Black Start MW. | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage.
8 | DER/DR with on-site generator | Medium | 16 hours of run hour requirements. Must have the ability to start within 180 minutes if not in a forced or planned outage. | Not allowed to be a fuel assured Black Start resource without on-site fuel capability able to meet the minimum run requirements | Must meet min run time duration requirements at all times. | 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September). Must have the ability to start within 180 minutes if not in a forced or planned outage.
D | Fuel Assurance Testing & Verification Requirements
1 | Dual fuel unit testing | High | None | Separate testing for each fuel in the same year | Separate testing for each fuel in the same year | Same as PJM. Paid for testing.
2 | Concurrent fuel testing | High | None | All Black Start resources connected to the same fuel source test concurrently | All Black Start resources connected to the same fuel source test concurrently | Same as PJM. Applies to more than Oil/Gas units. Paid for testing.
3 | Online fuel transition testing | Medium | None | Provide data annually on fuel switching restrictions/limitations that unit may have. | One test per year to demonstrate the ability to switch between fuels. | Same as PJM.
4 | Fuel inventory verification | Medium | Black start CTs reports to PJM dispatch and units are placed in max-emergency when they carry less than 10 hours of fuel (M14d). Some hydro units report pond levels via telemetry. | Based on resource unit and fuel type, on-site fuel inventory, water level, stored energy, etc. limitations must be communicated immediately to PJM via Markets Gateway Resource Limitation Reporting and (if possible) telemetry, for situational awareness | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM.
5 | Starting Systems verification |  | n/a | Starting system limitations must be communicated immediately to PJM via Markets Gateway Resource Limitation Reporting if starting systems not able to meet the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM
6 | Non-Fuel Consumables (eg. water, ammonia) inventory verification |  | n/a | Non-fuel consumables inventory limitations must be communicated immediately to PJM via Markets Gateway Resource Limitation Reporting if consumables fall below the run time requirement | Inability to meet Black Start obligations and all related status changes must be reported immediately. | Same as PJM
7 | Black start MW capability determination | High | Each Unit's ICAP MW is currently used for unit compensation | Black start MW capability based on the most limiting season, if applicable. | Black start MW capability based on the most limiting season, if applicable. | Black Start capability based on 24 hours of run hours requirements. Calculate 24 hour output after reaching the average summer "lowest point" during the summer operating day. (June -September)
8 | Black start MW capability verification | High | The annual capacity test | All Black Start resources connected to the same fuel source test concurrently | All Black Start resources connected to the same fuel source test concurrently | Same as PJM. Paid for testing.
9 | Emission permit limitation verification |  | n/a | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable. | Black start resource owners will certify using written waivers or other applicable documentation that emission permit limitations are available during restoration operations, as applicable. | Same as PJM.
E | Fuel assurance compensation | High | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A and also by taking into account run time hours AND Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance. PJM will determine the portion of incremental capital costs expended for fuel storage that is solely necessary for Black Start by netting energy revenues that are a direct result of the capital expenditures during the capital recovery period. | Units that store oil, propane or LNG on-site can be compensated for fuel carrying costs in accordance with Schedule 6A for the required fuel levels defined by required run time hours. Ability to have Black Start resources recover incremental capital costs solely associated with fuel assurance, capital costs submitted and approved in accordance with the schedule 6A process. | Same as PJM
1 | Fuel Assurance Compensation Capital Recovery Period. |  |  | (The greater of the Schedule 6A recovery period based on the age of the unit or 10 years); OR Cost recovery amortized over the remaining life of the unit as applied by the owning entity. |  | Existing Schedule 6A recovery period based on age of unit
2 | Minimum Tank Suction Level (MTSL) | Low | Oil , propane and LNG Black Start resources are compensated for carrying cost of the full MTSL volume. For Black Startresources that share tanks only one unit gets compensated. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 16 hours divided by the tank capacity times the MTSL. | When Black Start resources share a fuel tank the Black Start resource compensation should include only an allocated share of the MTSL equal to the BS fuel requirement for 24 hours divided by the average daily tank level from prior delivery year times the MTSL.
3 | Onsite fuel, water level, stored energy, etc., starting systems and non-fuel consumables compensation | Medium | None | Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy, or non-fuel consumables falls below the run hour requirement as the result of a regulatory requirement for an approved planned outage (full derate) or restoration events, monthly Black Start revenues will not be withheld. If fuel inventories fall below 16 hrs due to PAI event, monthly Black Start revenues will be foregone. | If the on-site fuel inventory, water level, stored energy, etc., starting systems, or non-fuel consumables falls below the run hour requirements for any length of time during any period, PJM dispatch must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory, starting systems, or non-fuel consumables are deficient. If the fuel inventory, water level, stored energy falls below the run hour requirement as the result of an approved planned outage (full derate), monthly Black Start revenues will not be withheld. | If the on-site fuel inventory, water level, stored energy, etc. falls below the run hour requirements for any length of time during any period, PJM must be notified immediately. Black start monthly revenues will be foregone for months in which the fuel inventory is deficient, except if do to an implemented PAH or actual system restoration.
4 | Fuel Assurance Testing Compensation |  | None | Units will be compensated for fuel assurance testing on both fuels. | Units will be compensated for fuel assurance testing on both fuels. | Same as PJM
5 | Compensation for non-CRF Black Start resources and non Black Start resources that do not require capital projects to provide fuel assured black start. |  | Base formula rate | For Fuel Assurance Blackstart resources, base formula rate compensation incentive factor changed to Z=0.2 (from Z=0.1) | For Fuel assurance BlackStart resources, base formula rate compensation incentive factor should remain the same Z=0.10 | Same as PJM
F | Implementation |  | N/A
1 | Existing Black Start resources | Medium - High | None | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service Existing Black Start resources that do not clear the RFP may be terminated and if terminated will recover their investment in accordance with Section 6 of Schedule 6A of the OATT | RFP process initiated by PJM within 6 months of FERC approval of OATT changes allowing existing non-fuel assured Black Start resources to submit proposals to become fuel assured and other non-Black Start resources to submit proposals to provide fuel assured Black Start service. Black Start resources should not be terminated until after the capital cost recovery term has been completed | Same as PJM.
2 | New Black Start resources | High | None | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | New fuel assurance requirements would apply to any submission to a future RFP. RFP process would not change beyond that. | Same as PJM.
3 | 2018 RTO wide RFP awarded Black Start resources | High | None | To be handled as Existing Black Start resources. Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements. Existing Black Start resources that do not clear the RFP will not be terminated during their capital recovery period, however these black start resources will not be used to meet Manual 36 Critical Load requirements. | To be handled as Existing Black Start resources. Non-fuel assured resources awarded in the 2018 RTO Wide RFP may participate in the PJM initiated RFP with proposals to meet fuel assurance requirements. Black Start resources should not be terminated until after the capital cost recovery term has been completed. Black Start resources should not be terminated until after the capital cost recovery term has been completed | Same as PJM.
4 | Procuring additional Black Start resources because of immediate deficiencies created by the new rules, as needed | High | None | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Existing incremental RFP process would be used with the requirement that any submitted proposal meets the fuel assurance requirements. | Same as PJM.

## 3a. Package Details
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description | options
Compensation for non-CRF black start units and non black start units that do not require capital projects to provide fuel assured black start. | Adder to the base formula rate for fuel assurance. | Increase the fuel storage component of the base formula rate and make available for all resource types in some form. | Increase the Z factor based on the fuel assured resource type.

## Revision History
MIC/OC Special Sessions: Fuel Requirements for Black Start Resources
Fuel Requirements for Black Start Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3