## Sheet1
PJM 2023 RTO Wide Black Start RFP | [5 empty] | Select Black Start and Fuel Assurance Proposal using the drop down menus by clicking on cells highlighted yellow (add columns if needed)
Level 2 Proposal Data Collection Form
[6 empty] | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type | Select Black Start Proposal Type
[6 empty] | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type | Select Fuel Assurance Proposal Type
Category |  |  |  | Data Required | Response | Proposal 1 (Name of Facility) | Proposal 2 (Name of Facility) | Proposal 3 (Name of Facility) | Proposal 4 (Name of Facility) | Proposal 5 (Name of Facility) | Proposal 6 (Name of Facility) | Proposal 7 (Name of Facility) | Proposal 8 (Name of Facility) | Proposal 9 (Name of Facility) | Proposal 10 (Name of Facility) | Proposal 11 (Name of Facility) | Proposal 12 (Name of Facility) | Proposal 13 (Name of Facility) | Proposal 14 (Name of Facility) | Proposal 15 (Name of Facility) | Proposal 16 (Name of Facility) | Proposal 17 (Name of Facility) | Proposal 18 (Name of Facility) | Proposal 19 (Name of Facility) | Proposal 20 (Name of Facility)
5.1. | Purpose and Scope
| 5.1.1 | Facility
|  | 5.1.1.1. | Name of facility | Name | Text
|  | 5.1.1.2. | Owner of facility | Owner | Text
|  | 5.1.1.3. | Geographic details | Address | Text
|  |  |  | County | Text
|  |  |  | State | Text
|  |  |  | Latitude / Longitude | Text
|  | 5.1.1.4. | Age of proposed black start unit | Age of proposed black start unit at time Black Start Service would commence | Text
| 5.1.2. | Black Start Unit
|  | 5.1.2.1. | Type of generation | Type of generation - CT, Combined Cycle (or CT that is part of a Combined Cycle plant), Intermittent, Run of River Hydro, Pump Storage Hydro, Diesel, Storage, Hybrids (renewables with storage), DER, etc | Text
|  | 5.1.2.2. | Manufacturer | Manufacturer (e.g. GE, Siemens) | Text
|  |  |  | Model/Unit Type (e.g. 7FA) | Text
|  |  |  | Diesel or battery or CT or other resource cranking the Black Start Unit (See Section 6.5 “Black Start Unit Configurations”). | Text
|  | 5.1.2.3 | Black Start MW capability | MW Capability (ICAP or equivalent) of the intended Black Start Unit and the full plant (if applicable). Indicate whether MW capability is in terms of capacity resource ICAP, maximum dependable capability (for energy only resources), ELCC MW, or nameplate MW rating. | Text
|  |  |  | Proposed BS Unit MW | Text
|  |  |  | Provide details if proposed BS unit MW are different than MW capability specified above. | Text
|  |  |  | Confirm any Power Augmentation MW included in BS MW Above (if applicable) | Text
|  |  |  | Indicate Power Augmentation Type (if applicable) | Text
|  |  |  | Describe any limitations due to the use of power augmentation (e.g. ambient temp.) where the unit would not be able to meet the proposed black start MWs year round during a restoration scenario. | Text
|  |  |  | For CC indicate ST MW Capability (ICAP or equivalent) | Text
|  | 5.1.2.4 | Black Start Unit fuel type(s) | Primary Fuel Type | Text
|  |  |  | Secondary Fuel Type (if applicable) | Text
|  |  |  | Primary Start-Up Fuel (if applicable) | Text
|  |  |  | Secondary Start-up fuel (if applicable) | Text
|  |  |  | Indicate fuel(s) used (if different) for any starting or cranking engines/diesels. | Text
|  | 5.1.2.5 | Plant with multiple units | For a plant with multiple units, identify which units are being proposed as black start resources. Also indicate which of the other units can be started by the proposed black start units. | Text
|  | 5.1.2.6. | Black Start operating mode | Indicate whether the black start unit is capable of operation in automatic isochronous mode or if it is controlled manually in isochronous mode. | Dropdown
| 5.1.3. | Interconnection
|  | 5.1.3.1. | Transmission level | Interconnecting Station Name | Text
|  |  |  | Voltage Level of Interconnecting Station | Text
|  |  |  | Transmission Owner zone | Text
| 5.1.4. | Necessary Upgrade(s) for Black Start Capability
|  | 5.1.4.1. | Brief description of the modifications required to convert the facility to black start | Briefly describe the modifications that are required to convert the facility to black start. If adding a diesel, please indicate quantity, the manufacturer, model, and rating of the unit, as well as which unit(s) it will be cranking. If adding a battery indicate cranking power, cranking duration, and overall battery MW size. | Text
5.2. | Generator Operational Details
| 5.2.1. | One-Line Diagram
|  | 5.2.1.1. | One line diagram | Provide a one-line diagram for the plant site, which includes the black start facility. The one-line diagram should include the proposed RFP response unit(s), all associated auxiliary loads, and transmission and distribution level equipment. Formal drawings are not required. Legible hand-written mark-ups of existing diagrams are sufficient. Visio diagrams with adequate detail are also sufficient. | (Upload PDF)
| 5.2.2. | Start-Up Sequence Description
|  | 5.2.2.1. | Black Start Unit Start-up sequencing description | If known, list the steps that the plant would follow immediately following a full or partial black out to get the Black Start Unit started, close to a dead bus, and any anticipated GO/TO coordination for load pickup from the Black Start Units minimum load to economic maximum load. The description should include clear references to the one-line diagram. | Text
| 5.2.3. | Reactive Capability
|  | 5.2.3.1. | Reactive (MVAR) capability curve (D-Curve) | Provide a reactive (MVAR) capability curve (D-Curve) indicating the over and under excitation limits, including MW, Min. MVAR, Max. MVAR, and a table including up to 8 MW points (if possible) with associated minimum and maximum MVAR points. Include the maximum sustained leading and lagging (MVAR absorption) capability. | (Upload PDF)
|  | 5.2.3.2. | Restrictions to MVAR capability curve | Describe any anticpated administrative (operational/procedural) restrictions that prevent the unit from providing MVARs up to over excitation and under excitation limit? | Text
|  |  |  | Can unit provide reactive support at 0 MWs (full speed no load) as cranking path is energized w/ no load | Yes/No
|  |  |  | What is acceptable generator terminal voltage range (ex. 0.95 to 1.05 of nominal)? | Text
|  |  |  | For inverter based resources, how does inverter based resource get online without outside electrical grid? | Text
|  | 5.2.3.3 | Voltage Regulator | Can voltage regulator operate in automatic voltage control mode during a restoration event? | Text
| 5.2.4. | Start-up Time
|  | 5.2.4.1. | Start-up Time | Estimated time to close to a dead bus | Text
|  |  |  | Estimated time to ramp to minimum load | Text
|  |  |  | Estimated time to ramp to economic max load | Text
|  |  |  | Confirm these times include time to start-up cranking power source as applicable. | Yes/No
|  |  |  | If offering more than one unit for Black Start Service, can all units close to a dead bus in 180 minutes when requested to start by Transmission Owner or PJM. | Yes/No
|  | 5.2.4.2. | Plant staffing details | Indicate whether the unit will be staffed 24 x 7 if it is selected to provide Black Start Service. If the plant will not be staffed 24 x 7, can the unit be started remotely? If so, describe the plan for starting the black start unit in the event of a telemetry failure. | Text
| 5.2.5. | Existing or Planned Black Start Unit Fuel Assurance Details
|  | 5.2.5.1. | Primary/Secondary Fuels | Primary Fuel | Dropdown
|  |  |  | Secondary Fuel | Dropdown
|  |  |  | Indicate any non-fuel consumables required to maintain 16 hrs of operation (e.g. NOx water injection). | Text
|  | 5.2.5.2. | Natural Gas Units | Indicate single or multiple pipelines, or LDC, and indicate name of pipeline(s) / LDC(s). | Text
|  |  |  | Gas Transportation and Supply Arrangements - If a primary or secondary fuel is natural gas, indicate gas transportation and supply arrangements. Indicate if these arrangements are primary firm or non-firm transportation contracts for primary or alternate pipeline feeds. Indicate any arrangements for the unit to secure additional fuel. | Text
|  | 5.2.5.3. | Dual Fuel Units | Can the unit start on both primary and secondary fuel? | Yes/No
|  |  |  | Is different start-up fuel required for either primary or secondary fuels? | Yes/No
|  |  |  | Indicate any fuel switching requirements to move from primary to alternate fuel (or vice versa) - e.g. does the unit need to reduce or shutdown in order to switch between primary and alternate fuels | Text
|  |  |  | Is the unit willing to run on both fuels during a restoration event ? | Yes/No
|  |  |  | Will resource be dual fuel available year round for black start without changing of equipment (e.g. burners, etc.)? Are there any other limitations such as emissions, ozone season, etc? Provide details if there are any limitations. | Text
|  | 5.2.5.4. | Hydro Units | Pumped Storage or Run of River | Dropdown
|  |  |  | Pumped Storage - Indicate maximum run time at proposed BS MW with a full pond | Text
|  |  |  | Run of River - indicate number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment. | (Upload PDF)
|  | 5.2.5.5. | Storage | Type of Storage Unit (e.g. Battery, Flywheel, or other) | Text
|  |  |  | Indicate max run time at proposed BS MW with a full charge. | Text
|  |  |  | Indicate the number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment. | (Upload PDF)
|  | 5.2.5.6. | Hybrid | Type of Hybrid (e.g. Solar/Battery, Wind/Battery or other) | Text
|  |  |  | Indicate max run time at proposed BS MW with a full charge. | Text
|  |  |  | Indicate the number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment. | (Upload PDF)
|  | 5.2.5.7. | Intermittent | Type of Intermittent (e.g. Solar, Wind, or other) | Text
|  |  |  | Indicate max run time at proposed BS MW | Text
|  |  |  | Indicate the number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment. | (Upload PDF)
|  | 5.2.5.8. | DER | Type of DER | Text
|  |  |  | Fuel Type | Text
|  |  |  | Indicate max run time at proposed BS MW | Text
|  |  |  | Provide details as indicated above in 5.2.5.1 through 5.2.5.7 for respective fuel types as applicable. | Text
|  | 5.2.5.9. | 16 hour run time requirement | Can unit operate for a minimum of 16 hours at proposed BS MWs based on fuel and non-fuel consumables? | Yes/No
|  |  |  | If not, how many hours can the unit run based on the proposed BS MW and provide details on limitations. | Text
|  |  |  | If the black start unit relies on a cranking resource (e.g. diesel generator, battery, or combustion turbine, compressed air) for starting or auxiliary power, verify the cranking resource has sufficient fuel for 16 hours of operation and a minimum of 4 starts in a 24 hour period. | Yes/No
|  |  |  | If not, how many hours can the cranking resource unit run and maintain a minimum of 4 starts in a 24 hour period based on the proposed BS MW and provide details on limitations. | Text
|  |  |  | Inverter based resource (if applicable) has a power source capable of 16 hours of operation and 4 starts | Yes/No
|  | 5.2.5.10. | Onsite Fuel Storage General | Onsite fuel storage description | Text
|  |  |  | Permitting limitations (and challenges to obtain permits) associated with burning on-site fuel | Text
|  |  |  | Description of the planned arrangements to both obtain and replenish on-site fuel. | Text
|  | 5.2.5.11. | Onsite Fuel Storage Details | Onsite fuel storage type | Text
|  |  |  | Volume / tank size | Text
Number of hours of sustained output at Economic Maximum output of the Black Start Unit
|  |  |  | Is Black Start Unit fuel storage shared with other non-Black Start Units? | Yes/No
|  |  |  | Explain the fuel supply and replenishment arrangements for this resource and explain the planned contractual arrangements for same. | Text
|  |  |  | Details for fuel storage if fuel is not constantly maintained in storage tanks (including why and when fuel is stored) | Text
|  | 5.2.5.12. | Non-Fuel Consumable Storage Capability | Briefly describe storage capabilities/tank sizes for any non-fuel consumables required for Black Start Service or Fuel Assured Black Start Service | Text
| 5.2.6. | Applicable minimum load, environmental, and black start testing restrictions
|  | 5.2.6.1. | Stabilizing Load | Does the unit require stabilizing load that exceeds internal plant loads / Can unit operate at full speed no load during restoration emergency? | Yes/No
|  |  |  | If stabilizing load is required, indicate minimum loading criteria / the amount of load external to the plant that is needed upon initial breaker closing. The external load requirement will be coordinated with the Transmission Owner for restoration planning purposes. | Text
|  | 5.2.6.2 | Minimum Output Restrictions | Provide minimum output restrictions at various stages of the startup sequence. | Text
|  |  |  | Provide step by step sequence (timing/ load pick/ ramp/ hold points/ hot spots aka MW points unit needs to avoid/ etc.) | Text
|  |  |  | Provide the units maximum allowable time at minimum load, and state the minimum load. Preference is placed on those units that are able to “idle” for the longest time serving only house load with no net output to the transmission grid because this reduces the complexity of GO/TO load pickup coordination. Plants that have multiple units should consider the potential of cranking auxiliaries of other units as additional “house load.” | Text
|  | 5.2.6.3. | Permit Compliance/Limitations | Provide the unit’s minimum load (MW) under the current emissions permit | Text
|  |  |  | Provide the maximum allowable time to come into compliance with emissions permit minimum load above during a restoration emergency. | Text
|  |  |  | What is the lowest load the unit can operate in a stable steady state configuration if there were no emission permit restrictions? | Text
|  |  |  | Are unit's run hours limited on primary or secondary fuel? | Text
|  |  |  | Identify any current or proposed legislation that will impact a units ability to provide black start service? | Text
|  | 5.2.6.4. | Emissions permit modifications | Does the unit have a permit emergency exemption from emission limits during restoration events? | Text
|  |  |  | Confirm the feasibility of obtaining an emissions permit modification to allow the unit to operate at the lowest possible load for restoration and black start testing (Units with emergency waivers or permits that allow low load capabilities for extended periods of time are strongly preferred). | Text
|  | 5.2.6.5. | Ramp rate details | In the context of a restoration event, provide unit ramp rate | Text
|  |  |  | Indicate largest block of load that can be picked up instantaneously | Text
|  |  |  | Provide the time between load pick-ups | Text
|  |  |  | Provide any applicable variations in ramp rate | Text
|  | 5.2.6.6 | Black Start Test | Can the unit perform an annual Black start Test where it operates isolated from the grid in isochronous mode carrying only station auxiliary load for at least thirty minutes? | Yes/No
|  |  |  | If not, identify alternative test options that may be needed. | Text
|  |  |  | Provide brief description of proposed annual Black Start Test | Text
|  | 5.2.6.7 | Combined Cycle Units | Can the Combustion turbines be operated in simple cycle mode? | Yes/No
|  |  |  | If so, identify for how long? (Summer / Winter). | Text
|  |  |  | If not, does the unit have steam bypass capability? | Text
|  |  |  | Does the unit have any limitation which requires bringing the steam turbine on line during the restoration event? Explain reason why. | Text
|  |  |  | If the steam turbine must be brought on can the ramp rate be manually controlled? | Text
|  | 5.2.6.8. | Steam bypass mode | What is the minimum and maximum load the combustion turbine can operate in Steam bypass mode? | Text
|  |  |  | Indicate any time limitations for operating in either mode. | Text
|  | 5.2.6.9. | Station auxiliary load | Is the station’s auxiliary load greater than the combustion turbine’s lowest possible minimum load? | Yes/No
|  |  |  | If not greater, then provide MW difference. | Text
| 5.2.7. | Refurbishment of Existing Black Start or Black Start Capable Resources
|  | 5.2.7.1. | Black Start Capability of proposed unit to be refurbished (if applicable) | Is the existing unit black start capable in accordance with the requirements stated in Tariff, Schedule 6A, and PJM Manual 12 – Balancing Operations? | Yes/No
|  |  |  | If not, what modifications are required? | Text
|  | 5.2.7.2. | Existing Black Start Units that would otherwise retire | Identify any equipment overhauls or refurbishment work that would be required for continued reliable Black Start Service. | Text
5.3. | Project Schedule
| 5.3.1 | Estimated In-Service Date
|  | 5.3.1.1. | Estimated In-Service Date | Indicate the estimated in-service date as a black start capable unit. For the purpose of this RFP proposal, assume a Black Start In-Service date of December 1, 2025. Dates will be adjusted based on actual award date. | Text
| 5.3.2. | Project Schedule
|  | 5.3.2.1. | Project Schedule | Detail the project milestones in tabular and/or graphical form. Include the milestone description and projected start/finish dates. | (Upload PDF)
| 5.3.3. | Procurement Plan
|  | 5.3.3.1. | Procurement Plan | Detail any work that is planned with vendors. | Text
5.4. | Total Estimated Capital Cost for Black Start Service and/or Fuel Assured Black Start Service
| 5.4.1 | Capital Cost
|  | 5.4.1.1. | Black Start Capital Recovery Rate(s) | Specify which Schedule 6A Fixed Black Start Service Cost (Fixed BSSC) Rate is being selected. If selecting the Base Formula Rate, enter 0 for the capital costs for Sections 5.4.1.2 and 5.4.1.3 below. | Text
|  | 5.4.1.2. | Black Start Service Capital Cost (if applicable) | Capital Cost required to provide Black Start Service (excluding any Black Start Service Fuel Assured Cost) | Number
|  | 5.4.1.3. | Black Start Service Fuel Assured Capital Cost (if applicable) | Capital Cost to become Black Start Fuel Assured (excluding any Black Start Service Cost) | Number
|  | 5.4.1.4 | Expected Capital Recovery Period | Provide the expected capital recovery period (years) based on the age of the unit when it enters Black Start or Fuel Assured Black Start Service. | Text
|  | 5.4.1.5. | Summary of Black Start Service and/or Fuel Assurance Capital Costs | Provide detailed summary of capital cost for both Black Start Service and/or Fuel Assurance at a minimum including engineering, construction, materials, in-house labor, overheads and contingency costs. | (Upload PDF)
| 5.4.2. | Estimated Fixed Black Start Service Cost
|  | 5.4.2.1. | Estimated Fixed Black Start Service Cost | Provide estimated Fixed Black Start Service Cost which includes cost for both Black Start Service and if applicable Fuel Assurance | Number
| 5.4.3. | Estimated Black Start Service Annual O&M Cost
|  | 5.4.3.1. | Estimated Variable Black Start Service Cost | Provide estimated Black Start O&M Cost including any cost required to meet NERC Standards and or Fuel Assurance | Number
|  | 5.4.3.2 | Summary of Variable Black Start Service Cost | Provide detailed summary of annual O&M costs for providing Black Start Service and Fuel Assurance | (Upload PDF)
| 5.4.4. | Estimated Black Start Service Annual Fuel Storage Costs
|  | 5.4.4.1. | Estimated Black Start Service Annual Fuel Storage Costs | Provide estimated Black Start Service Fuel Storage Cost | Number
|  | 5.4.4.2. | Fuel Usage Rate at Full Load (i.e. Burn Rate) | Provided estimated Black Start unit(s) fuel usage rate at full load | Text
|  | 5.4.4.3. | Minimum Tank Suction Level Volume | Provide Minimum Tank Suction Level Volume | Text
|  | 5.4.4.4. | Summary of Fuel Storage Cost | Provide summary of the calculation of the annual fuel storage costs above. | (Upload PDF)
5.5 | Black Start Unit Owner Contact Information
| 5.5.1. | Primary Contact
|  | 5.5.1.1. | Provide Primary Contact Information | Name | Text
|  |  |  | Title | Text
|  |  |  | Company | Text
|  |  |  | Phone Number | Text
|  |  |  | Email Address | Text
| 5.5.2. | Alternate Contact
|  | 5.5.2.1. | Provide Alternate Contact Information | Name | Text
|  |  |  | Title | Text
|  |  |  | Company | Text
|  |  |  | Phone Number | Text
|  |  |  | Email Address | Text