## Needs-Sept
Need Number | TO | Area | Needs Meeting | Solutions Meeting | Submission of Supplemental Projects for Inclusion in Local Plan | Upgrade ID | Withdrawn | Project Name | Project Description
ACE-2018-0001 | ACE | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  | Deterioration on Moss Mill - Motts Farm 69 kV line | Comprehensive inspection data revealed deterioration on Moss Mill - Motts Farm 69 kV line.
ACE-2018-0002 | ACE | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  | Deterioration on Deepwater - Paulsboro 69 kV line. | Comprehensive inspection data revealed deterioration on Deepwater - Paulsboro 69 kV line.
ACE-2018-0003 | ACE | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  | Deterioration on Mickleton - Paulsboro - Valero 69 kV line. | Comprehensive inspection data revealed deterioration on Mickleton - Paulsboro - Valero 69 kV line.
ACE-2018-0004 | ACE | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  | Deterioration on Mickleton - Paulsboro - Valero 69 kV line. | Inspection revealed deterioration on Mickleton - Paulsboro - Valero 69 kV line.
ACE-2018-0005 | ACE | PJM MA | 2018-10-29 |  |  |  |  | Deteriorated equipment at 138/12 kV Scull Substation | Inspections revealed deteriorated equipment at 138/12 kV Scull Substation
AEP-2018-AP001 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1851 |  | Fries - Independence 69 kV line | The Fries - Independence 69kV line is an 11 mile long radial line and maintenance cannot be performed due to a lack of outages available on the line. Approximately 20 MVA is served out of Independence during winter peak conditions and is dropped for outages on this circuit. From 2013-2018, the Fries - Independence 69 kV circuit has experienced 5 permanent outages and 4 momentary outages, resulting in approximately 5.7M customer minutes interrupted. Fries - Independence 69 kV line has 23 open conditions associated with the structures that make up the line. Conditions include woodpecker damage and rot top. Majority of the circuit utilizes 1950s wood structures
AEP-2018-AP002 | AEP | PJM West | 2018-10-26 | 2019-06-17 |  |  |  | New distribution station request in Mabscott, West Virginia | APCO Distribution has requested a new distribution station located in Mabscott, West Virginia. Winter projected load 15 MVA.
AEP-2018-AP003 | AEP | PJM West | 2018-10-26 | 2019-04-23 |  |  |  | Mullensville 138/46 kV transformer no. 1 | The need to address Mullensville transformer #1 is driven by the short circuit strength breakdown caused by the amount of electrical discharges of high energy has led to rising gas levels in the tank oil and carbonization of the insulating paper. Acetylene is at IEEE Condition 3 and Ethylene is at IEEE Condition 2 per the latest DGA readings in 2018 which contributes to poor dielectric strength. The rising presence of these hot metal gasses can be caused by poor connections, shorted turns, broken winding strands, or inadvertent core grounding from damage to the core ground insulation during through faults events; all of these are indicative of circulating currents in the core resulting in hotspots of the core and surrounding internal components. High energy discharges can be caused by flashovers, tracking or arcing, or short circuits between a number of internal components. In addition to the 2018 compressor failure on CB A, IPS malfunction records indicate that the compressor motor burnt up in 2008 and failed again in 2009. There are only 13 of these FK-69-1500-3 types on the AEP system, making replacement parts difficult or impossible to obtain. This oil filled breaker has no oil containment and requires O&M costs to maintain the unit's oil that similar SF6 type breakers do not require. The Ground-Switch MOAB on the high side of the 138/46 kV transformer at Mullensville are obsolete and create an overlap in the zones of protection.
AEP-2018-AP004 | AEP | PJM West | 2018-10-26 |  |  |  | 2019-04-11
AEP-2018-AP005 | AEP | PJM West | 2018-10-26 | 2019-05-20 |  |  |  | Flooding at 138/46 kV Clendenin Station | On Thursday, June 23, 2016, sustained heavy rain caused severe flooding along the Elk River in West Virginia. The flood waters engulfed much of the town of Clendenin, including Clendenin Station, which sustained significant damage. Clendenin station lies well under the FEMA 100 year flood plain.
AEP-2018-AP006 | AEP | PJM West | 2018-10-26 | 2019-04-23 |  |  |  | Huff Creek 138/69/46 kV transformer no. 1 | The need to address Huff Creek transformer #1 is driven by the oil's interfacial tension, which has been consistently below 30 mN/m (the acceptable limit for this voltage class). This is an indication of sludge beginning to form from oil contaminates, which will lead to accelerated aging of the unit; the sludge will impair oil circulation and lead to more frequent overheating. In addition, the moisture content and CO levels have begun a rapid increase over the past four years. CO is now at IEEE Condition 2 and dielectric strength is trending down. The presence of increased CO and moisture levels occurring over the same span of time is indicative of the cellulose breakdown from the insulating paper; this increases the risk of future shorts in the windings due to decreased insulating material. The need to address Huff Creek ground transformer #2 is driven by Thermal through fault events, mostly in excess of 700Ã‚Â°C, have led to, steady increases in gasses including the now IEEE Condition 3 levels of ethylene in PH A, IEEE Condition 2 levels of carbon monoxide in PH A, methane in PH B, and ethylene and methane in PH C. These faults have also generated carbonization of the insulating paper. In addition, all phases have seen sustained and elevated moisture levels which has resulted in low and decreasing dielectric strength. The 69kV circuit breaker D is an FK type oil filled circuit breaker with no oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. Circuit breaker D is 1 of the 13 remaining FK-69-1500-3 model family remaining on the AEP system. This circuit breaker family is no longer supported by their original vendor and spare parts are scarce to non-existent. In addition, CB D has seen at least 148 faults; based on the maximum fault current levels available for this circuit breaker location, it has likely exceeded the manufactured life expectancy of cumulative fault current, 113kA. Huff Creek Substation currently deploys 74 relays, implemented to ensure the adequate protection and operation of the substation. Currently, all 74 (100% of all station relays) are in need of replacement. There are 60 of the electromechanical and 4 of the static type which have significant limitations with regards to spare part availability and fault data collection and retention in addition to a lack of vendor support. The remaining 10 microprocessor relays were commissioned in 1997 and 2007; the warranties are now expired and the firmware is no longer supported by the vendor. There appears to be little available panel space in the existing control house.
AEP-2018-AP007 | AEP | PJM West | 2018-10-26 | 2019-02-20 | 2019-08-29 | s1852 |  | Fieldale Station 138 & 69 kV circuit breakers | Fieldale Station: Circuit breakers "J" (recently failed), "T" (39 operations), and "F" (15 operations) are FK type oil breakers. The drivers for replacement are age, bushing damage, no repair part availability and PCB (polychlorinated biphenyl) content. PCB was used as coolant and lubricant in electrical equipment because of their insulation capabilities. Their manufacturing was stopped in 1977 because of evidence of environment issues and harmful health effects. Breakers "BC" (30 fault operations) and "AC" (31 fault operations) are air blast breakers. AEP is replacing air blast breakers across the system because of safety concerns. These types of breakers tend to fail violently, frequently dispersing porcelain shards from their bushings during failures which is a safety issue for station personnel. Breakers "G" (36 operations), "C" (47 operations), and "D" (27 operations) are also oil breakers but of the type ITE (CB G) and CF-48 (CB C & D). Oil breaker maintenance has become more difficult due to the oil handling required. CF-48 also are notorious for mechanical damage related to the breaker's open and close contacts. Circuit switchers "DD" and "EE" are Mark V type. Mark V's are an obsolete type that do not coordinate with modern relaying packages. Other drivers for replacement are age and no repair part availability. Transformer 3 is showing a breakdown in winding insulation (dielectric strength). It also shows C2H2 levels above IEEE thresholds. Age and short circuit strength breakdown (due to the amount of through faults suffered) is the main driver for replacement. Transmission lines coming out of Fieldale still have pilot wire protection. Copper pilot wire is an obsolete technology, and since the telephone companies almost never use it anymore, it is increasingly difficult to find suitable pilot wire cable and hardware. Consequently, we are avoiding like-kind replacement of pilot wire because the technology will be increasingly difficult to maintain. The Fieldale Synchronous Condenser was originally installed in 1974 and is one of only two facilities that provide dynamic voltage regulation and power factor compensation to the 138kV system around Glen Lyn and Roanoke, VA. The unit was initially capable of +/-250 MVAR but has since been de-rated to +158/-35 MVAR primarily due to the original Amplidyne excitation control replacement in 1997 with a Basler control. There are no replacement parts or factory support for this Basler unit. If the Basler unit was to fail, the machine would be off-line until a replacement excitation system could be procured and installed. The DFR is being replaced due to the maintenance and reliability issues experienced with its model. Protection systems for the condenser utilize electromechanical relaying that is obsolete with no available spares. There is no longer vendor support for the existing controls system as well as limited spare parts availability. APCo personnel have devised replacements and workarounds that allow operation of the synchronous condenser. Particular issues include inconsistent mechanical temperature switches, intermittent electrical relays in the control circuitry, and intermittent operation of auxiliary circuit breakers. Other problems occur at the interface between the original mechanical and analog controls and more modern digital controls that have been added to the system, making startup syncing difficult. The existing device has multiple problems with the cooling such as water leakages. Corrosion of the steel parts of the cooling system is becoming more of a concern from a machine reliability standpoint. There is no longer vendor support for the cooling system which has made spare parts difficult to procure. Environmental concerns include the use of mercury in some switches (26 units with approx. 2 ounces of mercury per unit), the use of asbestos for insulation, and the possibility of bacterial contamination in the cooling system. Due to the open loop cooling system being at a higher risk to develop bacteria, respirators are required when cleaning the cooling pit during maintenance. DuPont Station: 69 kV circuit breakers 'A' (8 operations), 'B' (38 operations) and 'C' (14 operations) are GE 'FK' oil-filled breakers which have little to no replacement parts and were installed in 1960, 1959 and 1968 respectively. In general, oil breakers have become increasingly difficult to maintain due to the associated oil handling. Oil spills are frequent with failures and routine maintenance, which is an environmental hazard. Blaine Station: Circuit Switcher 'AA' is a Mark V switcher, which is no longer supported by the manufacturer and parts are not available. Parts are increasingly difficult to locate during maintenance. These are older designed circuit switchers with old controls that no longer coordinate well with modern relaying. Morris Novelty: 34 kV circuit breaker 'E' and 'F' are GE 'FK' oil-filled breakers which have little to no replacement parts. In general, oil breakers have become increasingly difficult to maintain due to the oil handling associated with them. Oil spills are frequent with failures and routine maintenance which is also an environmental hazard. Rich Acres: Because of pilot wire retirement on this line, a new circuit switcher on transformer #1 will be needed to coordinate with new line relays on the Fieldale - Ridgeway 69 kV line.
AEP-2018-AP008 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1853 |  | 69 kV delivery point at VTES | Virginia Tech Electric Service (VTES) requested a new 69 kV delivery point from AEP's Lane substation located in Blacksburg, VA to serve 5 MW of new load.
AEP-2018-AP009 | AEP | PJM West | 2018-11-29 |  |  |  |  | Babcock & Wilcox Upgrade Request. | Babcock & Wilcox (B&W) requested to upgrade their existing 12 kV service to 69 kV and be served directly from the B&W 69 kV bus. Expected peak demand is approximately 16 MVA.
AEP-2018-AP010 | AEP | PJM West | 2018-11-29 |  |  |  |  | Paintsville, KY | From 2013-2018 the Falcon -Prestonsburg 46 kV circuit (~ 23 miles) has experienced 19 momentary and permanent outages. Over the last three years the circuit has experienced 1.77 million customer minutes of interruption. The ~14.5 mile 46 kV line section between Falcon and Middle Creek has 84 category A open conditions associated with the structures that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. The majority of this line utilizes 1950s wood structures and 3/0 ACSR conductor. The ~8.5 mile 46 kV line section between Middle Creek and Prestonsburg has 27 category A open conditions associated with the structures that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. About half the structures that make up the line are 1940s wood structures with the majority of the line utilizing 1/0 Cu. conductor.
AEP-2018-AP011 | AEP | PJM West | 2018-11-29 |  |  |  |  | Capacitor switchs at Inez station | Capacitor switchers ‘BB’ and ‘CC’ at Inez station are Mark V model which no longer support modern relaying packages. Mark V’s have been historically prone to mechanism failures and are being replaced system wide where possible. S&C circuit switcher ‘AA’ at Inez station is an S&C 2030 type with no gas monitor. The Inez 138 kV yard was designed as a breaker and a half station, but the ‘B’ string was never completed leaving dissimilar zones of protection between the #1 bus and 20+ mile Inez to Johns Creek 138 kV circuit. Dissimilar zones of protection also exist between the 138 kV bus #2, 138/69 kV transformer #1, and the 138 kV circuit to the Martiki coal service point.
AEP-2018-AP012 | AEP | PJM West | 2019-01-11 | 2019-08-29 |  |  |  | 138 kV air-blast breakers across AEP system. | 138kV circuit breakers A, A1, B, B1, B2, D, D1, D2, E, E1, E2 are all PK type air blast breakers that were manufactured between 1971-1975. Air blast breakers are being replaced across the AEP system due to their potential for catastrophic and violent failures. During failures, sharp pieces of porcelain from their bushings are typically expelled from the breakers and can be a safety hazard to field personnel. In addition, breakers A, A1, B, B1, E, E1 have experienced 40, 28, 11, 17, 75, and 96 fault operations, which exceed the manufacturer's designed number of 10 fault operations.
AEP-2018-AP013 | AEP | PJM West | 2019-01-11 |  |  |  |  | Lakin - Racine 69 kV circuit condition | The Lakin - Racine 69 kV circuit (~13.2 mi) currently has 125 open conditions on 63/91 structures. These conditions include rot top, woodpecker damage, burnt insulator, broken knee/V braces. The majority of the circuit is constructed with 1960s wood structures. From 2015-2018, the line has experienced 8 momentary and 3 permanent outages which have resulted in 27k customer minutes of interruption. The 69kV CB F at Lakin is a CF type oil filled breaker. Oil filled breakers have significant maintenance requirements due to oil handling. This CB model family has experienced numerous documented mechanism bearing issues and failures within the AEP population. Lakin Substation deploys 42 relays implemented to ensure the adequate protection and operation of the substation. Currently 35 of the 42 relays (83% of all station relays) are in need of replacement. There are 32 electromechanical, 2 legacy ABB DPU microprocessor, and 1 static type relays with significant limitations in regards to spare part availability in addition to a lack of vendor support. The electromechanical and static relays have no capability for fault data collection and retention. The ABB DPU relays pose a safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. If there is any arcing or something goes wrong as the breaker operates, the operator is now in the line of fire.Ã‚Â Modern relays can program a delay (10 seconds) after an open or close button is pressed so the operator can have time to walk out of the line of fire. The 138kV line switches are mounted on cap and pin insulators at Lakin. The current MOAB/Ground SW configurations at Lakin create faults in the station to signal the remote end breakers to open; this results in Transmission lines breakers getting burdened to clear Transformer faults thus reducing their life span. Lakin 138/69 kV transformer bank #1 CO and CO2 levels have been on the rise since 2004 when all transformer bushings were replaced during minor transformer maintenance activities; the oil was processed at that time, accounting for the rapid decrease in gas concentrations in 2004. The latest CO reading of 493ppm is significantly high. Moisture content had been trending up from 2008 to 2016 and has been in excess of 25ppm since 2016. Dielectric strength is currently trending up, but this rapid and significant 15.1kV increase was unexpected given the minor drop in moisture content levels from 2016 to 2017. Together, these are potential indicators of insulating paper breakdown. In addition, H2 concentrations have been rising since 2004. The presence of H2 indicates the potential for stray gassing in the oil and carbonization of the insulating paper. The above conditions indicate a strong probability of degradation of the integrity of the paper insulation surrounding the transformer windings from carbonization, breakdown in cellulose, or both.
AEP-2018-AP014 | AEP | PJM West | 2019-01-11 | 2019-06-17 |  |  |  | Huntington Court 138 kV cap switcher | Huntington Court 138 kV cap switcher BB is a MARK V type which has experienced significant failures and mis-operations across the AEP system. 69 kV cap switcher AA is an SC-2030 type that has no gas monitor and sister units have experienced numerous gas and interrupter failures.
AEP-2018-AP015 | AEP | PJM West | 2019-01-11 | 2019-06-17 |  |  |  | 138 kV circuits breakers at Matt Funk Station | At Matt Funk Station 138 kV circuits breakers H1, K, K1, K2 are PK Air Blast breakers manufactured in 1968. Air blast breakers are being replaced across the AEP system due to their potential for catastrophic and violent failures. Other factors driving the replacement are age and scarce availability of spare parts. In addition, breakers H1, K, K1, K2 have experienced 55, 31, 32, and 26 fault operations, respectively.
AEP-2018-AP016 | AEP | PJM West | 2019-01-11 |  |  |  |  | Wythe 138/69 kV transformer | Wythe 138/69 kV transformer has experienced thermal through fault events, mostly in excess of 700 C, have led to numerous overheating events, steady increases in gasses including high levels of ethylene and ethane, and carbonization of the insulating paper. The oil's interfacial tension is showing signs of sludge beginning to form due to the carbonization created contaminants. In addition, the moisture content is beginning to climb which has not yet been reflected in a drop in dielectric strength. Wythe circuit breaker F is an FK type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. The FK-439-115-3500-3 is no longer vendor supported and is 1 of 2 remaining on the AEP system, making spare parts difficult or impossible to acquire. Wythe circuit breaker M is a CF type oil filled breaker. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. This particular unit has a recorded malfunction related to a broken S.S. line on the maintenance valve and pressure switches. Byllesby circuit breakers B and D are oil filled breakers manufactured in 1952 and 1965 respectively. Both breakers have exceeded the designed number of fault operations (10). These breakers are GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Galax circuit breakers G, F, and H are all GE FK type oil breakers with no oil containment. The GE FK type breakers are known to have an internal operating mechanism that are prone to high failure rates. Circuit Breakers G, F, and H are all approximately 50 years old and have exceeded the designed number of fault operations (10). Jubal Early 138/69kV Transformer has reoccurring bushing damage, dielectric strength breakdown (insulation breakdown) and short circuit breakdown (due to fault events). Recent test reports show oil interfacial tension to be below the minimum acceptable level for a unit of this voltage class. Reduction in oil interfacial tension is related to oil contamination and presence of oxidation byproducts in the oil. Huffman - Willis Gap 138 kV is a 15 mile long radial line that serves approximately 25 MVA of load at Willis Gap 138 kV station. There is approximately a total of 230 MVA of load being served on the 138 kV and 69 kV networks throughout Carroll County, Wythe County, Grayson County and Galax City. Approximately 120 MVA is served off of the 138 kV line from Jacksons Ferry - Huffman - Wythe. The 69 kV network around Cliffview/Galax/Fries serves approximately 110 MVA. Under N-1-1 scenarios involving the 138 kV sources there is the potential to drop all 230 MVA of load. Originally, AEP proposed supplemental project S1295 to address this concern. Based on recent needs identified in Floyd County VA, AEP believes a more holistic solution exists to resolve these needs collectively. AEP has recommended cancelation of supplemental project S1295 (Presented 5/31/2017 SRTEAC).
AEP-2018-AP017 | AEP | PJM West | 2019-01-11 |  |  |  |  | 138 kV breakers at West Kingsport station | 138 kV circuit breaker "E" at West Kingsport station is a type FX-11 breaker, which is one of only two remaining circuit breakers of this class on the AEP system . Due to a lack of spare replacement parts, it is not possible to maintain the breaker in the event of a failure. Breaker "E" has had historical issues with gas leaks. In addition, this circuit breaker has experienced 30 fault operations exceeding the manufacturers recommendation 10. Currently dissimilar zones of protection exist at the West Kingsport between the 138 kV bus #1, 138 kV circuit towards North Bristol (~25 miles), and the 138 kV service point towards the Royal Ordnance Ammunitions Plant. The existing configuration at West Kingsport station results in an outage of the entire 138 kV yard and all customers served from the station for a failure of 138 kV circuit breaker "G".
AEP-2018-AP018 | AEP | PJM West | 2019-01-11 |  |  |  |  | Chemical 138/46 kV transformer no. 1 | Chemical 138/46 kV XF #1 has been declared a failure. Operations has noted that Chemical 138/46 kV XF #1 fans and cooling system are not working properly and winding temperature was documented at an extremely hot level of 109 C prior to taking the unit offline in 2017.Ã‚Â There are no parts attainable to repair the obsolete cooling system. In addition, interfacial tension has been diminished since 2002. This is an early indication of the development of sludge which can impede oil circulation, further hampering the ability of the unit to cool. Based on dissolved gas analysis, the observed gas concentrations, specifically of ethylene and acetylene, are likely the result of a mixture of thermal and electrical faults along with the carbonization of the insulating paper. The signal of insulation paper carbonization, which generates particles in the oil, highly correlates to the generation of sludge indicated by the interfacial tension. Chemical 138/46 kV XF #2 moisture levels have recently been increasing, resulting in downward trending dielectric strength. In addition, interfacial tension has been on the decline. This is an early indication of the development of sludge which can impede oil circulation and cooling. Operations has noted numerous conditions with this unit, most critical of which is that the bank was derated to 33.75MVA because only one pump of three is operational for the cooling system. There are no parts attainable to repair the obsolete cooling system. The 46kV CBs C, G, H, Q, R, and S are oil filled breakers without secondary oil containment. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 equivalents do not require. CBs G and H are 2 of 40 in the FK-72.5-27000-10 model family remaining on the AEP system. CB A is the last FK-339-46-1500-Y model on the entire AEP system. CBs B, Q, R, and S are the last 4 in the FK-339-46-1500-5 model family remaining on the entire AEP system. CB C is the last FK-46-1500 model on the entire AEP system. This scarcity of sister units makes finding spare parts for these units difficult to impossible, and these models are no longer vendor supported. The 46kV CS CC is an S&C 2030-69 model. The S&C 2030 circuit switcher model family has no gas monitor and sister units on the AEP System have experienced malfunctions; the major ones include gas loss, interrupter failures, and operating mechanism failures.
AEP-2018-AP019 | AEP | PJM West | 2019-01-11 |  |  |  |  | Nitro 69 kV circuit breakers | Nitro 69 kV circuit breakers G and H are CF-48 oil type breakers that were manufactured in the 1960s. In general, oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance, which could cause environmental and safety hazards. In addition, breakers G and H have experienced 42 and 39 faults of operation, respectively. These both exceed the manufacturers designed number of fault operations of 10. "
AEP-2018-AP020 | AEP | PJM West | 2019-01-11 |  |  |  |  | Condition of Claytor - West Bassett 138 kV circuit | The Clayton - West Bassett 138 kV circuit (38.1 mi.) consists primarily of 1948 vintage wood pole structures with 556 ACSR overhead conductor and currently has 255 open conditions on 126 unique structures including rot top, rot heart, broken insulators and woodpecker/insect damage. From 2015-2018, a total of 7 permanent outages resulted in 167,488 customer minutes of interruption. The Fieldale - West Bassett 138 kV circuit (6.5 mi.) consists primarily of 1948 vintage wood pole structures with 556 ACSR overhead conductor and currently has 48 open conditions on 29 unique structures which is 71% of the circuit. Conditions include rot top, rot heart and woodpecker damage. Fieldale - Stuart 69 kV circuit (19.2 mi.) consists primarily of 1939 vintage wood pole structures and currently has 178 open conditions including broken cross-arms, broken conductor strands, damaged shield wire and woodpecker damage. From 2015-2018, a total of 6 permanent outages and 12 momentary outages were observed. Fieldale - West Bassett #1 69 kV circuit (7.1 mi.) consists primarily of 1926 vintage wood pole structures with 4/0 ACSR and 556 ACSR overhead conductor and currently has 23 open conditions on 21 unique structures including rot top, insect damage, broken ground wire, leaning in-line pole and woodpecker damage. Fieldale - West Bassett #2 69 kV circuit (6.9 mi.) consists primarily of 1962 vintage wood pole structures with 336 ACSR and 556 ACSR overhead conductor and currently has 20 open conditions on 16 unique structures including rot top, broken cross-arms, insect damage, loose knee brace and woodpecker damage. Stuart Station The 69kV CBs D and E are oil filled breakers without secondary oil containment. Oil filled circuit breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. CBs D and E are 2 of 15 in the FKA-72.5-19000-1 model family remaining on the AEP system. This scarcity of sister units makes finding spare parts for these units unviable, and these models are no longer vendor supported. A malfunction report from 2005 documented that CB D was slow to trip on a lightning fault on the Fieldale-Stuart circuit and that CB F at Floyd cleared it; this report also mentioned that this was the second such occurrence of a low trip for CB D. The 69kV CS AA is an S&C 2030-69 model. The S&C 2030 circuit switcher model family has no gas monitor and sister units on the AEP System have experienced malfunctions since 1999; the major ones include gas loss, interrupter failures, and operating mechanism failures. Stuart Substation deploys 48 relays, implemented to ensure the adequate protection and operation of the substation. Currently 45 of the 48 relays (94% of all station relays) are in need of replacement. There are 39 electromechanical type and 3 static type relays with significant limitations in regards to spare part availability in addition to a lack of vendor support and no capability for fault data collection and retention. West Basset Station The 138 kV CB A is a GE FK oil type breaker that has seen 77 fault operations over its in-service life. It is one of only 13 remaining of its model type (FK-439-5000) on the entire AEP system; spare parts availability is a major concern. The 72.5 kV CBs J, K, and L are GE FK oil type breakers as well with CB L seeing 40 fault operations over is in-service life. These are three of only 27 remaining of the their model type (FK-72.5-27000-1) on the entire AEP system; spare parts availability is a major concern. In addition, these four oil filled breakers have much more maintenance required due to their oil handling that their modern SF6 counterparts do not require. The 138/69/34 kV transformer #1 has an upward trending of oil moisture content resulting in decreasing oil dielectric strength. Increasing moisture content is a result of water ingress and/or break down of paper insulation of TF windings. The moisture content has since decreased without improvement to the dielectric strength. Short circuit strength breakdown caused by the amount of thermal through fault events, mostly in excess of 700 C, has lead to major gassing of the unit and carbonization of the insulating paper. West Bassett Substation currently deploys 62 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 55 of the 62 relays (89% of all station relays) are in need of replacement. There are 53 electromechanical and 2 static type with significant limitations in regards to spare part availability and fault data collection and retention in addition to a lack of vendor support. Floyd Station The existing MOAB ground switch design on the high side of transformer #2 needs to be replaced with a circuit switcher to improve the protection scheme and safety of personnel in the station. AEP has been strategically targeting ground switch MOABs for replacement due to the burden that these devices place on Transmission circuit breakers for clearing Distribution Transformer faults.
AEP-2018-IM002 | AEP | PJM West | 2018-10-26 |  |  |  |  | Pokagon Station circuit breakers | The Pokagon Station CBs J, E, and H are oil filled breakers without oil containment Fault operations: CB E(28), CB H(61) - Recommended (10) Lake Street Station CBs A and H are oil filled breakers without oil containment CB H is a GE FK type which are known to fail violently Fault operations: CB A(24), CB H(13) - Recommended (10) Transformer 1 - 1969 vintage CO2 IEEE level 3 Moisture level high and rising Wood tie supports Niles Station CBs A, B, M, and N are oil filled breakers without oil containment CB M and CB N are GE FK type which are known to fail violently Fault operations: CB A(30), CB B(42), CB N(21) - Recommended (10) Transformer 2 - 1969 vintage CO2 IEEE level 3 Moisture level high and rising Wood tie supports Lake Street - Niles 69kV circuit 1960's wood cross arm construction Poor shielding condition Lakehead Pumping Tap has open conditions on 30% of structures Total open conditions - 54 Lake Street - Niles 34.5kV circuit 1965 wood pole construction Total open conditions - 51 40% of structures with open conditions 97% of line original wood poles Wooden cross arm with cap and pin insulator construction No shield wire
AEP-2018-IM004 | AEP | PJM West | 2018-10-26 | 2019-04-23 |  |  |  | Hartford City, Indiana Area | Bosman-Delaware 34.5kV 1950's wood crossarm construction 3/0 copper conductor. It's subject to 45 category A conditions It's subject to 39 category B conditions Bosman Station Station currently resides in the regulatory floodway which presents safety and reliability risks. Transformer 1-1956 vintage High levels of carbon dioxide dissolved in the oil. Several fault events between 300-700 degrees Celsius which has caused short circuit strength breakdown Breakers N" and "M" 1970 FK oil type breakers with no oil containment. Fault Operations: CB N(38) CB M(76) - Recommended (10) Hartford City Station Transformer 1-1963 vintage Elevated levels of Ethylene and Ethane dissolved in the oil. Subject to multiple fault events exceeding 700 degrees Celsius which led to short circuit strength breakdown 3M Station Breaker A 1967 FK oil filled breakers without oil containment. Fault Operations: CB A(23) - Recommended (10) "
AEP-2018-IM005 | AEP | PJM West | 2018-10-26 | 2018-11-29 | 2019-04-12 | s1791 |  | Connection request off of The Pokagon Station | A customer has requested connection of a 2.3MVA load off of the The Pokagon Station .
AEP-2018-IM007 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1854 |  | Medford Station | Medford Station Transformer 1 – 1959 Vintage Extremely high values of combustible gasses Overheating faults have occurred within the unit. Interfacial tension and the power factor values are at concerning levels proving the oil quality degradation Breakers “A” “B” and “C” 1943-53 vintage FK oil breakers without containment Fault Operations: CB A(53) CB B(27) CB C(21) – Recommended(10) 23rd Street Station Breakers “B”, “C”, “D”, “E”, “G”, “J” and “K” 1971 vintage FK oil breakers without containment Fault Operations: CB B(30) CB C(44) CB D(16) CB E(0) CB G(25) CB J(18) CB K(28) – Recommended(10) Arnold Hogan Distribution XF 2 – 1970 Vintage Experienced a failure in 1999 Blaine Street Station Breaker “E” 1970 vintage oil filled FK-breakers without oil containment Fault Operations: CB E(29) – Recommended(10) Arnold Hogan – 23rd Street 1963 wood crossarm construction 3/0 copper and 4/0 ACSR Subject to 20 open A conditions Subject to 26 open B conditions In the past 10 years, 47 structures have had active maintenance performed. This is expected to increase as line ages. Elmridge Tap 3 terminal line outside of Elmridge Station. Arnold Hogan Station AEP Distribution has requested a new delivery point at Arnold Hogan Station Delco Battery Site AEP Distribution has requested a new delivery point at the old Delco site to facilitate the industrial load pocket Transmission has received multiple customer requests at the industrial park near Delco Battery Site
AEP-2018-IM008 | AEP | PJM West | 2018-10-26 | 2019-02-20 | 2019-08-29 | s1855 |  | Deer Creek - Delaware 138 kV line | Portions of Deer Creek - Delaware 1920's vintage steel lattice line. 397.5 ACSR Double Circuit 439 open structure and conductor category A and B conditions
AEP-2018-IM010 | AEP | PJM West | 2018-10-26 | 2019-04-23 |  |  |  | Elwood, Indiana | Jonesboro - South Summitville 1930's wood crossarm construction #2 copper Over the past 10 years this line has had 128 structures require active maintenance with the majority being wood rot. This trend is expected to increase as the line ages. 68 structures currently have an open condition South Elwood Breaker "C" 1951 FK oil type with no oil containment Fault Operations: CB C(19) - Recommended (10) Transformer 1 - 1955 vintage Type O Westinghouse bushings Increasing power factor Increasing Carbon Monoxide Failed internal heater circuit. Physically obstructs other station assets. Fairmount Breakers "A" and "B" Fault Operations: A(75) B(99) - Recommended(10) Transformer 1 - 1972 vintage High Carbon Dioxide level Dielectric issues Peacock Breaker "A" 1969 PR Oil breaker without containment Fault Operations: A(154) - Recommended(10) Transformer 1 - 1951 Vintage High levels of Ethane, Methane, and CO2. Increasing Insulation power factor. Both AEP Transmission and AEP distribution have received multiple inquiries about future economic development in the area around South Summitville. The current system would require significant rework in order to facilitate these requests, and the timeline for those fixes are not conducive to customer timelines. The 34.5kV system is subject to "Drop and Pick" operating procedure due to being out of phase with the 138 kV system. This operating procedure has been an issue for I&M Distribution operations as it results in less reliable service for the customer and causes outages that could otherwise be avoided.
AEP-2018-IM012 | AEP | PJM West | 2018-10-26 |  |  |  |  | Kline Station Rebuild, Indiana | Kline 69 kV Station * Breakers A, B & C 34 kV * 1968 vintage GE FK Oil breakers * Fault operations: CB A(95), CB B(28) & CB C(15) - Recommended (10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported. * They also have Bushing Problem and High Moisture Reading * Cap Switcher AA * 1989 vintage * Mark V type * Doesn't coordinate with AEP's standard relaying package * Transformer #1 138/34 kV * 1978 vintage * High levels of Carbon Dioxide * Interfacial tension is below the acceptable limit * Oil is severely aged * Accelerating aging of insulation * Transformer rusted due to leaking issues * Cooling system does not work. * Equipment condition concerns include dielectric strength breakdown (winding insulation), short circuit strength breakdown (due to the amount of through fault events), and accessory damage (bushings).
AEP-2018-IM014 | AEP | PJM West | 2018-10-26 |  |  |  |  | Columbia Station 69 kV circuit breakers | Columbia Station Circuit Breakers J 69kV Vintage 1968 GE FKA type oil-filled breakers - without oil containment Fault operations: CB A(95) - Recommended (10) Trip coil failure Spring charging motor failure Gateway Station Circuit Breaker E 69kV 1975 vintage GE FKA type oil-filled breakers - without oil containment Fault operations: CB E(49) - Recommended (10) Three documented instances of breaker failing to close Wallen-Whitley 34.5 kV circuit 1945 vintage wood pole construction Total Structures - 689 Total Open Conditions - 124 Customer Outage Minutes - 613,727 Insect Damage, Rotten Poles, Broken/Burnt cross-arm, Woodpecker holes, broken/burnt insulators and stolen/broken ground wires Gateway-Whitley 34.5 kV circuit 1965 vintage wood pole construction Total Structures - 37 Total Open Conditions - 11 Broken Strands, Split Cross-arm, Rotten Poles and Broken Insulators. Currently, two delivery points to Northeastern REMC (Eel River and Union Stations) are served radially out of Carroll Station by two separate 4 mile 34.5 kV radial lines, leaving each delivery point susceptible to single event outages.
AEP-2018-IM017 | AEP | PJM West | 2019-01-11 | 2019-05-20 |  |  |  | Deer Creek 34.5 kV breakwea | Deer Creek 34.5kV Breakers “K”, “F”, “M”, “H”, “V”, “W” 1949-62 vintage FK oil breakers without containment Fault Operations: CB K(9) CB F(1) CB M(17) CB H(16) CB V(5) CB W(1) CB U(38)– Recommended(10) CB W is over the recommended amount of switching operations. Deer Creek – Miller Ave 34.5kV (6.1 Miles) 1952 wood crossarm construction (age based on age of station) 3/0 copper Subject to 15 open B conditions Subject to 13 open A conditions In the past 10 years, 37 structures have had active maintenance performed. This is expected to increase as line ages. Grant – West End 34.5kV (2.1 Miles) 1950 wood crossarm construction (age based on age of West End station) Legacy Cap and Pin type insulators Subject to 5 open conditions In the past 10 years, has had to have 65 open conditions addressed Deer Creek – Marion 34.5kV (3.6 Miles) 1949 wood crossarm construction (age based on age of Deer Creek breaker) Legacy Cap and Pin type insulators Subject to 5 open conditions In the past 10 years, has had to have 26 open conditions addressed Deer Creek – Marion Plant 34.5kV 4 Moabs in series
AEP-2018-IM018 | AEP | PJM West | 2019-01-11 | 2019-05-20 |  |  |  | Jay - College Corner 138kV line | Jay - College Corner 138kV line 1941 & 1951 vintage wood H frame line Non-standard EHS Steel Shield Wire The most recent 6-year inspection showed 91 open conditions (A:52 B:39) with the majority being structural issues. In the past 10 years 97 structures have had to have active maintenance on them. This trend is expected to increase as the structures and conductor age. In the past 5 years AEP has experienced 13 scheduled outages and 2 forced momentary outages.
AEP-2018-IM019 | AEP | PJM West | 2019-01-11 |  |  |  |  | Mottville Hydro Station 34.5 kV grounding transformers | Mottville Hydro Station - 1975 vintage 34.5kV grounding transformers carbon dioxide is at IEEE level 3 PCB"s and obsolete bushings Moore Park Station - CB C is a 23 year old 69kV SF6 Breaker (ABB - 72PM31-20) 38 fault operations 38 recorded instances of SF6 additions since 2006 Stubey Road Station - Transformer high side ground switch Sturgis Station - CB A and B 63 year old oil CBs with 37 and 28 fault operations, respectively Replacement parts are very difficult to find for these legacy units Moore Park Tap 69 kV - 1960s vintage wood structures 20 poles identified with structural integrity concerns Part of a three terminal line (~9 miles) Sturgis - Howe (NIPSCO tie) - Vintage 1950s wood cross arm construction with suspended insulators (~3 mi) low capability 4/0 ACSR HMD Station - Permanently jumpered disconnects on main bus Sturgis - Howe (NIPSCO tie) Outage constrained - difficult to outage due to local dependence
AEP-2018-IM020 | AEP | PJM West | 2018-10-26 | 2019-05-20 |  |  |  | Delaware station | Delaware Station Breakers “C”, “H”, “I”, “L”, “M” and “N” 1963-1971 FK oil breakers without oil containment Fault Operations: CB C(6) CB H(27) CB I(50) CB M(57)– Recommended(10) Delaware – Haymond 1948 wood 5 circuit construction 3/0 Copper 22 open A conditions 13 open B conditions Delaware – Jay 1920’s Vintage wood crossarm construction 1/0 Copper conductor 100 structures had to undergo active maintenance in the last 10 years and this trend is expected to rise as the line ages. 55 open A conditions 33 open B conditions 556,661 CMI Barley Station AEP Distribution has requested a new delivery point off of the 138kV line near Barley station.
AEP-2018-IM021 | AEP | PJM West | 2018-10-26 | 2019-05-20 |  |  |  | Arnold Hogan – Kenmore 34.5 kV line | *Arnold Hogan – Kenmore 34.5kV*1930’s and 1960’s vintage construction*3/0 copper and 336.4 ACSR conductor*15 of the 47 structures had to undergo active maintenance in the last 10 years and this trend is expected to rise as the line ages.*Majority of current and past maintenance concerns relate to integrity of structures and crossarms
AEP-2018-IM022 | AEP | PJM West | 2019-01-11 | 2019-06-17 |  |  |  | Hummel Creek 34.5 kV breakers | Hummel Creek 34.5kV Breakers “L” and “M” 1949-1950 vintage FK oil breaker without containment Fault Operations: CB M(33) CB L(2) – Recommended(10) Gas City 34.5kV Breakers “A” 1940 vintage FK oil breaker without containment Fault Operations: CB A(50) – Recommended(10)
AEP-2018-IM023 | AEP | PJM West | 2019-01-11 |  |  |  |  | Deer Creek – Hummel Creek 34.5 kV line condition | Deer Creek – Hummel Creek 34.5kV (11 miles) 1940 wood crossarm construction (age based on age of station) Subject to 16 open A conditions Subject to 17 open B conditions In the past 10 years, 16 structures have had active maintenance performed. This is expected to increase as line ages.
AEP-2018-IM024 | AEP | PJM West | 2019-01-11 |  |  |  |  | Miller Avenue 34.5 kV breakers | Miller Avenue 34.5kV Breakers “A” and “B” 1950 vintage FK oil breaker without containment Fault Operations: CB A(10) CB B(16) – Recommended(10)
AEP-2018-IM025 | AEP | PJM West | 2019-01-11 | 2019-04-23 |  |  |  | Deer Creek 34.5 kV breakers | Deer Creek 34.5kV Breakers “U” 1949-62 vintage FK oil breakers without containment Fault Operations: CB U(38)– Recommended(10)
AEP-2018-IM026 | AEP | PJM West | 2019-01-11 |  |  |  |  | Grant Tap 138 kV 3-terminal line | Grant Tap 138kV There is a three terminal line about 4 miles outside Deer Creek station.
AEP-2019-IM035 | AEP | PJM West | 2019-08-29 |  |  |  |  | South Bend, Indiana & Michigan Area | South Bend – Niles 69 kV Line (~11.47 Miles) •1968 vintage wood pole construction •Forced Momentary outages: 5 •Forced Permanent outages: 3 •Total structure related open conditions – 47 •Unique structure count with open conditions – 44 •Insect Damage, Rotten Poles, Broken/Burnt cross-arm, Woodpecker holes, broken/burnt insulators, stolen/broken ground wires, broken guy strain insulators and cracked stub pole. •More than three in-line sectionalizing MOABS
AEP-2018-OH001 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1856 |  | Customer load request for the City of Wapakoneta | Obligation to serve new customer load for the City of Wapakoneta. Total future load expected to be served from Gemini station is approx. 127MW. The total 127 MW future load includes an additional estimated 40MW of new load from other new potential customers at the same location.
AEP-2018-OH002 | AEP | PJM West | 2018-10-26 | 2019-02-20 | 2019-08-29 | s1857 |  | Customer 138 kV delivery request near Babbitt station | A new customer delivery point has been requested. *Initial load of 150MW with permanent service available by Q1-2020. *Ultimate load for this customer is projected to reach 720MW as early as Q4 2026. *10 MW of distribution construction power for this customer is required in May 2019. 7 MW of distribution construction power for an existing customer planning to expand is also required in 2019. The existing customer has reserved distribution capacity for up to 10 years of expansion activity. As a result, AEP-Ohio has requested a 138kV delivery Point at Babbitt station to serve a “temporary” skid station for up to 10 years. *Additional large customers are in discussions to take service in this area. *Facilities will be designed to accommodate anticipated future load but only facilities required to serve committed load will be constructed.
AEP-2018-OH003 | AEP | PJM West | 2018-10-26 |  |  |  |  | 138 kV delivery point request near Don Marquis Substation | The US Department of Energy has informed AEP of its intention to retire its existing X-530 345 kV Station, adjacent to AEP's Don Marquis Substation. The DOE has requested a new 138 kV delivery point at the same location.
AEP-2018-OH004 | AEP | PJM West | 2018-10-26 |  |  |  |  | Load requests in the Dublin, OH area | AEP has received requests for increased demand in the Dublin, Ohio area. Analysis shows Bethel - Sawmill 138 kV will be a constraint. Consequent inspection identified clearance violations along the Bethel - Sawmill 138 kV line. AEP has de-rated the thermal capacity of the line to mitigate potential safety issues. Brookside-Sawmill -> N-1-1=127%, N-1=117% Bethel-Brookside -> N-1-1=102%, N-1=92% (N-1-1: Bethel - Roberts 138 kV + Davidson - Roberts 138 kV) AEP believes that the loading issues exist today due to the recent 30% de-rate of the line. Newly connected customer loads are scheduled to ramp up, significantly contributing to area thermal concerns.
AEP-2018-OH005 | AEP | PJM West | 2018-10-26 |  |  |  |  | Loading of the Dublin-Sawmill 138 kV circuit | The Dublin-Sawmill 138kV circuit will experience loading of 116% under N-1-1 conditions involving the loss of Bethel-Davidson 138kV & Davidson-Roberts 138kV circuits. With load growth in the area, we anticipate this line to overload starting in 2022. AEP-Ohio has requested a third 138kV source to Dublin station to maintain acceptable reliability levels for the load at risk. Dublin Station serves 75 MVA of peak demand with minimal load transfer capability. Dublin station serves some critical loads. Newly connected customer loads are scheduled to ramp, significantly contributing to area thermal concerns.
AEP-2018-OH006 | AEP | PJM West | 2018-10-26 |  |  |  |  | Killbuck - South Coshocton 34 kV line condition | The Killbuck - South Coshocton 34 kV line (30.18 mi) was constructed in 1926 using wood pole structures and conductor ranging from 3/0 Copper (23 MVA rating) to 336.4 ACSR (37 MVA rating). There are 144 open A conditions on this line, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Killbuck - South Coshocton 34 kV line has experienced over 1 million CMI over the past three years. The Killbuck - South Millersburg 34 kV (2.59 mi) line was constructed in the 1920'susing wood pole structures with 336.4 ACSR (36 MVA rating). There are 53 open A conditions on this line, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Killbuck - South Millersburg 34 kV line has experienced over 1 million CMI over the past three years. At South Coshocton 69 kV circuit breaker 'K' (fault ops 18), 34.5 kV circuit breakers 'A' (fault ops 3), 'B' (fault ops 7), 'C' (fault ops 72), 'D' (fault ops 0), 'E' (fault ops 0), and 'G' (fault ops 2) are 'FK' oil-filled breaker (vintage 1946 -1973). These oil type breakers have extensive maintenance and oil handling requirements. There is a potential for oil spills during fault operations and maintenance. The FK model is no longer supported by the manufacturer making spare part availability scarce. The South Coshocton 138 kV circuit breaker 'H' has had 11 malfunctions, 3 of which are confirmed to be related to low gas. This HS145-3000 model is prone to low gas malfunctions. The South Coshocton 138/34.5 kV transformer's dielectric strength has declined for the past seven years. Concentrations of CO2 are elevated as well. These conditions indicate that the insulating paper is deteriorating. The South Millersburg 34.5 kV circuit breakers 'A' (fault ops 3) and 'B' (fault ops 21) are 'FK' oil-filled breakers (vintage 1951 and 1953 respectively). These oil type breakers extensive maintenance and oil handling requirements. The FK model is no longer supported by the manufacturer making spare part availability scarce. The South Millersburg 138/34.5 kV transformer has elevated moisture levels for at least seven years with a recent sharp increase. The dielectric strength has corresponding decreased since 2016. Concentrations of CO2 are also elevated Customer Service: Customer #2 Holmes-Wayne Co-op (at Stillwell) and AEP Ohio (at Glenmont) are currently served via a radial 34.5 kV (12.58 mi) line. The Stillwell delivery point has accumulated 1.7 million CMI over the past five years. Over the last 10 years (2008-2017), Stillwell delivery point has averaged nearly 875,000 CMI/year. Customer Service: Customer #3 Licking and Holmes-Wayne members are currently served via a radial 69 kV (24.1 mi) line. The North Liberty to Jelloway radial line is 9.50 miles and the Ripley to Loudonville radial line is 14.16 miles. Their total load is 8.73 MVA and they have experienced 1.13 million CMI over the last three years.
AEP-2018-OH007 | AEP | PJM West | 2018-10-26 |  |  |  |  | Condition of 138/34 kV transformers and 34 kV circuit breakers at New Liberty, North Baltimore, and North Findlay Stations | The 138/34kV transformers and 34kV circuit breakers at New Liberty, North Baltimore, and North Findlay Stations have significant asset renewal needs. Between these three stations (17) 34.5kV circuit breakers/ circuit switchers have been identified as needing replacement, 15 of which are oil filled (vintage1950's) and have seen a high number of faults operations. Short circuit capability is also a concern for many of these 34.5 kV breakers at the New Liberty and North Findlay. North Findlay Station: 34.5kV CBs F, G, H, J, K, L 34.5kV circuit switcher BB Transformers #1 and 2 New Liberty Station: 34.5kV CBs C, E, G, H, I, J Transformers #1 and 2 North Baltimore Station: 34.5kV CBs A, B, C, E Morrical Switch 34.5kV CB A Morrical Switch Evaluation of the station has shown the wooden bay structures, the 34.5kV circuit breaker and all existing relaying (electromechanical) at the station are in need of replacement. The following line sections have identified asset renewal concerns and many have seen loading greater than 90% under contingency conditions. New Liberty - North Baltimore 34.5kV: The 10 mile circuit is a combination of 4/0 ACSR and 336 ACSR (circa 1940) with wood structures (Predominately pre-1980's). The line section has 30 open A conditions. North Findlay - North Baltimore 34.5kV #1: The 8 mile circuit identified is predominately 4/0 ACSR (circa 1961) with small portions of 2/0 Copper, 336 ACSR, 556 ACSR, and 795 ACSR. This line has predominantly wood structures (ranging from 1920's - 2000's) with14 open A conditions. New Liberty - Findlay Center 34.5kV: This 3.3 mile line has a combination of 4/0 Copper, 336 ACSR, and 556 ACSR (circa 1934-1964) with wood structures and 10 open A conditions. Whirlpool Extension 34.5kV: This 0.15 miles of rebuild identified is 336 ACSR (circa 1967) with wood structures (circa 1967). Operational Flexibility and Efficiency There is an existing 34.5kV three terminal line at Morrical Switch and hard taps at in the area that increase outages to customers in the area (Totten and Centrex).
AEP-2018-OH008 | AEP | PJM West | 2018-10-26 |  |  |  |  | Dunkirk - Arlington 34.5 kV line condition | The Dunkirk - Arlington 34.5 kV line has a combination of #2 ACSR (vintage 1980) and 1/0 CU (vintage 1920's) and is built to distribution standards. The Forest - South Berwick 69 kV line has a combination of 1/0 ACSR, # 1 CU (vintage 1920's), 4/0 ACSR (vintage 1920's - 1960), and 556 ACSR (vintage 1971 - 2003). There are 10 open A conditions on the Arlington - Dunkirk 34.5 kV line (~ 7.29 miles) & 29 open A conditions on the Forest - South Berwick 69 kV line (~29.3 miles). There is a three-terminal hard just west of Hurd Switch. South Carey Switch and North Wharton Switch are both three-terminal lines. West Crawford Switch and Hurd Switch are set in an N.O. position to prevent thermal overloads. The City of Carey has reliability concerns, where both feeds to the city can be lost for a single outage. Hancock-Wood Co-op has reliability and maintenance concerns due to radial loads at Arlington and Blanchard Stations. Arlington - Dunkirk Circuit: Peak Load Impact: 6.57 MW CMI (2015 - 2018): 162,840 Forest - South Berwick Circuit: Peak Load Impact: 7.68 MW CMI (2015 - 2018): 1,713
AEP-2018-OH009 | AEP | PJM West | 2018-10-26 | 2019-02-20 | 2019-08-29 | s1858 |  | Harmar Hill 138 kVstation | RJF is a customer owned substation that is served off a 138kV hard tap. Harmar Hill is served from a tap with a one way switch that is currently inoperable. Any line work along between Mill Creek and Gorsuch causes considerable outages to both customer loads. There is limited transfer capability at Harmar Hill and no transfer capability for RJF. AEP's internal guidelines justify sectionalizing on this line (FOI: 10.17). Mill Creek will be replaced by a new substation Devola as part of an unrelated project (S1125).
AEP-2018-OH010 | AEP | PJM West | 2018-10-26 | 2018-11-29 | 2019-04-12 | s1792 |  | Load request on the Crooksville – North Newark 138 kV circuit | *Customer Service #1: AEP Ohio has requested a connection to the Crooksville – North Newark 138 kV circuit. Isabella station will replace their Redfield station. Redfield Distribution equipment is in need of rehab and it is distant from Distribution load centers. The starting load at Isabella will be 3.5 MVA and the ultimate load will be 10 MVA. Load will be transferred load from Redfield and South Fultonham. The existing Redfield 69kV Station has experienced 1,730,000 CMI over a three year period.
AEP-2018-OH011 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1859 |  | Gable-Carrollton 138 kV circuit condition | The 29-mile Gable-Carrollton 138kV circuit (vintage 1917) is in poor condition and is a reliability risk to the transmission system. The circuit consists of lattice towers and 6-wired 200 kcmil copper conductor. After a century in the field, the lattice towers have degraded significantly, with heavy rusting and broken tower legs. The copper conductor has become very brittle and is difficult for crews to repair. Some towers are sitting in water. The suspension insulators and hardware are also heavily worn. The circuit has 39 open conditions, with the majority being structural issues (e.g., degraded tower parts & broken insulators). The circuit has experienced 5 outages in the last 3 years (2016-2018 YTD), including a 50-hour outage due to broken conductor. This circuit spans the center of the Ohio Utica shale gas region in Carroll/ Harrison Counties, with major activity from existing industrial customers and frequent economic development inquiries for future loads (e.g., pipeline compressor stations & midstream processing plants).
AEP-2018-OH012 | AEP | PJM West | 2018-10-26 |  |  |  |  | 69 kV breakers at Lick station | At Lick substation there are six 69 kV circuit breakers with condition issues. CB's 61,62, 65, 66, 67, and 69 are oil type breakers that were manufactured between 1956 - 1967. There is a potential for oil spills during routine maintenance and fault operations. In addition, spare parts are difficult to obtain. The breakers' fault operation counts are as follows: {61-126, 62-11, 65-26, 66-8, 67-19 and 69-4}. For most of these breakers, the number of fault operations exceed the manufacturers recommended number of 10. There are three 138/69 kV, 18 MVA transformers at Lick. T#1 is a Westinghouse transformer manufactured in 1956. Transformers #2 and #3 are both GE transformers manufactured in 1950. All three transformers have maintenance issues with their LTCs and have significant oil leaks. In addition, loss of two of the transformers can load the remaining transformers tertiary winding above it's rating.
AEP-2018-OH013 | AEP | PJM West | 2018-10-26 | 2019-06-17 |  |  |  | 138 kV breaker at Mound Street | The 138kV CB-101 at Mound Street is the last remaining oil breaker at the station. This oil breaker doesn't have oil containment. Oil breaker maintenance has become more difficult due to the oil handling required to maintain them. Oil spills can occur with breaker failures and routine maintenance which has the potential for an environmental risk. This breaker is a model that has identified reliability concerns due to past failures and lack of spare part availability. This CB separates two transformers that serve critical hospital loads. A failure could cause a sustained outage to the entire facility.
AEP-2018-OH014 | AEP | PJM West | 2018-10-26 | 2019-01-11 | 2019-08-29 | s1860 |  | Reno substation 138 kV hardtap | Reno Substation is served off a 138kV hard tap. If there is an outage, planned or unplanned on the line sections between Belmont and Levee, the Reno load will be dropped. There is partial transfer capability for Reno during light load periods only. Levee Station cannot take all Renos load because the distribution circuits are over five miles between the two stations dictated by geography. The nearby Wade station is being retired as part of an area project to address an unreliable 23 kV system. Levee Station will will take a portion of Wade"s load and the remaining load will be served from Reno Station. "
AEP-2018-OH015 | AEP | PJM West | 2018-10-26 | [5 empty] | Rarden and Rosemount Stations are connected by a 34.5 kV line with four 34.5/12 kV substations and several distribution customers served directly from the line. The total load served along this 24 mile line is 26/30 MVA (summer/winter). There is a normal-open point near Otway. The area suffers from reliability issues due to the rugged terrain and remote access. Customers have experienced over four million customer minutes of interruption over the past three years. The area's peak load can exceed the source transformers (Rarden and Rosemount). The 336 AAC conductor has already been overloaded (115% on 2014). The two 69-34.5 kV transformers at Rarden are protected with high-speed ground switches which can cause through-faults on the transmission system.
AEP-2018-OH016 | AEP | PJM West | 2018-10-26 |  |  |  |  | Strasburg, Ohio | The Beartown- West Wilmont 69kV section 10.5 miles long and serves 1 AEP Ohio distribution station and 2 1 Holmes-Wayne Co-op station in northeast Ohio. Over the past several years, the circuit has experienced below-average reliability. For the 2017-2018 YTD period, it has experienced 7 sustained outages, an additional 8 momentary interruptions, and 2 emergency repair incidents on the entire circuit. The majority of the outages were due to T-Line structural issues and forestry. The line section consists of primarily 336 ACSR (1962-64 vintage); it is entirely wood pole construction, with the majority being installed in the 1960’s. The section has a reported CMI of 2.0M between 2014 – 2018 and currently has 52 open conditions (25 Category A, 25 Category B, 5 Forestry). Examples of the conditions include: rotted poles, missing ground-leads, and damaged conductor. During the 2010-2018 period, 112 prior conditions were repaired/addressed on the circuit as a whole.
AEP-2018-OH017 | AEP | PJM West | 2018-10-26 | [5 empty] | Continental - Roselms 69 kV is a 18 mi radial circuit serving ~10.6 MVA load. The customers served from this radial line have experienced 2.1 million customer minutes of interruptions over last 5 years. These radial loads are not automatically transferable. Any maintenance on this line results in outages to multiple stations. ajority of the line has 4/0 ACSR conductor with a 2 mi section with 795 ACSR. This circuit has 89 open conditions. Most of the 258 structures on this circuit are 1960s and 1970s wood pole vintage with rotting issues.
AEP-2018-OH018 | AEP | PJM West | 2018-11-29 | [5 empty] | * A study of the current physical loading capability of the structures along the Astor-Shannon-Groves & Shannon - Bixby 138 kV circuits revealed that many of the poles are currently overloaded under NESC Heavy Loading Conditions. Additionally, the line structures are unable to handle the addition of telecom fiber, which is needed to improve communications in this area. Existing NESC Heavy Loading Conditions: * 36% of poles on the Astor-Bixby 138 kV circuit show overloading. * 29% of poles on the Bixby - Shannon 138 kV circuit show overloading. * 20% of the poles on the Shannon - Refugee 138 kV circuit show overloading. * 58% of poles on the Refugee - (Future) Brice 138 kV circuit show overloading. * 35% of poles on the (Future) Brice - Astor 138kV circuit show overloading. * Primarily 1952 wood poles (57% of total line) * Conductor is all from 1952 * 43 (out of 155) structures on the circuit have at least 1 open condition (28%), with a total count of 63 open conditions. 23 reported closed conditions - 1 forestry, 4 conductor, 18 structure * No outage history (0 CMI/CI) * The Astor-Groves-Shannon 138 kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping. * Astor 138 kV Station has ground switch MOAB’s on both 138/13 kV transformers. Ground switch MOABs cause intentional high side faults, which can damage nearby equipment.
AEP-2018-OH019 | AEP | PJM West | 2018-11-29 | 2019-03-25 | 2019-08-29 | s1861 |  |  | A transmission customer has requested new 69kV service on the northeast side of Wooster, Ohio. The total peak demand is 11 MVA.
AEP-2018-OH020 | AEP | PJM West | 2019-01-11 | [5 empty] | Hilliard Station 69kV: CB 61, CB 62, and CB 63 are 1960's vintage 69kV oil-filled breakers. Oil type breakers are difficult to maintain due to oil handling requirements, and have had a number of fault operations: CB 61 (15), CB 62 (21) and CB 63 (31). 105 of the 119 relays are electromechanical relays. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. The RTU is obsolete and does not meet current standards. The structure steel is deteriorating due to rust and the foundation supporting the steel shows severe cracking. Trabue Station 138/69kV: The 1960"s vintage, 138/69 kV, 115MVA Transformer #3 is recording elevated gas levels due to through fault conditions. 60 of the 86 relays are electromechanical relays. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. Galloway Station 69kV: 104 of the 122 relays are of the electromechanical type. EM relays have limited spare part availability, no vendor support, no SCADA functionality, and no fault data collection ability. The RTU is obsolete and does not meet AEP standards. The structure steel is deteriorating due to rust and the foundation supporting the steel shows severe cracking. Beatty-Galloway 69kV: The total circuit (~ 8 mi) currently has 51 open A conditions (structure, conductor, shielding grounding, hardware, and other) with a number of deteriorated overhead structures. Beatty Station 138/69kV: Three 1960"s vintage 69 kV oil breakers, CB 63, CB 64, and CB 65, show signs of bushing damage, lack of available repair parts, and high PCB content. Oil type breakers are difficult to maintain due to oil handling requirements, and have had a number of fault operations: CB 64 has seen 34 fault operations. 1960"s vintage, 138/69 kV 50 MVA transformers #2 & #4 are showing signs of short circuit strength breakdown due to the amount of through fault events, dielectric strength breakdown, and bushing damage (bushings). Transformer #2 also has a high levels of dissolved gas in the oil.
AEP-2018-OH021 | AEP | PJM West | 2018-11-29 | 2019-01-11 | 2019-08-29 | s1862 |  |  | Baltimore 69kV CBs E and F are oil type breakers (vintage 1951) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB E (5), CB F (5). Baltimore currently has 20 electro-mechanical relays employed. EM relays have limited spare part availability, a lack of vendor support, no SCADA functionality, and no fault data collection ability. Lancaster 69kV CBs B and D are oil type breakers (vintage 1989) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB B (4), CB D (18). Lancaster currently has 46 electro-mechanical relays employed. EM relays have limited vendor support, lack of SCADA functionality, and dont offer fault data collection "
AEP-2018-OH022 | AEP | PJM West | 2018-11-29 | 2019-02-20 | 2019-08-29 | s1863 |  |  | * Cyclops 69kV circuit switcher A is currently being used as a line CB. This model has limited spare parts availability and reliability concerns. This circuit switcher has also experienced 41 fault operations. * Cyclops 69kV CB B is an oil type breaker (vintage 1955) that has exceeded the manufacturers recommended number of fault operations (36 total faults). Oil breakers are difficult to maintain due to oil handling requirements. Oil spill can occur during maintenance and fixes. * Cyclops station currently has 19 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. * Cyclops station is currently built upon a four-pole wooden bay that is progressively deteriorating.
AEP-2018-OH023 | AEP | PJM West | 2018-11-29 | 2019-02-20 | 2019-08-29 | s1864 |  |  | * East Cambridge 34.5kV CB “D”, 69kV CB “A” and 69kV CB “C” are vintage (1970- 1975) circuit breakers. Oil breakers are difficult to maintain due to oil handling requirements and risk of oil spills during maintenance and failures. In addition, these CB’s have exceeded the manufacturers recommended fault operations: CB A (8), CB C (28), and CB D (91). * East Cambridge circuit switcher AA (vintage 1970) is recommended for replacement due to reliability concerns and lack of spare part availability. * East Cambridge currently has 36 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability.
AEP-2018-OH024 | AEP | PJM West | 2018-11-29 | [5 empty] | The 138kV riser is currently the Most Limiting Series Element on the 765/138 kV transformer at Maliszewski, reducing the summer normal rating by 170MVA. With customer load requests in the area, we anticipate this limitation overloading in the future. A transformer outage is already scheduled so utilizing already mobilized crews to save on costs in the long run would be desirable.
AEP-2018-OH025 | AEP | PJM West | 2018-11-29 | 2019-01-11 | 2019-08-29 | s1865 |  |  | Hocking 138kV MOAB “W” is in a failed state. When operating, arcing occurs, resulting in the tripping of remote breakers/circuit switchers. The structures supporting this MOAB will not allow for a like for like replacement due to the extra weight.
AEP-2018-OH026 | AEP | PJM West | 2018-11-29 | 2019-03-25 | 2019-08-29 | s1866 |  |  | * The New Lexington - East Logan 22.3 mile 69 kV (vintage 1916) was built using wood pole structures with conductors ranging from #1 Copper 3 conductor (31 MVA rating) to 336.4 KCM ACSR 18/1 (73 MVA rating). * There are 139 open A conditions on this line, including burnt/broken conductors, and broken structures. The New Lexington - East Logan 69 kV circuit has experienced over three million customer minutes of interruption in the past three years.
AEP-2018-OH027 | AEP | PJM West | 2018-11-29 | [5 empty] | Equipment Material / Condition / Performance / Risk: * Elliott 138 kV circuit breaker 102 (vintage 1956) is an oil type breaker recommended for replacement due to bushing damage, reliability, and lack of spare part availability. * Elliot 69kV circuit breakers 61, 66, and 67 (vintage 1972) have experienced the following numbers of fault operations: CB-102 (38), CB-67 (10), CB-66 (40), and CB-61 (1). These breakers are oil type breakers recommended for replacement due to reliability and lack of spare part availability. * Strouds Run 69kV circuit breakers 63 and 66 (vintage 1969-1973) are oil breakers recommended to replace due to reliability and lack of spare part availability. Maintenance has become more difficult due to the oil handling required to maintain them. They have experienced the following fault operations: CB 63 (24), CB 66 (0). * Strouds Run 138kV Circuit switchers “CS-TR1” and “CS-TR2” are Mark type switchers. Mark switchers are being recommended for replacement system wide due to their inability to coordinate with modern relaying packages. Circuit switchers have experienced the following fault operations: CS-TR1 (17), CS-TR2 (18). * Strouds Run 138/69 kV 33.6MVA transformer #1 (vintage 1972) is also showing significant signs of deterioration. Drivers for replacement include dielectric strength breakdown, short circuit strength breakdown, and bushing damage. * Clark Street 69 kV circuit breakers 61 and 64 (vintage 1968) are oil filled breakers that have been recommended for replacement due to oil handling requirements, no longer has vendor support, lacks sufficient spare part availability, and has a history of malfunctions. The breakers have had the following fault operations: CB 61 (8) and CB 64 (15). Equipment Material / Condition / Performance / Risk: * The Elliot - Lee 69kV 8 mile, 69 kV line (vintage 1974) was constructed using wood pole structures with 336.4 KCM ACSR 18/1 conductor (73 MVA rating). * There are 106 open A conditions on this line, including rotten structures, burnt/broken insulators, and loose/broken/sagging conductor sections, improperly installed shield wires and woodpecker damaged structures. * These stations still have the following amount of electromechanical relays employed: Elliot (29), Strouds Run (78), Clark Street (25). EM relays have limited vendor support, lack SCADA functionality, and don’t offer fault data collection. Operational Flexibility and Efficiency: * The Crooksville - Poston - Strouds Run 138kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping. * The Dexter - Elliot - Poston 138kV circuit is a three-terminal line, which limits sectionalizing and can cause mis-operations and over tripping.
AEP-2018-OH028 | AEP | PJM West | 2019-01-11 | 2019-06-17 |  |  |  | Bixby 345/138 kV station | The 345/138kV, 675MVA transformer #1 failed and caught fire at Bixby station. The MOAB switch, and risers cannot be repaired. A replacement is needed to support the load in the area.
AEP-2018-OH029 | AEP | PJM West | 2019-01-11 | [5 empty] | The Fisher-Hall-Wilson 138kV circuit is a three terminal line. Three-terminal lines cannot be protected adequately and lead to mis-operations including over tripping. At Wilson Road station, 138kV CB’s 2, 3, 4, 5, 6, 7, 8, & 9 (vintage1960-1970), 46 kV cap switcher AA (vintage 1995), and 40kV CB’s 30 & 35 (vintage 1956) are all oil type interrupting devices. Oil type equipment is difficult to maintain due to the oil handling requirements and due to environmental risk associated with spills that are common. In addition, some of these devices have exceeded the manufactures recommended number of fault operations 40kV CB 35 (55) and 138kV CB 4 (17). 40kV is considered to be an obsolete voltage technology because of lack of replacement/repair parts and lack of vendor support. McComb station is served from two 138kV sources, one of which relies on an underground oil filled pipe type cable. This is a reliability concern because any significant outage will likely require several months to repair, leaving the station radialized. We have experienced several prolonged outages of oil filled cables. These cables are only manufactured by a single manufacturer with a lead time of 8-12 months. Two 50MVA transformers at McComb are protected by ground switch MOABs which can cause damage nearby equipment when they operate. The 1.7 mile Briggsdale-McComb 40kV line (vintage 1973) has 8 open conditions including hardware, shielding/grounding, and forestry. The 5.19 mile Briggsdale-Wilson 40kV line (vintage 1935 – 2011) has 87 open conditions including structures, conductor, shielding/grounding, hardware, and forestry.
AEP-2018-OH030 | AEP | PJM West | 2019-01-11 | [5 empty] | The 27-mile 69kV Portsmouth-Ironton line (vintage 1915) uses wood pole structures with variety of conductors, mostly 2/0 Cu (40 MVA rating). A 11.9 mile section between Millbrook Park and Franklin Furnace has 73 open A conditions, including rotten cross-arms, burnt/broken insulators, and loose/broken conductor hardware. The Millbrook Park-Franklin Furnace-Argentum line is a 3-terminal line. Three-terminal lines cannot be adequately protected due to the complexity of coordination, which, causes misoperations including over-tripping. The Millbrook Park-North Haverhill-Argentum circuit is protected by an impedance based Directional Comparison Blocking (DCB) pilot system, which cannot adequately protect a three terminal lines. Over the past several years, the Millbrook Park-Argentum-North Haverhill circuit has experienced reliability issues including 5 sustained outages and 21 momentary outages. The Texas Eastern Substation serves a peak load of 26 MW via a 2.1-mile radial line from East Wheelersburg. Also, K.O. Wheelersburg is a 1.2 MVA 69 kV retail load served off a 1.3-mile radial line. These radial loads are at risk of extended outages for line maintenance or repair. At Sciotoville, CBs A and B are both oil type breakers with 16 and 10 fault operations respectively. This particular model has no spare parts and a history of poor reliability. Sciotoville has a ground switch MOAB on the transformer. Ground switch MOAB’s cause intentional high side faults to clear the transformer faults which cause damage to and reduction in life of nearby equipment. Sciotoville and Wheelersburg currently have 8 (of 10) and 10 (of 10) electro-mechanical relays respectively. EM relays have no spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability.
AEP-2018-OH031 | AEP | PJM West | 2019-01-11 | 2019-02-20 | 2019-08-29 | s1867 |  |  | The existing 18.4 mile 69 kV section between Thornville –Lancaster 69 kV line was constructed in 1915 using wood pole structures with copper conductors (mostly 1/0 Cu). There are currently 228 open A conditions along this line. The Baltimore-East Lancaster 69 kV circuit section has experienced over 350,000 customer minutes of interruption over the past three years. The majority of outages were due to conductor failures, shielding failures, structure washouts, and insulators failures.
AEP-2018-OH032 | AEP | PJM West | 2019-01-11 | [5 empty] | A customer has requested new service west of Cameron, West Virginia. The forecasted peak demand is 30 MVA.
AEP-2018-OH033 | AEP | PJM West | 2019-01-11 |  |  |  |  | Bluffton Area Improvement Project | Equipment Material/Condition/Performance/Risk: North Woodcock 138/69/34.5 kV Station: * 138/69/34.5 kV, 50 MVA Transformer #1 (1966 vintage) is recommended for replacement due to dielectric strength breakdown, short circuit strength breakdown and bushing damage. * 1200 A/21 kA, 69 kV CB A" (1966 vintage) and 1200A/17 kA,34.5 kV CB "E" (1952 vintage), are in need of replacement due to bushing damage, excess numbers of fault operations (143), and lack of spare part availability. * 34.5 kV grounding bank is recommended for replacement due to dielectric strength breakdown, numerous thermal faults and carbonization of insulating paper. Bluffton - Rockhill 34.5 kV: * The circuit has 55 open conditions. Most of the 381 wood poles on this circuit are pre 1980 vintage. This line has experienced 9 momentary and 4 permanent outages in the last 10 years. Morrical - N. Woodcock 34.5 kV: * The circuit has 77 open conditions. Half of the 400 wood poles on this circuit are pre 1980 vintage. This line has experienced 16 momentary and 3 permanent outages in the last 10 years. Operational Flexibility and Efficiency: Bluffton 34.5 kV: * The switch towards Woodcock is normally open (N.O.) to prevent thermal overloads under N-1-1 conditions. * Hard taps currently exist for customers at both DTR and National Lime and Stone. Hard taps limit sectionalizing can cause mis-operations and over tripping "
AEP-2019-AP001 | AEP | PJM West | 2019-02-20 | [5 empty] | Bim 69 kV * Breaker “D” * 1967 FK oil type breaker without containment * Fault operations: 369, recommended 10 operations * Cap Switchers “AA” and “BB” * SC-2030 type * No gas monitoring * Sister units have experienced numerous gas and interrupter failures Bim 46 kV * Breakers “A”, “B”, “C”, and “E” * 1967 FK oil type breakers without containment * Fault operations: CB A (85), CB B (14), CB C (131), CB E (63), recommended 10 operations Bim Station * Existing Gr. SW. MOAB configuration creates faults in the station; known safety hazard in legacy station designs * Transformer Bank #1 138/69/46 * Oil leaking at a steady rate * Deteriorating wooden crossties, obsolete arresters and bushings, LTC is not in adequate condition * Cooling system and controls need replaced * GND Bank * Interfacial tension in all three units has been on the decline or at sustained low levels for around 15 years, indicating the development of sludge which can impede oil circulation/cooling * Rising/Sustained high moisture content has resulted in degrading/sustained low levels of dielectric strength * Obsolote arresters/bushings, deteriorating wooden crossties * Cooling system/controls need replaced
AEP-2019-AP002 | AEP | PJM West | 2019-02-20 | [5 empty] | Mullens Station * Transformer Bank #4 138/46 kV * Short circuit strength breakdown caused by the amount of high energy electrical through fault events * Numerous gases are at the IEEE level 2 condition level with acetylene and ethylene being at the highest condition level 4, which negatively impacts the oil dielectric * Major carbonization of the insulating paper as occurred from these numerous through fault events, indicating that this unit is near the end of its useful life * There is a bad fan on transformer #4, on the bottom of cooling group 2 * Grounding Bank #3 * Upward trending of oil moisture content resulting in downward trending to the oil dielectric strength * Increasing moisture content is a resultant of water ingress and/or break down of paper insulation of TF windings * Short circuit strength breakdown caused by the amount of thermal through fault events * Existing Gr. SW. MOAB configuration on the 138/46 kV and 138/34.5 kV transformers create faults in the station; known safety hazard in legacy station designs * 63 of the 74 relays in the station (85% of all station relays) are of the electromechanical type which have significant limitations with regards to fault data collection and retention * 13.2kV CBs R & S at are oil filled breakers without oil containment
AEP-2019-AP003 | AEP | PJM West | 2019-02-20 |  |  |  |  | Lynchburg, VA | * The 1959 vintage 138/69/34.5 kV transformer #1 at South Lynchburg Substation has elevated levels of carbon dioxide which began increasing in 2004. Additionally, the interfacial tension is steadily decreasing and the oil power factor is steadily increasing indicating that the oil insulation is beginning to degrade as well. This data proves that the transformers insulation is aged and has degraded. * The 34.5 kV Grounding Bank was manufactured in 1954 and has high concentrations of combustible gases, specifically CO and CH4, due to various thermal faults and electrical discharges. Short circuit breakdown caused by the amount of through fault events, some greater than 700 degrees Celcius has contributed to the deterioration of the bank. * 12 kV CBs P, L, K, N, M, and R are oil breakers * Number of fault operations: P (44), L (42), K (152), N (132), M (34), R (135) * 34.5 kV CB F has 31 fault operations * 34.5 kV CB G has 63 fault operations
AEP-2019-AP004 | AEP | PJM West | 2019-02-20 | 2019-05-20 |  |  |  |  | The Amherst-Clifford 69 kV circuit (13.9 mi.) consists primarily of 1960 wood pole structures with 4/0 ACSR overhead conductor and currently has 26 open conditions including rot top, woodpecker damage, split poles, broken insulators and damaged shield wire. Over the 2015-2018 time frame there were 5 momentary outages which occurred during lightning and wind events due to the lack of shield wire on half of the circuit, exposing it to a higher probability of forced momentary and permanent lightning induced outages. The Clifford-Scottsville 46 kV circuit (45.5 mi.) consists primarily of 1926 wood pole structures with 4/0 ACSR overhead conductor and currently has 93 open conditions including rot top, rot heart and woodpecker/insect damage. Over the last recorded 3 year period, 6 permanent outages were observed. Also, only 16% of the line has shielding, mainly on the tap sections. Riverville station serves a large industrial customer (Grief Brothers Corporation) consisting of approximately 45 MW from a radial 138 kV line served from Boxwood S.S. located between Clifford and Reusens. This radial line is approximately 9.2 miles long, leaving a large amount of load exposed to a variety of single contingency events.
AEP-2019-AP005 | AEP | PJM West | 2019-02-20 | [5 empty] | The 138/12 kV Transformer #3 at Fremont station is 1971 vintage and is showing dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). 138/69 kV Transformers #1 and #2 at Fremont station are 1957 vintage and show significant signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults).
AEP-2019-AP006 | AEP | PJM West | 2019-03-25 |  |  |  |  | Montgomery County, VA | Craig-Botetourt Electric Cooperative (CBEC) requested a new delivery point from AEP to be located in Montgomery County, Virginia. The new station will serve approximately 10 MVA.
AEP-2019-AP007 | AEP | PJM West | 2019-03-25 | [5 empty] | Fleming Station * 138/69 kV Transformer #1 * 1984 vintage transformer. * Shows signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). * Reports from the field show active oil leaks from the gaskets and slight leaks from the unit’s welds. * Utilizes a ground switch MOAB scheme as part of the high side transformer protection. * 69/12 kV Transformer #3 * 1979 vintage transformer. * Shows signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). * 69 kV Circuit Breakers B, E, and F * CF-48 type oil breakers. (1965, 1968, and 1967 vintage) * These are oil breakers are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturers recommendations. * Have experienced 114, 26, and 68 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. * This circuit breaker model family has experienced numerous documented mechanism bearing issues and failures within the AEP population. CBs B & F have had malfunction records indicating a failure to properly latch during operation. Fleming Station * S&C Circuit Switcher ‘AA’ * No gas monitor, sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures. * 12 kV Circuit Breakers C and D * ES type oil breakers. (1979 vintage) * These are oil breakers that have become more difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * These are oil breakers that have become more difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. * Have experienced 36 and 19 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. * 69 kV Circuit Breaker A * 72EPB-31.5-20 SF6 type breaker with known gas leaks. (1990 vintage) * 18 malfunction records for this breaker since 2009 related to low gas alerts. * 1 of 12 remaining breakers of this type on the AEP system.
AEP-2019-AP008 | AEP | PJM West | 2019-03-25 | [5 empty] | Racine 69 kV circuit breaker B * CG-48 oil type breakers that was manufactured in 1980. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * Experienced 43 fault operations, exceeding the manufacturer's designed number of fault operations of 10.
AEP-2019-AP009 | AEP | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | The 14.2 mile long Amherst-Reusens 69 kV circuit was originally constructed in 1946 using wood pole structures with the lack of shielding on most (98%) of the circuit. Within the last 3 years it has experienced 33 momentary outages and 3 permanent outages with an average outage duration of 78.4 hours. The circuit currently has 26 open conditions. The majority (84.1%) of overhead conductor consists of 4/0 ACSR, also from 1946.
AEP-2019-AP010 | AEP | PJM West | 2019-04-23 |  |  |  |  | South Charleston, West | * South Charleston 46 kV CBs A and B are 460G-3000 oil filled breakers. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * These are the last 2 circuit breakers in the 460G-3000 CB model family on the AEP system, making spare parts difficult or impossible to obtain. * Chemical – South Charleston 46 kV #1 (~0.5mi) currently has 9 open conditions on 8/8 structures. * The majority of the circuit is constructed with 1950s wood structures and lattice structures. * The conditions include rot shell, insect damage and heavy rust.Chemical – South Charleston 46 kV #2 (~0.5mi) currently has 16 open conditions on 9/9 structures. * The majority of the circuit is constructed with 1950s lattice and wood structures. * The conditions include rot and heavy rust and rot shell.
AEP-2019-AP011 | AEP | PJM West | 2019-04-23 |  |  |  |  | Winfield, West Virginia | 69 kV circuit breakers F and G at Bancroft station are CF-48 oil type breakers that were manufactured in 1965. * Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which can be an environmental and safety hazard. * Breakers F and G have experienced 55 and 70 fault operations, exceeding the manufacturer's designed number of fault operations of 10.
AEP-2019-AP012 | AEP | PJM West | 2019-06-17 |  |  |  |  | Danville, VA Area | Danville, VA Area Pilot Wire Several documented mis-operations have occurred related to defective and disabled pilot wire relaying between Danville, East Danville and the local 69 kV network. Pilot wire maintenance is a known safety concern especially during poor weather conditions. Elimination of pilot wire in the Danville area will address ground splice concerns, pilot wire cabinet access issues and low hanging pilot wire on poles. Corrective maintenance continues to be a concern due to the lack of spare relay components and it being an obsolete technology. Due to the abnormal conditions and overall age of the pilot wire in the Danville area, mis-operations have impacted several large industrial customers. East Danville Station 138 kV Circuit Breakers L and M 12 malfunction records indicating low SF6 gas during cold weather conditions with continued maintenance required Have experienced 19 and 49 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. 138 kV Circuit Breaker P CB P is FK type oil breaker (1955 vintage) Oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. 69 kV Circuit Breakers F and H FK type oil breakers (1965 vintage) Malfunction on CB H for an air leak on the control valve Have experienced 46 and 78 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. 69/12 kV T#3 High side MOAB Ground Switch Tapped off of East Danville-US Gypsum 69 kV line, not currently tapped off bus Goodyear Station 69 kV Circuit Breakers A, C and D FK type oil breakers (1959, 1973 and 1972 vintage respectively) Oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Have experienced 18, 9 and 7 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. Customer metering CTs and PTs are over 50 years old and accuracy class below recommended US Gypsum Station Customer metering CTs and PTs are over 50 years old and accuracy class below recommended 69 kV Circuit Breaker A FK type oil breaker (1966 vintage); experienced 21 fault operations Rigis Station 138/69 kV T#1 High side MOAB ground switch protection Corning Glass Station 69 kV Circuit Breaker B FK type oil breaker (1966 vintage); experienced 80 fault operations Circuit Switchers A and AA S&C 2030-69, no gas monitor, model family has numerous documented malfunction records concerning gas loss and interrupter failures Danville Station 69 kV Circuit Breaker J FK type oil breaker (1966 vintage)
AEP-2019-AP013 | AEP | PJM West | 2019-06-17 | [5 empty] | Bancroft – Nitro 69 kV (~7.6 miles) Majority of the circuit is constructed with 1930s (46/97, 47%) and 1960s (20/97, 21%) wood structures The circuit currently has 27 open conditions Structure loading does not meet current NESC standards. The conductor is greater than 65 years old, and exceeds the recommended lifespan. Grounding on this line does not meet current standards. Between 2015-2018 the circuit experienced 2 momentary and 1 permanent outage resulting in approximately 800k customer minutes of interruption Nitro – Turner 69 kV (~7.3 miles) Over half of the circuit is constructed with 1920s wood structures (51/75 structures, 68%) The circuit currently has 60 open conditions Approximately half of the line is not shielded. From 2015-2018 the circuit has experienced 8 momentary and 6 permanent outages resulting in approximately 130k customer minutes of interruption
AEP-2019-AP014 | AEP | PJM West | 2019-05-20 | [5 empty] | *Turner 46kV CB-O *One of only six remaining of the 72EPB-20-12 model on the AEP system. *These model types have historically exhibited bad gas leaks, bushing failures, and CT cores getting wet. *Since 2015, there have been 25 documented malfunction records on this unit in regards to low SF6 gas levels. *Turner 138/69 kV Bank #5 *Recently de-rated due to the loss of a cooling pump that cannot be replaced. *This unit could experience an increasing number of overheating events with the potential to cause damage to internal components *Moisture content has been rising for a number of years but more severely over the past 11. * The rise in moisture content correlates to a significant drop in dielectric strength and rising power factor level for the oil. *All three high side bushings are of the Type U design that have extensive manufacturer alerts related to catastrophic failures. *Turner GND Bank #7 *Ethane concentrations in this unit increased drastically in 2018, CO2 levels have increased in 2018 as well. The relative gas concentrations are indicative of numerous overheating events. *Decreasing interfacial tension since 2002, this transformer has likely developed sludge in the oil from deteriorating internal components. The presence of this sludge is likely what is impairing proper oil circulation and contributing to the number of overheating events. *Increase in moisture levels, correlating with an increased power factor and also indicative of oil degradation. *The current station configuration has each bank located on a 138kV Bus with only a MOAB on the high side. A transformer fault on any of the transformer banks will cause a momentary outage of one of the 138kV Buses. *Turner Station Control House *Has asbestos and lead paint and existing water leaks. *Steps leading up to control house are hazardous to anyone entering station. *Currently, 61 of the 95 relays (64% of all station relays) are in need of replacement at Turner Station *There are 55 of the electromechanical which have significant limitations with regards to fault data collection and retention. *There are 5 ABB DPU microprocessor type relays. *ABB DPU relays pose a safety risk to persons performing breaker operation because the DPUs are mounted directly on the circuit breaker without a delay for opening and closing the breaker. *An additional microprocessor is an RFL that utilizes obsolete firmware and is no longer vendor supported.
AEP-2019-AP015 | AEP | PJM West | 2019-05-20 | [5 empty] | *A customer station is currently served off a hard tap on the Belle – Cabin Creek – Marmet Hydro 46 kV circuit.*Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch.*Hard taps can also result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP016 | AEP | PJM West | 2019-06-17 |  |  |  |  | Trap Hill Area Project | Trap Hill Station serves approximately 20 MVA of load from a 6 mile radial thus exceeding AEP’s threshold for looped service of 75 MVA-mile. Long radial line or radial lines serving a significant amount of load are concerning as they age due to: Maintenance of radial facilities being difficult due to the required customer outages. Radial delivery points resulting in extended outages to customers for any loss of the feed due to the lack of looped service and transferability of the load. Bolt Tap 138 kV is a hard tap off the Baileysville – Sundial 138 kV #1 circuit. Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. It can also result in extended outages to customers due to the inability to sectionalize faulted facilities. Dameron 46 kV CB-A Oil filled ITE 69KA-2500-12D type breaker, 1 of 13 of this type of model left on the AEP system. These types of breakers experience issues with their parts and maintenance costs due to lack of vendor support. Oil breakers are more difficult to maintain as oil spills have the potential to occur during maintenance which could pose an environmental and safety hazard. Dameron 46 kV Cap switcher AA S&C 2030-69 unit that has no gas monitor and sister units on the AEP system have experienced 62 malfunctions since 1999. Major events include gas loss, interrupter failures, and operating mechanism failures. Dameron 138/46 kV Bank #1 Rising moisture, carbon monoxide (CO), and carbon dioxide (CO2) levels which indicate a deterioration of the insulating paper. Sustained low levels of interfacial tension also ties to insulation degradation and is an indication of sludge formation. Sludge can impede oil circulation and generate numerous instances of overheating, further accelerating the declining health of the unit. The current MOAB/Ground SW configuration on the high side. Dameron grounding transformer 99 year old unit in which all 3 phases are facing similar condition issues. Sustained elevated moisture levels and power factor have led to decreasing dielectric strength. Sustained low levels of interfacial tension is an indication of sludge formation. Sludge can impede oil circulation and generate numerous instances of overheating, further accelerating the declining health of the unit. Dameron Substation currently deploys 41 relays, implemented to ensure the adequate protection and operation of the substation. Currently, 36 of the 41 relays (88% of all station relays) are in need of replacement. There are 33 of the electromechanical type and 1 static type which have significant limitations with regards to fault data collection and retention. In addition, 2 microprocessor relays were commissioned in 1997 and 2005, indicative of obsolete firmware that is no longer vendor supported. Bolt 46 kV cap switcher AA 1 of 15 remaining VBM-69 types left on the AEP system. These types of cap switchers perform poorly in cold weather and replacement parts are known to be expensive when they are available per the TFS obsolete list. Bolt 46 kV grounding transformer All 3 phases are facing similar condition issues as listed. Sustained elevated moisture levels and power factor have led to decreasing dielectric strength. Sustained low levels of interfacial tension is in indication of sludge formation, in which sludge can impede oil circulation and generate numerous instances of overheating, further decreasing the health of the unit. Bolt 138/46 kV XFR Moisture levels and power factor have been on the rise since 2004. These increases correspond to decreasing dielectric strength levels seen over the same period. The most probable causes of moisture in oil for this unit are paper breakdown (aging), moisture ingress through gaskets, and leaks (main tank; pumps; etc.). Interfacial tension has been at a sustained low level since 2008; this is an early indication of the development of sludge from contaminates in the oil. Over time, the sludge can further impede the ability of oil to properly circulate, potentially leading to more frequent unit overheating.
AEP-2019-AP017 | AEP | PJM West | 2019-06-17 | [5 empty] | Beaver Creek – McKinney #1 46 kV Circuit From 2016-2018, the approximately 24.6 mile Beaver Creek – McKinney #1 46 kV circuit has experienced 22 outages. The circuit is comprised of 152 structures, the majority of which are wood structures dating back to 1929 (22/152, 14%) and 1949 (61/152, 40%). There are 142 open conditions along the 24.6 mile long line. These include damaged poles and cross-arms, conductor/shield wires, and guy anchor/knee/vee braces. Hays Branch Station Hays Branch serves a ~30 MW gas compressing operation that is currently radially fed from a ~8.25 mile line out of Morgan Fork station. Saltlick Station Saltlick serves an EKPC co-op that is currently radially fed off the Beaver Creek – McKinney 46 kV circuit. Spring Fork Spring Fork station serves KPCo distribution customers and is currently radially fed off the Beaver Creek – McKinney 46 kV circuit. Consolidation Metering Consolidation Metering station serves a mining operation and is currently radially fed off the Beaver Creek – McKinney 46 kV circuit.
AEP-2019-AP018 | AEP | PJM West | 2019-05-20 | [5 empty] | *Speedway 138 kV Tap *There are 34 open conditions associated with the 1960s wood structures that comprise the 7.3 mile Speedway Tap that serves Speedway station. These conditions include damage due to woodpecker holes, damaged poles, and corroded cross-arms. *Glen Lyn – Hatcher 138 kV Line Section *The Glen Lyn – Hatcher 138 kV line section utilizes double circuit lattice structures and conductor installed during the 1920s. The structures, conductor, hardware, and insulators on the line are displaying issues associated with their age. *Speedway Station *Speedway station is currently radially served off the ~7.3 mile Speedway 138 kV Tap. *Speedway station has 20 MW of nontransferable load (25 MW peak).
AEP-2019-AP019 | AEP | PJM West | 2019-05-20 | [5 empty] | *West Kingsport 34.5 kV *34.5 kV Circuit breakers A, C, and F *FK type oil breakers. (1955, 1955, and 1966 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. *Have experienced 26, 26, and 21 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10.
AEP-2019-AP020 | AEP | PJM West | 2019-05-20 | [5 empty] | *34.5 kV Circuit breakers A, B, and N *FK type oil breakers. (1956, 1956, and 1954 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturer’s recommendations. *Have experienced 40, 34, and 15 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. *S&C Circuit Switcher ‘AA’ *No gas monitor, sister units on the AEP system have a history of gas loss, interrupter failures, and operating mechanism failures.
AEP-2019-AP021 | AEP | PJM West | 2019-05-20 | [5 empty] | *Holston Station *138/34.5 kV Transformer #1 *Manufactured in 1979. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings/windings), and short circuit breakdown (due to through faults). *Currently tied directly to 138 kV bus #1 via a MOAB on high side. *34.5/23-2.4 kV Transformer #8 (GND Bank) *Manufactured in 1954. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). *Capacitor switchers ‘BB’ and ‘CC’ *Capacitor switchers ‘BB’ and ‘CC’ at Holston station are Mark V model which no longer support modern relaying packages. *Mark V’s have been historically prone to mechanism failures and are being replaced system wide where possible. *34.5/23-2.4 kV Transformer #9 (GND Bank) *Manufactured in 1953. *Showing signs of dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). *34.5 kV Circuit breakers E, F, and U *FK type oil breakers. (1959, 1955, and 1950 vintage) *These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. *Other drivers include damage to bushings and the breakers have experienced 2,19, and 7 fault operations respectively. The manufacturer’s recommendation for this type of break
AEP-2019-AP022 | AEP | PJM West | 2019-05-20 | [5 empty] | AEP Kentucky Power Distribution has requested a new distribution service out of the existing Cedar Creek Station located in Pikeville, Kentucky. Winter projected load is 12.5 MVA.
AEP-2019-AP023 | AEP | PJM West | 2019-07-24 |  |  |  |  | Fayette County, WV | Amos – Hopkins 138 kV (~31.37 miles) – Majority of the circuit is constructed with 1920s lattice structures * The lattice towers used for this line are approximately 94 years old. Structure loading does meet the NESC 250B, 250C and 250D standards for all structures that were analyzed. * Steel lattice towers and hardware are currently exhibiting medium to heavy rust – The shield wire and conductor for this line is 94 years old. Current shielding for the majority of the line does not comply with current standards.
AEP-2019-AP024 | AEP | PJM West | 2019-07-24 |  |  |  |  | Wyoming/McDowell Counties, WV | Baileysville – Hales Branch 138 kV (~27.8 miles) * Majority of the circuit is constructed with 1970s wood structures. * Between 2015-2018 the circuit experienced 24 momentary outages. * All momentary outages are attributed to lightening, insufficient shielding and aging towers as the structures, conductor, hardware, and insulators on the line are displaying issues associated with their age * The circuit currently has 54 open conditions * Open conditions include: Rotten Tops, Woodpecker damage, Split Poles, Corroded Crossarms, Rotten Shells, Broken Ground Lead Wires, and Buildings Encroachment in Right Of Way * Structures loading does not meet current NESC standards.
AEP-2019-AP025 | AEP | PJM West | 2019-07-24 |  |  |  |  | Floyd County, Kentucky | * The existing Allen station has historically experienced severe flooding due to the stations current location in the flood plain. Historical flooding issues have lead to significant deterioration of the stations foundations and structures. * The 46 kV Circuit Breakers (CBs) A, B, C, & D are oil filled breakers without oil containment manufactured in 1960s. Oil filled breakers have much more maintenance required due to oil handling that their modern, SF6 counterparts do not require. These units comprise 4 of the remaining 12 of the FZO-69-1500P model family on the AEP System. Spare parts for these units are difficult to impossible to procure, and this model type is no longer vendor supported. * The circuit breakers have experienced the following fault operations, CB A (27), C (20), and D (17). The manufacturer recommendation is 10 fault operations during it’s in-service life. In addition, all CBs have documented malfunction records with A, C, and D having at least 1 documented since 2016. These include mainly air leaks, a broken trip latch component, and a trip test switch malfunction. The platform foundations that these are mounted on are crumbling in several locations. * The 46 kV CS AA is a VBM-69 model type, 1 of 15 remaining on the AEP System. Spare parts for these units are difficult to impossible to procure, and this model type is no longer vendor supported. These circuit switcher models are poor cold weather performers. This unit has 8 documented malfunction records including multiple failures to trip on poles 2 and 3 and one instance in 2011 in which the unit failed to close.
AEP-2019-AP026 | AEP | PJM West | 2019-07-24 |  |  |  |  | Fayette County, WV | Carbondale – Kincaid 46 kV #1 (~14.8 miles) * Majority of the circuit is constructed with 1950s wood and lattice structures * The conductor is greater than 65 years old. Grounding on this line does not meet current standards. * Between 2015-2018 the circuit experienced 16 momentary and 6 permanent outage resulting in approximately 140k customer minutes of interruption Carbondale – Kincaid 46 kV #2 (~18.6 miles) * Majority of the circuit is constructed with 1950s wood and lattice structures * The conductor is greater than 65 years old. Grounding on this line does not meet current standards. * From 2015-2018 the circuit has experienced 16 momentary and 7 permanent outages resulting in approximately 390k customer minutes of interruption. Carbondale 138/69/46 kV Station – 46 kV and 69 kV CBs A, B, C, D, F and G are all 1968, CF-48-69-2500 type breakers. * Spare parts for these units are difficult to impossible to obtain, and this model type is no longer vendor supported * These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling * These breakers have each exceeded the designed number of full fault operations (10). CB-A: 154, CB-B: 49, CB-C: 78, CB-D: 75, CB-F: 94, CB-G: 100 – Carbondale 138/69/46 kV transformer TR-1, manufactured in 1972, has experienced a sharp increase in combustible gas concentrations in January 2016. * Numerous gasses have remained at elevated levels, including acetylene at IEEE Condition 4 and ethylene at IEEE Condition 2. * The concentrations present are strongly correlated to electrical discharges of high energy and thermal faults in excess of 700° C. * Despite declining moisture levels and improving interfacial tension, oil power factor levels are on the rise, and dielectric strength is declining. This supports contamination in the oil from the high energy discharges and thermal faults. – The current MOAB/Ground SW configuration on TR-1 creates a fault in the station to signal the remote end breakers to open; this is a known safety hazard in legacy station designs. – The 138 kV line section towards Kanawha River terminates directly into the bus which creates a lack of operational flexibility when switching for faults on the circuit. – Carbondale Substation currently deploys 64 relays, implemented to ensure the adequate protection and operation of the substation. * 36 of the 64 relays (56% of all station relays) are in need of replacement. * 36 of the electromechanical which have significant limitations with regards to fault data collection and retention. Spare parts for these relays are difficult to obtain. Kincaid 138/69/46 kV Station – 46 kV CBs A, B, and J are all 1972 FK-72.5-27000-9 type breakers, accounting for 3 of 21 remaining of this model remaining on the AEP system. * Spare parts for these units are not available and this model type is no longer vendor supported * These breakers are oil filled without oil containment; oil filled breakers have much more maintenance required due to oil handling * These breakers have each exceeded the designed number of full fault operations (10). CB-A: 61, CB-B: 123, CB-J: 72 – GND transformer PH 1-3 * All three single phase units of GND TR are experiencing similar health deterioration. * There are elevated levels of Acetylene at IEEE condition 2 and Carbon Dioxide at IEEE Condition 2 or 3. * The presence of excess acetylene may be a product of arcing causing overheating on this unit. High levels of carbon dioxide support this observation. * In addition, significantly diminished oil interfacial tension corroborates the frequent overheating events. Sludge has likely developed in the oil from particulate formation during arcing and other fault events. This sludge impairs the natural circulation of oil. * Moisture levels are on the rise which can lead to diminished dielectric strength over time. – The current 138 kV MOAB/Ground SW configuration on TR-1 creates a fault in the station to signal the remote end breakers to open; this is a known safety hazard in legacy station designs. – Kincaid Substation currently deploys 51 relays, implemented to ensure the adequate protection and operation of the substation. * Currently, 45 of the 51 relays (88% of all station relays) are in need of replacement. * There are 45 of the electromechanical which have significant limitations with regards to fault data collection and retention. Of these relays, 18 are in the top 90th percentile of relays on the AEP system targeted for replacement by PCE. * There appears to be little room in the existing control house to accommodate a relay replacement of this suggested magnitude. – The existing RTU installed at Kincaid is a GE D200MEII/Ethernet and has 2 documented malfunction records Boomer 46 kV Station – Customer no longer served from this station, no load at this station. Raynes 46 kV Station – Customer no longer served from this station, no load at this station. Alloy 46 kV Station Hard Tap – Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. – Hard taps can also result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP027 | AEP | PJM West | 2019-08-29 | [5 empty] | Belle – Cabin Creek – Marmet Hydro 46 kV Circuit (7.58 miles) •Majority of the circuit is constructed with 1930s lattice structures. •Between 2015-2018 the circuit experienced 4 momentary and 3 permanent outage resulting in approximately 24 k customer minutes of interruption •There are currently 13 open conditions associated with the structures and hardware and include heavy rust, broken insulators and damaged shield wire hardware. •The line does not comply with current NESC Standards. •Most structures are situated on an extreme side hill, which also sits above the WV Turnpike which presents a significant danger/risk should the structures fail. •This line parallels the Belle – Cabin Creek – Marmet line, need AEP-2019-AP028.
AEP-2019-AP028 | AEP | PJM West | 2019-08-29 | [5 empty] | Belle – Cabin Creek 46 kV Circuit (7.14 miles) •Majority of the circuit is constructed with 1930s lattice structures. •Between 2015-2018 the circuit experienced 6 momentary and 2 permanent outage resulting in approximately 242 k customer minutes of interruption •There are currently 13 open conditions associated with the structures and hardware and include heavy rust, broken insulators and corroded shield wire. •The line does not comply with current NESC Standards •Most structures are situated on an extreme side hill, which also sits above the WV Turnpike which presents a significant danger/risk should the structures fail. •This line parallels the Belle – Cabin Creek – Marmet line, need AEP-2019-AP027.
AEP-2019-AP029 | AEP | PJM West | 2019-08-29 | [5 empty] | Marmet Hydro is currently served off a hard tap on the Belle – Marmet Hydro – Cabin Creek 46 kV circuit •Hard taps are difficult to maintain due to required outages or temporary jumper configurations in lieu of a switch. •Hard taps result in extended outages to customers due to the inability to sectionalize faulted facilities.
AEP-2019-AP030 | AEP | PJM West | 2019-08-29 |  |  |  |  | 138 kV delivery point request near Neibert, WV | Bandmill Coal LLC has requested a new transmission delivery point to serve a new facility in Neibert, WV. Projected load is 8 MW.
AEP-2019-AP032 | AEP | PJM West | 2019-08-29 |  |  |  |  | Pike County, Kentucky | Equipment Material/Condition/Performance/Risk: The 46 kV transmission Cedar Creek – Elwood 46kV circuit (~15.5 miles) is 1966 Vintage and has 81 open conditions. The majority of open conditions are structure related including rot top/shell, woodpecker and burnt damage. The two permanent outages on this circuit have caused 176,728 CMI over the past five years. Also over this time span, there have been 18 momentary outages.
AEP-2019-IM001 | AEP | PJM West | 2019-02-20 | 2019-06-17 |  |  |  | Medford – Blaine Street 34.5kV line | Medford – Blaine Street (~3.3 Miles) 1940’s vintage wood crossarm construction with cap and pin insulators There are currently 40 open conditions on this line. This trend is expected to increase as the structures and conductor age. Medford – Haymond (section in question is Medford – near 21st Street ~3.3 miles) 1940’s vintage wood crossarm construction with cap and pin insulators There are currently 29 open conditions on this segment of the line. This trend is expected to increase as the structures and conductor age. Haymond – Blaine Street (~3.7 miles) 1950’s vintage wood crossarm construction with cap and pin insulators There are currently 7 open conditions on this segment of the line. This trend is expected to increase as the structures and conductor age.
AEP-2019-IM002 | AEP | PJM West | 2019-02-20 |  |  |  |  | Hickory Creek - Main Street 34.5kV Line | Hickory Creek - Main Street 1 (~6.7 Miles) * 1950’s vintage wood pole line * There are currently 31 open conditions, This trend is expected to increase as the structures and conductor age. Hickory Creek - Main Street 2 (section in question is the Langley Extension ~.7 miles) * 1950’s vintage wood pole line * There are currently 11 open conditions on this segment of the line, This trend is expected to increase as the structures and conductor age.
AEP-2019-IM003 | AEP | PJM West | 2019-02-20 | 2019-05-16 |  |  |  | Tanners Creek, IN | * Tanners Creek * Currently a line fault on the Dearborn circuit causes 5 EHV breakers to open. This is above the AEP max of 4 and must be addressed. * According to the DEDSTFMRS PJM document, 200kV+ facilities with 7+ elements are required to be in a complete breaker and a half setup at a minimum. This facility has 9 elements and is currently in an incomplete breaker and a half setup.
AEP-2019-IM004 | AEP | PJM West | 2019-02-20 | 2019-04-23 |  |  |  | Greentown, IN | * Greentown * According to the DEDSTFMRS PJM document, BES facilities with 7+ elements are recommended to be in a complete breaker and a half setup at a minimum. This facility has 7 elements and is currently in an incomplete breaker and a half setup.
AEP-2019-IM005 | AEP | PJM West | 2019-02-20 | 2019-04-23 |  |  |  |  | Associated Needs: AEP-2018-IM010 Strawton - Arnold Hogan 138 kV * This line currently has 4 MOABS in series (2 at Aladdin and 2 at Jones Creek) which is above AEP’s max of 3.
AEP-2019-IM006 | AEP | PJM West | 2019-02-20 |  |  |  |  | Hamilton, Indiana Area Improvements | The load at Hamilton is 9.19 MW and its radially served from Butler station via a 7.74 miles long line. In addition to this there are significant open and closed conditions on the Butler - Hamilton 69kV Line. Butler - Hamilton 69kV Line * 1956 vintage wood pole line. * 33 open conditions with the majority being structure issues. * CMI - 5,268,522 Dome Tap 69kV Line * 1978 vintage wood pole line. * 14 open conditions with the majority being structural issues.
AEP-2019-IM007 | AEP | PJM West | 2019-02-20 |  |  |  |  | South Bend, Indiana Area | Kankakee - Jackson Rd 34kV Line (~4 miles) * Wood pole line * 88 open conditions with the majority being structure issues. This trend is expected to increase as the structures and conductor age.
AEP-2019-IM008 | AEP | PJM West | 2019-02-20 | 2019-05-20 |  |  |  |  | Decatur – Berne 69kV line 1966 vintage wood pole line This line is currently subject to 95 open conditions with the majority being structural issues. This trend is expected to increase as the structures and conductor age. Jay – Lincoln 138kV line 1953 vintage wood H frame line This line is currently subject to 111 open conditions with the majority being structural issues. This trend is expected to increase as the structures and conductor age. Antiville Potential economic developments have not materialized due to system load limitations.
AEP-2019-IM009 | AEP | PJM West | 2019-04-23 | 2019-06-17 |  |  |  | LaPorte-New Buffalo 69 kV line | * Bridgman 69 kV Station * Breakers C, A, & B 69 kV * 1968 vintage FK Oil breakers * Fault Operations: C(204), A(48) & B(58) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported * Three Oaks 69 kV Station * Breakers C & B 69 kV * 1968 vintage FK Oil breakers * Fault Operations: C(73) & B(63) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported * LaPorte 69 kV Station * Breakers B 69 kV * 1968 vintage FK Oil breakers * Fault Operations: B(62) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported. * Transformer #1 138/69/34 kV * 1967 vintage * Its showing significant signs of deterioration and has high levels of Carbon Dioxide dissolved in the oil. * Equipment condition concerns include dielectric strength breakdown (winding insulation), short circuit strength breakdown (due to the amount of through fault events), and accessory damage (bushings). * Laporte Junction – New Buffalo (IN) 69 kV Line (~4 Miles) * 1960’s vintage wood crossarm construction * Approximately 78% of the structures have Insect Damage * There are currently 132 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases.
AEP-2019-IM010 | AEP | PJM West | 2019-04-23 |  |  |  |  | Dowagiac, Michigan Area | Colby Station * Breakers A, B, C, D, and E * 1963-1968 vintage oil breakers * CB Fault operations: CB A(38), C(67), D(86), E(12) – Recommended(10) * Breaker B control cabinet has documented corrosion concerns * Since 2017 breaker D's operation counter hasn’t functioned * Currently contains a 3-terminal line within the station.
AEP-2019-IM011 | AEP | PJM West | 2019-04-23 | 2019-05-20 |  |  |  | Marion, Indiana | West End 34.5 kV station * AEP I&M Distribution is rebuilding and reconfiguring their West End Station to address aging equipment and capacity concerns.
AEP-2019-IM012 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | Illinois Road 138 kV station * Breakers A & B 69 kV * 1969 and 1970 vintage Oil breakers * Fault Operations: A(23) & B(67) – Recommended(10) *Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported
AEP-2019-IM013 | AEP | PJM West | 2019-04-23 | 2019-08-29 |  |  |  | Ft. Wayne, Indiana | Robison Park – Haviland 138 kV Line (~12 Miles) * 1926 vintage steel lattice line construction * There are currently 56 open conditions on this line with majority (84%) being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * Forced Momentary Outages: 2 * Forced Permanent Outages: 1 * The current line shielding angle on the steel towers is inadequate for current AEP shielding angle requirements.
AEP-2019-IM014 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | Robison Park – South Hicksville 69 kV Line (~27 Miles) * 1967 vintage wood cross arm construction. * There are currently 56 open conditions on this line with majority (94%) being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * 4/0 ASCR conductor with horizontal post type porcelain insulators. * CMI: 526,269 * Forced Momentary Outages: 6 * Forced Permanent Outages: 5 * St Joe Tap 69 kV Line (~0.6 Miles) * 1967 vintage wood cross arm construction * There are currently 3 open conditions on this line. The O&M cost of the line is expected to increase as the age of the line increases. * St. Joe is radially served out of Robison Park – South Hicksville 69 kV Line and it is susceptible to single event outages. * It occasional encounter floodwaters of Bear Creek that leave some of the existing poles inaccessible. * St. Joe Tap Switch * The Switch has accessibility challenges due to St. Joseph River floodwaters.
AEP-2019-IM015 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | The loads at Bixler and North Kendallville are 20.58 MW and 17.13 MW respectively. Bixler is radially served from a 2.89 mile long 138 kV line. North Kendallville is radially served from a 1.79 mile long 69 kV line.* Kendallville – North Kendallville 69 kV Line (~1.7 Miles) * 1960’s vintage wood pole construction * There are currently 5 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * CMI: 1,541,297 * Forced Momentary Outages: 1 * Forced Permanent Outages: 9
AEP-2019-IM016 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | Anthony – Harvest Park No.2 34 kV Line (~2.5 Miles) * 1930’s vintage wood crossarm construction * There are currently 14 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * Lincoln – Tillman 69 kV Line (~13 Miles) * 1968 vintage wood crossarm construction * There are currently 24 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * Anthony 34 kV station * Breakers H, Q, D, C & A 34 kV * 1970 vintage FK Oil breakers * Fault Operations: H(21), A(12) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported * Harvest Park 34 kV station * Breakers S, N, A & B 34 kV * 1962 vintage FK Oil breakers S, N & B * 1956 vintage FK Oil breakers B * Fault Operations: A(49) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported
AEP-2019-IM017 | AEP | PJM West | 2019-04-23 |  |  |  |  | Ft. Wayne, Indiana | Industrial Park – Wallen 34 kV (~3.3 Miles) * 1925 vintage steel lattice construction * There are currently 5 open conditions on this line with majority being structure issues. The O&M cost of the line is expected to increase as the age of the line increases. * Six wired Copper conductor with copper weld shield wire. Copper conductors become brittle with age and Copper weld conductor has long been obsolete * Industrial Park 138 kV * Breakers F, D & E 34 kV * 1967 vintage Oil breakers * Fault Operations: F(18), D(0) & E(14) – Recommended(10) * Breakers G 69 kV * 1967 vintage Oil breakers * Fault Operations: G(50) – Recommended(10) * Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require. Finding spare parts for these units is difficult or impossible, and these models are no longer vendor supported. * Multiple wood pole 138 kV transformer lead support structures inside Industrial Park Station.
AEP-2019-IM019 | AEP | PJM West | 2019-06-17 | [5 empty] | Adams 138/69kV station The 138/69kV XFR currently is protected by a high side ground switching MOAB. Currently there are 3 dissimilar zones of protection at this station with a 138kV line, 138kV bus and a 138/69kV transformer Pennville 138kV station This station’s through path is composed of wood support structures and cap and pin bus insulators, both have been identified as safety concerns. The Cap and Pin support insulators have a documented history of failing due to degradation in the glue that holds them together. It is currently AEP policy to remove these support style insulators whenever we come across them. The support structures for the station’s through path reside mostly outside of the station footprint. These bus support structures straddle the station fence which leaves most of the main bus, switches, insulators and support structures outside the station’s footprint where there is no ground grid. This has been identified as a safety hazard and will be addressed.
AEP-2019-IM022 | AEP | PJM West | 2019-06-17 | [5 empty] | Mount Etna 69kV Tap (~6.8 Miles) 1959 wood pole construction 5 open conditions 116 active maintenance events in the past 10 years Structures on this line fail to meet the current NESC loading requirements 7 permanent and 14 momentary outages in the 3 year timeframe between 2015-2018 641,081 CMI Radial lines are difficult to maintain without significant impacts to the customer
AEP-2019-IM023 | AEP | PJM West | 2019-06-17 |  |  |  |  | Deer Creek - Makahoy 138 kV Line | Deer Creek – Makahoy 138kV line ~15 miles – 1950’s wood pole construction ~1.5 miles – 1920”s steel tower construction 64 open conditions with the majority being structure and conductor issues 18 momentary outages 6 permanent outages over the last 10 years
AEP-2019-IM024 | AEP | PJM West | 2019-06-17 |  |  |  |  | Delaware - Kenmore 34.5 kV Rebuild | Delaware – Bethel overhead 34.5kV Line (2.8 miles) 1960’s vintage wood construction. 16 open conditions all related to structural issues. Issues with ROW encroachments. Bethel – Kenmore underground 34.5kV line (.8 miles) 1960’s vintage underground construction. Both cables are through common man-hole ducts, which can present a safety issue. Currently TFS personal will not work on this line unless both northern feeds to Kenmore are de-energized due to this configuration. Underground construction makes it difficult to identify and fix outages. This means that as this cable ages, the area will start experiencing prolonged forced outages. This line has already experienced multiple of these type of outages. This UG section was out for 14 straight days in June 2010 and 29 straight days in August 2017
AEP-2019-IM026 | AEP | PJM West | 2019-02-20 | 2019-05-20 |  |  |  |  | *Kenmore – 23rd street (Section is .53 miles) 34.5kV*Section has been identified as having multiple physically overloaded structures and must be addressed.
AEP-2019-IM027 | AEP | PJM West | 2019-08-29 | [5 empty] | Adams 69 kV Station: 69 kV Circuit Breaker D Vintage 1966 Oil filled McGraw Edison CF type breaker Last oil breaker at Adams station Oil filled breakers have much more maintenance required due to oil handling that their modern, vacuum counterparts do not require Spare parts are not available and these models are no longer vendor supported Fault operations (10) – Manufacturers recommended maximum (10)
AEP-2019-IM028 | AEP | PJM West | 2019-08-29 |  |  |  |  | NIPSCO Olive 345/138/69kV station | Olive 345/138/69 kV station NIPSCO has requested a new 69 kv delivery point at Olive station for a ~1.5 MW load.
AEP-2019-IM029 | AEP | PJM West | 2019-08-29 |  |  |  |  | NIPSCO Bosserman 138/69 kV Station | Bosserman 138/69kV station: NIPSCO has requested a new 69kV delivery point at Bosserman station for a ~1.5MW load.
AEP-2019-IM030 | AEP | PJM West | 2019-02-20 | [5 empty] | Hillcrest – Bluffton 69kV line 1964 vintage wood pole line This line is currently subject to 155 open conditions with the majority being structural issues. This trend is expected to increase as the structures and conductor age. Adams – Bluffton 69kV line 1957 vintage wood pole line This line is currently subject to 32 open conditions with the majority being rotting structural issues. This trend is expected to increase as the structures and conductor age. Kingsland 69kV station Breakers “A” and “B” 1969 vintage Oil breaker Fault Operations: A(31) B(27) – Recommended(10) WVPA/Heartland Industrial Park 1 (Pleasant station) WVPA/Heartland has requested a new 138kV delivery point to feed a new industrial park. 2 industrial customers are already building on this site with room for further expansion. This load growth further constrains an already constrained 69kV network WVPA/Heartland Industrial Park 2 (Ossian station) WVPA/Heartland has target this area for industrial development. Potential economic developments have not materialized due to system load limitations. Kinnerk (WVPA/Heartland station) Customer has made an offer to upgrade this station to 138kV in order to enable to connect 138kV to the Pleasant and Ossian industrial parks. Kingsland (I&M Distribution) I&M Distribution has indicated a want to move toward 138kV at this facility due to the expected load growth in the industrial park north of this station.
AEP-2019-IM031 | AEP | PJM West | 2019-02-20 | [5 empty] | Portland 69kV station Breakers “A” and “G” 1962-1969 vintage Oil breakers Fault Operations: A(57) G(89) – Recommended(10) Trinity Tap (Jay REMC/Wabash Valley Power Authority) Potential economic developments have not materialized due to system load limitations. WVPA is targeting this area for load growth.
AEP-2019-IM032 | AEP | PJM West | 2019-08-29 |  |  |  |  | Nipsco Bendix 34.5 Station | Bendix – West Side 34.5 kV line NIPSCO is modifying their Grandview feed on the Bendix – West Side 34.5kV line to become their main feed. This feed is currently normally open and is served off of a hard tap.
AEP-2019-IM033 | AEP | PJM West | 2019-09-12 |  |  |  |  | Dumont 765/345 kV Station | 765/345 kV Transformer No.2 at Dumont station 1994 vintage Transformer No.2 Phase 2 failed catastrophically in 2018. This unit had increased ethylene and methane which increased dramatically after a 2016 Phase 3 failure.
AEP-2019-IM036 | AEP | PJM West | 2019-09-12 |  |  |  |  | Sullivan 765kV Breaker Failure | Sullivan 765/345kV Station 765kV CB “A” Legacy ELF type circuit breaker that has a record of failure within AEP. Limited availability of parts should a failure event happen. Breaker CT’s are developing combustible gasses to the point where AEP has deemed this breaker a hazard and have disconnected it from the system until it’s been replaced.
AEP-2019-OH001 | AEP | PJM West | 2019-02-20 | 2019-07-24 |  |  |  | Glencoe-Somerton 69 kV Upgrade | The Glencoe-Somerton 69kV circuit is 22.5 miles in length and has numerous condition issues. Within the last 5 years, it has experienced 18 momentary outages (3.6 per year) and 7 permanent (sustained) outages (1.4 per year). The average outage duration has been 13.7 hours. AEP and South Central Power Co-op customers served from this circuit suffered nearly 3.5 million minutes of customer interruption (CMI) during the 2015-2018 timeframe. The circuit currently has 148 open conditions (43 structural, 23 on conductor, 5 for shielding/grounding, 24 for hardware, and 53 for forestry/ROW). The majority of the wood poles were installed in 1953 and 1970 (84% of circuit length). The conductor was also primarily installed in 1953 (219 kcmil ACSR) and 1970 (336 kcmil ACSR). The majority of the outage causes have been attributed to T-Line condition issues. The two 69kV delivery points for South Central Power Co-op’s Beallsville and Pipe Creek stations are connected via hard taps (no sectionalizing switches present). This requires an outage to the customer whenever maintenance or emergency repairs must be done on either side of the customer tap.
AEP-2019-OH002 | AEP | PJM West | 2019-02-20 | 2019-05-20 |  |  |  |  | The Blackhawk-Dillonvale-Sparrow 69 kV line was originally constructed in 1918 and approximately 30% of the wood structures are still from 1918. More than half of the structures are of pre-1980 vintage and are affected by heavy rot and woodpecker/insect damage. 70% of the conductor is from 1926 (or prior) and is showing signs of tensile-related failures. There are 180 open A conditions on this line. Sections of the Blackhawk-Parlett line (Blackhawk Extension, Raider Extensions and Rexford Extension) have been recently rebuilt to 138 kV standards. (Shown in Red)
AEP-2019-OH003 | AEP | PJM West | 2019-02-20 | 2019-05-20 |  |  |  |  | A Customer plans to install a 2nd 69/12 kV transformer in their facility to support increased load. This customer had already procured a transformer in advance.
AEP-2019-OH004 | AEP | PJM West | 2019-03-25 | [5 empty] | * Timken 138/23kV Station (vintage 1966) has many asset renewal issues, which is a concern, as the Station serves one of AEP’s largest industrial customers. * The 138/23 kV transformer #3 (vintage 1966) has had overheating events, insulating paper carbonization, and signs of gassing. * The 138/23 kV transformer #1 (vintage 1966) has dielectric strength breakdown from numerous through-fault events. * There are two oil-filled 138kV circuit breakers (A & B, GE ‘FK’ type, rated 1200A / 20.9kA) that actually pre-date the station (1953-vintage, as they were transferred from an older station). There are no oil-containment systems for the transformers or breakers. * The protection & control system is very antiquated, and comprises of 59 electromechanical relays, 1 static relay, and an obsolete RTU. EM relays have no spare part availability, lack vendor support, have no SCADA functionality, and lack fault data collection ability. The control house has no fenced boundary which is a security concern. * An outdated pilot wire scheme connects to the two 138kV remote-ends. * Timken is also space constrained making any improvements/modifications to the Station difficult. * Timken is a 3 breaker Station in a straight-bus configuration (2- 138kV sources, 4- 138-23kV transformers). This configuration has several instances of dissimilar zones of protection (bus, line, and transformer ) which can cause miss-operations and over tripping. In addition, a lack of sectionalizing makes maintenance a concern from an customer outage perspective.
AEP-2019-OH005 | AEP | PJM West | 2019-03-25 | [5 empty] | A customer has requested new service south of Benwood, West Virginia. The forecasted peak demand is 8 MVA.
AEP-2019-OH006 | AEP | PJM West | 2019-03-25 |  |  |  |  | Moundsville, WV | A customer has requested new service four miles east of Moundsville, West Virginia. The forecasted peak demand is 20 MVA.
AEP-2019-OH007 | AEP | PJM West | 2019-03-25 | [5 empty] | Findlay Center Station: * 34.5 kV CB’s A, B, C, and D are oil type breakers (vintage 1962). Many of these breakers have exceeded the manufacturers recommended number of fault operations (10): “ A “(37), “B “(7),”C” (6), and “D” (39). * 34.5 kV cap switcher AA is a MARK-V model (2004) which has been identified for replacement due to lack of spare parts, operational and reliability concerns, and maintenance issues. Findlay Station: * 34.5 kV CB’s A, B, D, and E are oil type breakers (vintage 1953– 1955). Many of these breakers have exceeded the manufacturers recommended number of fault operations (10): “A”(20), “B” (33), “D” (41), and “E” (3). * 34.5 kV cap switcher AA is a VBM model (1988) which has been identified for replacement due to lack of spare parts, operational and reliability concerns, and maintenance issues. Plaza Street Station: * 34.5 kV CB A is an oil type breaker (vintage 1948). This breaker has exceeded the manufacturers recommended number of fault operations (10): “A” (13). East Findlay Station: * The three-way switch (1958) has ongoing difficulties maintaining proper alignment of switches. The insulators are cap-and-pin type which often physically failing during switching operations. **Oil breaker maintenance is difficult due to the oil handling requirements and there is a risk for oil spills during failures and maintenance. These breakers are FK model breakers that have historical reliability concerns and lack of spare part availability.
AEP-2019-OH008 | AEP | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Meigs 69 kV CB “1” is a 1954 oil-filled circuit breaker. Oil breakers are difficult to maintain due to oil handling requirements and risk of oil spills during maintenance and failures. This model (G.E. FK-439-69-1000-4) is also recommended for replacement due to reliability issues, lack of vendor support, and lack of spare part availability. In addition, this CB has exceeded the manufacturers recommended number of fault operations: CB 1 (20).
AEP-2019-OH009 | AEP | PJM West | 2019-03-25 | 2019-06-17 |  |  |  | Parlett-East Cadiz 69 kV line | * East Cadiz Switch (1950’s) serves Cadiz station on a mile long radial line, which is in a remote part of our system. In addition, this switch is sitting in an area prone to flooding. * The Parlett-East Cadiz 69kV line, approximately 8 miles long, is comprised of deteriorated 1929 vintage wood structures and still has original 1/0 Cu and 4/0 ACSR conductor on it. * The South Cadiz-East Cadiz 69kV line, approximately 2 miles long, is comprised of deteriorated 1954 vintage wood structures with the original 4/0 ACSR conductor on it. * The Parlett-South Cadiz 69kV line has 190 open conditions. * All load at Nelms Station has been removed. * The Blackhawk – Miller Switch 69 kV line section, approximately 2.5 miles long, has some of the original 1918 conductor still on it (1/0 Cu). More than half of the wood pole structures on this sections are of pre1980 vintage and are affected by heavy rot, woodpecker, & insect damage through the years. There are 22 open conditions on this circuit.
AEP-2019-OH010 | AEP | PJM West | 2019-04-11 | 2019-06-13 |  |  |  | Don Marquis-Stuart 345 kV line | AEP will take over full ownership of specific facilities previously owned by the CCD partnership as assigned by an approved FERC filing. The planned work will allow transfer ownership and control of these facilities to AEP. AEP will apply our rating methodology to these assets. * Killen Plant is retiring and AEP is taking ownership of the Don Marquis-Stuart 345kV line except for the 345kV leads going towards Killen Station which will be retired by Dayton Power. AEP needs to bypass the Killen taps to complete the Don Marquis-Stuart 345kV circuit.
AEP-2019-OH011 | AEP | PJM West | 2019-03-25 | [5 empty] | * The Apple Valley (Licking Co-op) 138 kV delivery point serves approximately 2,300 customers with a peak demand of 6.5 MW. Apple Valley isn’t 100% transferrable during all times of the year and can take several hours to complete the required switching. This delivery point has experienced 971,280 customer minutes of interruption. * This delivery point is connected with a hard tap which limits sectionalizing during outages and maintenance. In addition, relay coordination can be difficult with hard taps.
AEP-2019-OH012 | AEP | PJM West | 2019-03-25 | [5 empty] | * South Central Power is rebuilding Lockbourne 138kV Station due to asset renewal conditions. Lockbourne is currently radially served via AEP’s Harrison Station, this line is partially owned by AEP and South Central Power with the point of ownership change being Circleville. The current loading on this radial line is 65MW with plans for increased load. Total CMI 2.7M over 3 year period. (2015-2018). * Radial service restricts the ability to perform routine maintenance and can cause extended outages to customers. The maintenance of radial transmission lines often requires cost-prohibitive temporary facilities or other labor-intensive measures.
AEP-2019-OH013 | AEP | PJM West | 2019-04-23 |  |  |  |  | Franklin County Ohio | * AEP Ohio is requesting a new delivery point next to the existing Fifth Ave Station, which is being retired. This new delivery point will be able to accommodate existing load and future expansion. * The existing Fifth Avenue Station is being removed due to asset renewal conditions and the fact that it cannot be expanded due to being land locked on all sides. * This station has limited transferability, serves approximately 7,000 customers via a single transformer (22 MVA of load on the tertiary winding), and is located in an urban environment. * 13/16 relays at Fifth Ave are Electro Mechanical type. These relays have limited spare part availability, lack vendor support, have no SCADA ability, and lack fault data collection. * The RTU at this Station has a high failure rate, lacks spare parts, and no longer provides load data. * AEP Ohio has identified several of the feeders served out of this Station that are expected to exceed their capacity with the load growth in the area.
AEP-2019-OH014 | AEP | PJM West | 2019-04-23 |  |  |  |  | Adams County, Ohio | * The existing 28.5 mile, 69 kV line section between Stuart (DP&L/Duke) and Seaman(AEP) was constructed in 1974 using wood pole structures with 636 ACSR conductor. There are 260 open A conditions distributed across the 170 structures on this line. * The Stuart-Seaman 69 kV circuit has experienced over 2.2 million customer minutes of interruption in the past three years: 753,716 for AEP and 1,517,618 for Adams Coop.
AEP-2019-OH016 | AEP | PJM West | 2019-04-23 |  |  |  |  | Bucyrus, Ohio | * The Bucyrus-Howard No.2 69 kV circuit was originally constructed in 1919 with wood structures and copper conductor (#1 CU and 3/0 CU). 84% of the line still utilizes the original 1919 copper conductor. * Some structures have been replaced over the years; however, they have been like for like wood pole replacements. * The circuit has had 38 forced operations in the last 11 years of which 7 have been permanent and resulted in 54 hours of down time. 2 out of the 7 outages have been caused by conductor failures, the most recent of which resulted in 188,000 CMI. * There are currently 144
AEP-2019-OH017 | AEP | PJM West | 2019-04-23 |  |  |  |  | Columbus, Ohio | * AEP-Ohio is requesting a new 138 kV delivery point at Hayden Station by 6/1/2020. * There are several highly loaded distribution circuits at Dublin, Davidson, & Hilliard Stations that require a new delivery point.
AEP-2019-OH018 | AEP | PJM West | 2019-04-23 |  |  |  |  | Muskingum to Stark Counties, Ohio | * The Philo-Sunnyside 138 kV transmission line is 75 miles long, originally constructed in 1923. The vast majority of the structures are still original, as well as the six-wired 336 ACSR conductor, insulators, and hardware. This line is made up of several circuits connected between Muskingum River and Sunnyside stations. * Insulator assemblies are showing corrosion and deterioration, which could lead to additional failures and safety concerns. * There have been 2.1 million customer-minutes-of-interruption (CMI) over the 2008-2018 time period. * This line has experienced 44 momentary outages and 8 sustained outages over the past 10 years. * The East New Concord Station is connected via a hard tap (no sectionalizing switches present). Lack of sectionalizing requires a substation outage whenever maintenance or emergency repairs are performed on either side of the 138 kV tap.
AEP-2019-OH019 | AEP | PJM West | 2019-04-23 |  |  |  |  | Belmont / Harrison County, Ohio | * The Glencoe – Robyville 69 kV circuit is 13.3 miles long and originally constructed in 1915-1925 using wood pole structures. This circuit currently has 556 ACSR 18/1 (Osprey) conductor rated for 126 MVA WE. * The Glencoe – Robyville 69 kV circuit has 136 open A conditions which includes broken shield/ground wires, heavy structure rot, woodpecker damage, broken insulators, and split cross arms/knee braces. * This circuit has experienced 789,612 CMI between 2013 – 2018. * The existing switch at Highland Terrace two-way GOAB that restricts our ability to perform routine maintenance and restoration activities in this remote area of our system. * The Shepherdstown delivery point is connected via a hard tap which limits operational flexibility, can cause over tripping and relay mis-operations, and restricts restoration activities.
AEP-2019-OH020 | AEP | PJM West | 2019-04-23 |  |  |  |  | Columbus, Ohio | * Equipment Material/Condition/Performance/Risk: * The 40 kV system is an obsolete voltage class and as a result is difficult to obtain replacement parts. * Wilson Road Station * 1 – 40 kV: CB-34 has 55 Fault Operations * 1 – 40 kV: CS-AA is an SF6 2030-69 model circuit switcher, which has been identified as needing replacement due lack of to spare part availability, historical reliability, and lack of vendor support. * 3 – 40 kV: (CBs 30,35, & 36) & 8 - 138 kV: (CBs 2-9) are oil type breakers. * 7-138 kV: (CBs 2-7) 1974 vintage FK oil breakers. * 2-138 kV: (CBs 8 & 9) 1967 & 1968 vintage GM oil breakers. * 138 kV CB-4 has 17 Fault Operations. * 195 – Electromechanical relays: EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. * Wilson Continued: * 13 – Microprocessor relays: The identified relays are obsolete, no longer supported, or have been identified as high risk of failures. * 4 – Static relay: this type of relay has significant limitations with regard to fault data collection and retention. * McComb Station * 5 – 46 kV: (CBs 41-45) oil type breakers * Fault Operations: (CB-42 = 15 & CB-43 = 26) * 1 – 138 kV CS-CC (Mark V): This model of switcher has been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. It also has 16 fault operations. * 117 – Electromechanical relays: EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. * McComb Station utilizes either ground switch/MOAB’s or MOAB’s for high side transformer protection. * Operational Flexibility and Efficiency: * There is currently a 3-terminal 138 kV hard tap between Wilson, Fisher Rd, and Hall Stations. 3-terminal lines are problematic because they limit sectionalizing and can cause mis-operations and over tripping. A single breaker failure will result in the loss of 5 transformers. * Customer Service: * AEP-Ohio plans to replace the Briggsdale 40 kV Station with a new Reaver 138 kV Station (s1606), which eaves Phillipi (customer owned station) on the local 40 kV system.
AEP-2019-OH021 | AEP | PJM West | 2019-04-23 | 2019-06-17 |  |  |  | Carrothers 69 kV station | * The Carrothers 69 kV Station has three dissimilar zones of protection (Bus, Transformer, and Line). Dissimilar zones of protection can cause misoperations and over tripping.
AEP-2019-OH022 | AEP | PJM West | 2019-05-20 | 2019-06-17 |  |  |  | Vassell 138 kV station | Transformation at the 34.5/13kV Sunbury station failed leading to the immediate need to install a 138/13kV skid station at Vassell station to continue serving customer load. AEP-Ohio has requested to remove the existing temporary skid station outside Vassell station and to replace it with a new 138kV delivery point installation at Vassell station.
AEP-2019-OH023 | AEP | PJM West | 2019-05-20 | [5 empty] | Equipment Material/Condition/Performance/Risk: The East Beaver – Buckeye Co-Op 69 kV line was built in 1952. 60 out of the 71 wood pole structures on this 4.5 mile line are original. There are currently 26 open A conditions on this line, including heavy rot and woodpecker & insect damage. Operational Flexibility and Efficiency. Currently, the East Beaver 138/69 kV Station has more than 2 dissimilar zones of protection (bus, line, and transformer).
AEP-2019-OH024 | AEP | PJM West | 2019-05-20 | [5 empty] | *The 1943 Hillsboro – Millbrook Park 138 kV circuit (~52 miles) is wood pole construction and has 1,342 open conditions. *The majority (93%) of the original conductor (vintage 1944 & 1948) is 477 MCM (26/7) ACSR and is still in-service. *Half of the wood pole structures from the 1940’s are still in-service; the remaining are a mixture from 1960’s – 1980’s. *There are additional concerns with the shielding, grounding, and hardware along this 52 mile long line. *Sinking Springs is in a remote part of AEP’s service territory making manual switching difficult.
AEP-2019-OH025 | AEP | PJM West | 2019-05-20 | [5 empty] | *The South Point – Portsmouth 138 kV double circuit is 34.7 miles and the Bellefonte 138 kV Extension is 4 miles in length.*The conductor is primarily 397.5 ACSR (167 MVA).*The South Point-Portsmouth line was originally constructed in 1929, with the majority of the structures and conductor being original.*There are 45 open conditions on the line, including conductor issues, burnt/broken insulators, and loose/broken conductor hardware.*Insulators of this vintage have shown heightened failure rates.*In general, several issues impact 1920 lattice tower lines:*The steel conductor attachment plates have significant wear resulting in a loss of 50% of its strength.*The cross arm hanger tension members are single mode of failure elements that are deteriorated and undersized due to the original design criteria.*Lattice towers of this vintage do not meet current design requirements for wind and ice loading.*Foundations are undersized for modern wind loading.*Towers are beginning to show corrosion.
AEP-2019-OH026 | AEP | PJM West | 2019-05-20 | [5 empty] | *The 58-mile South Point – Sporn 138 kV double circuit line has four delivery points that are connected via hard taps. The hard taps complicate restoration activities and extend outages.*The four Buckeye Coop delivery points are at Mercerville, Windsor, Fayette and Addison. These stations are in a remote part of AEP’s service territory, which makes outage restoration activities more difficult and resulting in longer outages.*Over the last five years these delivery points have accumulated 1,348,755 CMI.
AEP-2019-OH027 | AEP | PJM West | 2019-05-20 | [5 empty] | *The majority (94%) of the Sunnyside-Torrey 138 kV line (4.3 miles) is comprised of steel lattice towers built in 1918, with the remaining 6%, dating back to 1954.*The conductor is original vintage (1918), consisting of 6-wired 200 MCM copper & 250 MCM copper.*Note that the 0.3-mile customer tap was built in 2007 and is in adequate condition.
AEP-2019-OH028 | AEP | PJM West | 2019-03-25 | [5 empty] | Coolville 69kV station is radially served on a 1954 vintage line (~12.6 miles) utilizing 4/0 ACSR 6/1 (Penguin) conductor (50/63 MVA SN/WN). This radial line has 84 structures, 22 of which have pole related open conditions and 28 of which have ground lead wire issues/concerns. It has experienced 4.4 million CMI over the last three years. Radial lines restricts the ability to perform routine maintenance and restoration activities.
AEP-2019-OH029 | AEP | PJM West | 2019-06-17 | [5 empty] | Buckeye Power, on behalf of South Central Power Co-op, has requested transmission service in Stock Township of Harrison County, Ohio. The forecasted peak demand is 16 MVA, with an in-service date of 9/1/2020.
AEP-2019-OH030 | AEP | PJM West | 2019-06-17 | [5 empty] | Line: Crooksville – North Newark (Vintage - 1952) Length: 30.63 Miles Original Construction Type: Wood Original Conductor Type: 266,800 CM ACSR 26/7 (Partridge) Momentary/Permanent Outages: 5 outages last 5 years Number of open conditions: 338 Open conditions include: Pole Rot, Insect/Bird Damage, Damaged Conductors, Ground Wires, & Guy Wires.
AEP-2019-OH031 | AEP | PJM West | 2019-06-17 | [5 empty] | Honey Creek SW - North Central Co-op Line Section (vintage 1955) Length: 8.06 Miles Original Construction Type: Wood Original Conductor Type: 1/0 ACSR 6/1 (Raven) Momentary/Permanent Outages: 13 in the past 5 years CMI: 2,505,168 Number of open conditions: 46 Open conditions include: Damaged HP Insulators, Poles, Ground Lead, & Guy Wires Additional Info: Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH032 | AEP | PJM West | 2019-06-17 | [5 empty] | West Rockaway – North Central Co-op Line (vintage 1960) Length: 8.32 Miles Original Construction Type: Wood Original Conductor Type: 1/0 ACSR 6/1 (Raven) Momentary/Permanent Outages: 13 in the past 5 years CMI: 2,505,168 Additional Info: Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH034 | AEP | PJM West | 2019-06-17 | [5 empty] | South Greenwich-Willard (vintage 1964) Length: 15.22 Miles Original Construction Type: Wood Original Conductor Type: 4/0 ACSR 6/1 (Penguin) Momentary/Permanent Outages: 13 in the past 5 years Number of open conditions: 77 Open conditions include: Damaged Insulator, Structure, Guy Wire, Ground Lead Wire, & Shield Wire Radial service severely restricts the ability to perform routine maintenance and restoration activities. The maintenance of radial transmission lines often requires costly temporary facilities or other labor-intensive measures involving energized work because a maintenance outage to such radial loads is generally not feasible.
AEP-2019-OH035 | AEP | PJM West | 2019-06-17 | [5 empty] | Holmes-Wayne Electric Cooperative customers are connected to the Trail and Alpine delivery points that are served from the Berlin – Sugarcreek Terminal and Beartown – Moreland Sw 69 kV circuits in eastern Holmes County. The Trail and Alpine delivery points have accumulated approximately 2.4 million minutes of CMI in the past five years. The Trail delivery point is served radial via a ~4.1 mile wood pole line out of Shiehill Road Switch. Maintenance on the line is difficult to coordinate as it requires outages to Trail station.
AEP-2019-OH036 | AEP | PJM West | 2019-06-17 |  |  |  |  | Western Columbus/Beatty Area | Hilliard Station 69 kV: 69 kV Circuit breakers 61, 62, and 63 - CF-48 type oil breakers. (1967, 1967, and 1966 vintage) - These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. - Other drivers include damage to bushings and the breakers have experienced 15, 21, and 31 fault operations respectively. The manufacturer's recommendation for this type of breaker is 10. Relaying - 105 of the 119 relays are electromechanical relays. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Station Structures - The structure steel is deteriorating due to rust and the foundation supporting the steel shows severe cracking. 69/13.2 kV Transformer #1 and #2 - AEP Ohio Distribution Transformers 1 & 2 are protected by high speed ground switch MOABs. Beatty Station: 69 kV Circuit breakers 63, 64, and 65 - FK type oil breakers. (1965, 1966, and 1965 vintage) - These are oil breakers that are difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. - Other drivers include damage to bushings and the breakers have experienced 5, 34, and 6 fault operations respectively. The manufacturer's recommendation for this type of breaker is 10. 138/69 kV Transformers #1 and #2 - Showing signs of deterioration. Both are experiencing short circuit strength breakdown (due to the amount of through fault events) and dielectric strength breakdown with a history and overheating and stray gassing. - Transformers 1 & 2 are in the same 138 kV zone of protection causing both to experience an outage whenever there is a fault in that zone. 345/138 kV Transformer #4 - Showing signs of deterioration. Experiencing short circuit strength breakdown (due to the amount of through fault events), dielectric strength breakdown, and bushing damage. 138/13 kV Transformer #5 - Currently directly connected via a MOAB to the 138 West Bus at Beatty Station 138/13 kV Transformer #6 - Currently directly connected via a ground switch MOAB scheme to the 138 East Bus at Beatty Station 138 kV McComb line - Connected via a partial breaker string resulting in line outage with an outage of the east bus, including those caused by outage of Transformer #6. Cole Station 138/13 kV: - AEP-Ohio has requested a new 138/13 kV delivery point at Cole station. Trabue Station: * More than two dissimilar zones of protection in the 138 kV yard (transformer, line, and bus) * AEP-Ohio has requested sectionalizing to separate two distribution transformers to improve reliability. * 60 of the 86 relays are electromechanical relays. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Blair - Galloway 69 kV circuit: Line section between Galloway station and Structure 26 (~1.0 miles) - Wood pole line with structures and conductor dating back to 1968. - 19 open structure conditions including rotted and split poles.
AEP-2019-OH037 | AEP | PJM West | 2019-06-17 | [5 empty] | The Cameron-Switzer 69kV circuit is 16.2 miles long and serves 3 wholesale customer stations (over 3,800 customers), with a combined peak load of 11 MW. The circuit is radially fed from AEP’s Switzer Station, making it difficult to perform proactive maintenance or restoration activities after an outage. The circuit is located in a remote part of AEP’s service territory and traverses very hilly and wooded terrain. The 69kV transmission line is of wood pole construction and was built in 1970. There are currently 121 open conditions on the circuit, with the majority being structure deficiencies (e.g., burnt insulators, insect damage, & cracked cross-braces). In addition, the City of Woodsfield is served via a 69kV hard tap, with no line sectionalizing switches present. South Central Power Co-op has reported 1.1 million customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH038 | AEP | PJM West | 2019-06-17 | [5 empty] | 138kV circuit breaker 105S at Hyatt station is showing signs of deterioration. This is an oil breaker installed in 1980. Oil breaker maintenance has become more difficult due to the oil handling required to maintain them. Oil spills are frequent with breaker failures and routine maintenance and can become an environmental hazard. This is the last remaining oil breaker at Hyatt. Transformer 1A has failed at Hyatt station and needs to be replaced. Transformer 1B is the same age (1973) and type, and Transmission Field Services has expressed similar concerns with 1B as they did with 1A (pre-failure), including dielectric breakdown (insulation), accessory damage (bushings), and short circuit breakdown (due to through faults). The existing configuration of Hyatt station includes both 345/138kV transformers in the same protection zone. The 345kV side of this zone is only energized from one bus such that a single bus outage would outage both transformers.
AEP-2019-OH039 | AEP | PJM West | 2019-06-17 | [5 empty] | Lott Delivery Point (CEC): Buckeye Power, on behalf of Consolidated Electric Cooperative, has requested transmission service in Delaware County west of Centerburg, Ohio. Consolidated Electric Cooperative customers are currently connected to a radial 34.5 kV distribution line from AEP Ohio’s Trent station. The delivery point has consistently been identified as having poor reliability by Buckeye. Consolidated Electric Cooperative has reported approximately 700 thousand customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH040 | AEP | PJM West | 2019-06-17 | [5 empty] | Derwent – Senecaville 69 kV circuit The Derwent – Senecaville 69 kV circuit is ~4.3 miles long and serves a AEP Ohio and Guernsey-Muskingum Electric Cooperative station radially out of Derwent station. Guernsey-Muskingum Electric Cooperative and AEP Ohio customers are currently served off the radial line. Maintenance on the line is difficult to coordinate as it requires outages to multiple stations. Guernsey-Muskingum Electric Cooperative has reported approximately 210,000 customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH041 | AEP | PJM West | 2019-06-17 | [5 empty] | Springfield Radial 69 kV Line Maintenance of the 4.5-mile radial line is difficult to coordinate as it requires an outage to Carroll’s station. Carroll Electric Cooperative has reported approximately 204,000 customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH042 | AEP | PJM West | 2019-07-24 |  |  |  |  | Hocking, Ohio | East Logan – South Lancaster 69kV (vintage 1923) * Length: 16.43 Miles * Original Construction Type: Steel Lattice/Wood * Original Conductor Type: 2/0 Copper * Momentary/Permanent Outages: 43 total outages * CMI: 872,607 in the last 3 years * Number of open conditions: 40 – Open conditions include: Burnt/broken insulators, pole rot, insect damage, damaged conductor
AEP-2019-OH043 | AEP | PJM West | 2019-07-24 |  |  |  |  | Newark, Ohio | North Newark – Sharp Road 138 kV (vintage 1951) * Length: 19.38 Miles * Original Construction Type: Wood Pole * Original Conductor Type: 477 kcmil Hawk * Number of open conditions: 68 – Open conditions include: Burnt insulators, insect damage, pole rot, woodpecker damage
AEP-2019-OH044 | AEP | PJM West | 2019-07-24 |  |  |  |  | Vinton, Ohio | * South Central Power is requesting a new 138 kV delivery point on the Lemaster – Ross 138 kV circuit by September 2020. Anticipated load is about 4 MW.
AEP-2019-OH045 | AEP | PJM West | 2019-07-24 |  |  |  |  | Washington County, Ohio | * Buckeye Power, on behalf of Washington Electric Cooperative, has requested transmission service in western Washington County, Ohio. * Washington Electric Cooperative customers are currently connected to radial 23 kV and 12 kV AEP Ohio distribution lines in the area. * The delivery points connected to the 23 kV system have consistently been identified as having poor reliability by Buckeye. * Washington Electric Cooperative has reported approximately 745 thousand customer-outage minutes (CMI) over a three year period (2015-2017).
AEP-2019-OH046 | AEP | PJM West | 2019-07-24 |  |  |  |  | Wayne County, Ohio | * Holmes-Wayne Co-op’s Moreland delivery point is served via a hard tap from the Beartown-Moreland 69kV circuit, with no line sectionalizing switches present. The hard tap limits operational capabilities in the area. It is difficult to coordinate maintenance efforts because the T-line cannot be removed from service without a customer outage for Holmes-Wayne Co-op. * Load is approximately 7 MVA. * CMI: .155 M reported by Holmes Wayne (2015-2018)
AEP-2019-OH047 | AEP | PJM West | 2019-07-24 |  |  |  |  | Senecaville/Summerfield, Ohio | Derwent – Summerfield 69 kV * Majority of 13.8 mile circuit utilizes wood structures installed in 1962. * Circuit utilizes 336.4 kcmil ACSR 30/7 Oriole conductor installed in 1962. * Five momentary and permanent outages over last three years. * 62 Open Structure/Conductor conditions * Insect damage, woodpecker holes, along with rotted and cracked structures.
AEP-2019-OH050 | AEP | PJM West | 2019-08-29 | [5 empty] | •The Bladensburg Licking Rural Electrification Co-op (LRE) 138 kV delivery point, connected to the 45 mile North Bellville – Ohio Central 138 kV circuit, has a load of 3.9 MW peak demand serving 1449 customers. The Bladensburg load is 100% transferrable but under high loading conditions transferring loads can take several hours. For heavy loading periods LRE has experienced areas of low voltage while transferring loads. •The Blandensburg delivery point has experienced approximately 553,000 minutes of CMI over the last 5 years. •This delivery point is connected to the North Belleville – Ohio Central 138 kV circuit via a hard tap which limits operational flexibility and the effectiveness of protection schemes. In addition, it is difficult to coordinate maintenance efforts because the line cannot be removed from service without either a customer outage or temporary jumper configuration.
APS-2019-001 | APS | PJM West | 2019-01-11 | 2019-02-20 | 2019-07-26 | s1826 |  |  | New Customer Connection - A customer requested 138 kV service; anticipated load is 15 MW; location is near the Pursley - Franklin 138 kV line. Requested in-service date is June 2020.
APS-2019-002 | APS | PJM West | 2019-01-11 | 2019-02-20 | 2019-07-26 | s1827 |  |  | New Customer Connection * A customer requested 138 kV service, anticipated load is 20 MW, location is near the Fawn - Lawson Jct 138 kV line. * Requested in-service date is July 2020.
APS-2019-003 | APS | PJM West | 2019-03-25 | 2019-07-24 |  |  |  | Crupperneck – Grassy Falls 138 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need Number ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦-------------¦------------------------------------------¦--------------------------------¦-------------------------------------¦-----------------------------¦ ¦ APS-2019-003 ¦ Crupperneck – Grassy Falls 138 kV Line ¦ 160 / 192, 293 / 306 ¦ 160 / 192, 308 / 376 ¦ Line Relaying ¦
APS-2019-004 | APS | PJM West | 2019-03-25 | 2019-07-24 |  |  |  | Collins Ferry – Lake Lynn 138 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ Need Number ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦-------------¦------------------------------------------¦--------------------------------¦-------------------------------------¦-----------------------------¦ ¦ APS-2019-004 ¦ Collins Ferry – Lake Lynn 138 kV Line ¦ 329 / 406, 324 / 395 ¦ 353 / 406, 324 / 395 ¦ Substation Conductor ¦
APS-2019-010 | APS | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  | Elko – Shawville 230 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Elko – Shawville 230 kV Line Exiting line rating: 489/554
APS-2019-011 | APS | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  |  | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Shawville – Shingletown 230 kV Line Exiting line rating: 489/554
ATSI-2018-001 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1754 |  | Avon 345/138 kV transformer | Avon 345 / 138 kV 448 MVA #91 Transformer * Transformer is gassing at an increasing rate * Oil condition is degraded * Leaks - Not cost effective to repair * Severe loading history * Cooler condition is degraded
ATSI-2018-002 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1755 |  | Fox 345/138 kV transformer | Fox 345 / 138 kV 224 MVA #5 Transformer * Oil Pump/cooler maintenance * Aging/deteriorating bushings * Increased failure risk Fox 138 kV Circuit Breaker Q5 * Mechanism issues * Aging/deteriorating bushings * Spare part availability/vendor support limitations * Negative impact on equipment health (transformer)
ATSI-2018-003 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1756 |  | New Castle | New Castle 138 / 69 kV 75 MVA #7 Transformer * Oil Leaks/moisture ingress * Aging/deteriorating bushings * Increased failure risk New Castle 69 kV Circuit Breaker B32 * Mechanism issues * Aging/deteriorating bushings * Spare part availability/vendor support limitations * New breaker will offer improved transformer protection
ATSI-2018-004 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1757 |  | Beaver 345/138 kV transformer | Beaver 345 / 138 / 13.2 kV 392 MVA #1 Transformer * Oil Pump issues and maintenance * Increased failure probability * Aging/deteriorating bushings Beaver 345 / 138 / 13.2 kV 392 MVA #2 Transformer * Oil Pump issues and maintenance * Increased failure probability * Aging/deteriorating bushings
ATSI-2018-005 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1758 |  | Nfield Jun Bus | Northfield 138 kV Bus 2 and Bus 4 * Deteriorated bushings and insulators, increased failure risks * Reliability issues, EM relaying mis-operations Juniper 138 kV Bus 1 * Deteriorated bushings and insulators, increased failure risks * Reliability issues, EM relaying mis-operations
ATSI-2018-006 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1759 |  | Frisco Maple | Frisco-Maple # 1 and #2 69 kV line Terminal Equipment * Mitigate PJM issued PCLLRWs / Pre-contingency switching orders, eight times, for thermal concerns on the 69 kV system under contingency conditions. - Loss of the New Castle-Hoytdale #1 and New Castle-Hoytdale #2 138 kV lines. - Results in potential thermal loading greater than 100% on the Frisco-Maple #1 69 kV line or potential thermal loading on the Frisco-Maple #2 69 kV line depending on system conditions.
ATSI-2018-007 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1794 |  |  | Zelienople 69 kV Area Load At Risk * Outage of the Zelienople circuit results in loss of 16.6 MW and 3,762 customers * Radial line exposure is 1.2 miles * Line has experienced 2 sustained outages in the past 5 years
ATSI-2018-008 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1795 |  |  | NLMK 69 kV Load At Risk * Reduce the amount of local load loss under contingency conditions. - Loss of Crossland-NLMK 138 kV line - Results in loss of approximately 58 MWs of load. Or - Masury 69 kV bus fault - Results in potential local voltage collapse of the Masury 69 kV area * Equipment Material Condition, Performance and Risk - NLMK 69 kV system cable trenches are deteriorated and in need of replacement - 69 kV breakers in need of replacement (bus-tie breaker has already failed) - NLMK 138/69 kV transformer # 6 and # 12 are aged (> 50 years) and not standard design. - Transformer #6 has elevated gas levels. - Existing 69 kV transmission line conductor around NLMK is corroded and deteriorated with multiple splice locations. - Need to upgrade to current standards
ATSI-2018-009 | ATSI | PJM West | 2018-09-28 | 2018-10-26 |  |  |  |  | Avon-Fowles 138 kV Q1 and Q3 Line Load at Risk * Reduce the amount of local load loss at risk and mitigate non-planning criteria voltage concerns on the > 100 kV system under contingency conditions. - Loss of Avon-Fowles Q1 138kV line (“B_LINE1_NR_006”) and path-end outage of the Avon-Fowles Q3 138 line. - Results in the potential loss of approximately 60 MWs and 14,000 customers. - Results in the potential low voltage (0.91 p.u.) at Dawson 138kV Substation Or - Common tower outage Avon-Fowles Q1 138kV line and the Avon-Fowles Q3 138 line (“C5-TWL-NR005”). - Results in the consequential load loss of approximately 237 MWs and 68,200 customers.
ATSI-2018-010 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-04-15 | s1760 |  |  | Ironville-Citgo 69 kV Condition Assessment (Approximately 4 miles) Line Condition Rebuild / Replacement * Identified obsolete and deteriorated equipment. - 60-68 year old construction; poor inspection results, 89 % rejection rate. - Approximately 2 repair records over the past 5 years. * Multiple transmission delivery points (3) impacted; back-up source to (4) transmission delivery points.
ATSI-2018-011 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1796 |  |  | Abbe-Medina 69 kV Condition Assessment (Approx. 30 miles) * Identified obsolete and deteriorated equipment. - 62 year old construction; poor inspection results. - Negative outage history over past 5 years. - Approximately 17 repair records over the past 5 years; increasing trend . * Multiple transmission delivery points (8) impacted. * Need to upgrade to current standards
ATSI-2018-012 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1797 |  |  | Wellington-Hanville-Steuben 69 kV Condition Assessment (Approx. 33 miles) * Identified obsolete and deteriorated equipment. - 50 to 56 year old construction; poor inspection results. - Negative outage history over past 5 years; - Previous radial line (now networked) with 5 distribution delivery points. - Approximately 13 repair records over the past 5 years; increasing trend. * Multiple transmission delivery points (5) impacted. * Need to upgrade to current standards
ATSI-2018-013 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1798 |  |  | Ravenna-West Ravenna #1 69 kV Condition Assessment (Approx. 4 miles) * Identified obsolete and deteriorated equipment. - 50 year old construction; poor inspection results, 94 % rejection rate. - Negative outage history over past 5 years; - Approximately 21 repair records over the past 5 years; increasing trend. * Need to upgrade to current standards
ATSI-2018-014 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1799 |  |  | Bingham-Cardington (Schaff) 69 kV Condition Assessment (Approx. 15 miles) * Identified obsolete and deteriorated equipment. - 45-62 year old construction; poor inspection results, 92 % rejection rate. - Negative outage history over past 5 years; - Approximately 10 repair records over the past 5 years; increasing trend. * Need to upgrade to current standards
ATSI-2018-015 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1800 |  |  | Bellevue-Carriage 69 kV Condition Assessment (Approximately 13 miles) * Identified obsolete and deteriorated equipment. - 48 year old construction; poor inspection results, 62 % rejection rate. - Negative outage history over past 5 years; - Approximately 9 repair records over the past 5 years; increasing trend. - Sections of older 3/0 CU conductor. * Multiple transmission delivery points (7) impacted. * Need to upgrade to current standards
ATSI-2018-016 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1801 |  |  | Hanna-Newton Falls 138 kV Condition Assessment (Approximately 20 miles) * Identified obsolete and deteriorated equipment. - 62 year old construction; poor inspection results, 87 % rejection rate. - Negative outage history over past 5 years; - Approximately 45 repair records over the past 5 years; increasing trend. * Need to upgrade to current standards
ATSI-2018-017 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1802 |  | Star-Seville (Rittman) 69 kV line | Star-Seville (Rittman) 69 kV Condition Assessment (Approximately 18 miles) * Identified obsolete and deteriorated equipment. - 56 year old construction; poor inspection results, 82 % rejection rate. - Negative outage history over past 5 years; - Approximately 30 repair records over the past 5 years; increasing trend. * Multiple transmission delivery points (3) impacted. * Radial 69 kV transmission line with approximately 30 MWs and approximately 7,700 customer at risk.
ATSI-2018-018 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1803 |  |  | Carlisle-Wellington 69 kV Condition Assessment (Approximately 29 miles) * Identified obsolete and deteriorated equipment. - 50-75 year old construction; poor inspection results, 75 % rejection rate. - Negative outage history over past 5 years; - Approximately 29 repair records over the past 5 years; increasing trend. * Multiple transmission delivery points (9) impacted.
ATSI-2018-019 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1804 |  |  | Maysville-Canal (Greenville) 69 kV Condition Assessment (Approximately 1.5 miles) * Identified obsolete and deteriorated equipment. - 61 year old construction; poor inspection results, 100 % rejection rate. - Approximately 4 repair records over the past 5 years. * Radial 69 kV transmission line with 16 MWs and approximately 6,800 customer at risk.
ATSI-2018-020 | ATSI | PJM West | 2018-09-28 | 2018-10-26 | 2019-06-12 | s1805 |  |  | Line Condition Rebuild / Replacement Assessment of existing transmission lines for equipment characteristics that are at, or beyond their existing service life, or contain components that are obsolete. * Aged or deteriorated wood pole transmission line structures. * Negatively impact customer outage frequency and/or durations. * Demonstrate an increasing trend in maintenance findings and/or costs
ATSI-2018-021 | ATSI | PJM West | 2018-11-29 | 2019-02-20 |  |  |  | Medina-Medina Industries 69 kV | New Customer Connection - A customer requested 69 kV service for load of approximately 10 MVA near the Medina-Medina industries 69 kV line.
ATSI-2018-022 | ATSI | PJM West | 2018-11-29 | 2018-11-29 |  |  |  | New 138 kV Customer | New Customer Connection - A customer requested 138 kV service for load of approximately 6 MVA near the Delta-Wauseon 138 kV line.
ATSI-2018-023 | ATSI | PJM West | 2018-11-29 | 2019-02-20 |  |  |  | Black River 138 kV | Black River 138 kV Area * Thermal constraints identified in previous Gen Queue and Gen Deliverability Studies. * Future year analysis shows potential thermal constraints. ―For the loss of the Avon-Beaver #1 345 kV Line and the Avon-Beaver #2 345 kV Line results in the Charleston-Lorain 138 kV Line loading to greater than 90%.
ATSI-2019-001 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Black River-Shinrock 69 kV | Black River-Shinrock 69 kV Line The Black River-Shinrock 69 kV line is approximately 24 miles long and serves five (5) transmission customers. The transmission line conductor is the limiting element. * A Black River-Shinrock 69 kV line outage (N-1) results in approximately 47 MW and 14,200 customers being interrupted. * Over the past five years, the Black River-Shinrock 69 kV line has experienced approximately 17 outages (9 sustained , 8 momentary).
ATSI-2019-002 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Brady 138 kV | Brady 138 kV Area PJM has issued PCLLRW to potentially drop 20 MW of load at Brady substation for the (N-1-1) outage of the Brady-Hanna 138 kV line and the Chamberlin-Hudson Muni 138kV line. * Post-contingency voltage at Brady drops below 0.92 p.u. under this back-feed condition from Darrow 138 / 69 kV substation. * The overall load at risk is approximately 61 MW, and the number of customers impacted is approximately 18,800.
ATSI-2019-003 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Lincoln Park Riverbed | Lincoln Park and Riverbend 138 kV Area Lincoln Park 138 - 23 kV substation presently serves approximately 35 MW and 5,000 customers * The loss of the Lincoln Park-Masury 138 kV line followed by the loss of the Lincoln ParkLowellville 138 kV line (N-1-1) results in the loss of approximately 35 MW and 5,000 customers. Riverbend 138 - 23 kV substation presently serves approximately 40 MW and 9,100 customers. Additionally the Wickliffe 138 kV substation serves approximately 22 MW and 10,000 customers. * The loss of the Boardman-Wickliffe 138 kV line followed by the loss of the Riverbend-Salt Springs 138 kV line (N-1-1) results in the loss of roughly 62 MW and 19,100 customers. System Performance * Over the past 5 years, the Lincoln Park-Masury 138 kV line has experienced 1 outage (0 sustained , 1 momentary). * Over the past 5 years, the Lincoln Park-Lowellville 138 kV line has experienced 4 outages (3 sustained , 1 momentary). * Over the past 5 years, the Boardman-Wickliffe 138 kV line has experienced 2 outages (2 sustained , 0 momentary). * Over the past 5 years, the Riverbend-Salt Springs 138 kV line has experienced 1 outage (1 sustained , 0 momentary).
ATSI-2019-004 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Amherst 69 kV | The Amherst 69 kV substation is owned by Amherst Municipality with transmission service from a tapped 69 kV transmission line. The Henrietta-Johnson 69 kV line outage (N-1) results in approximately 39 MW & 9,195 customers at three transmission service points being interrupted. * Over the past five years, the Henrietta-Johnson 69 kV line has experienced approximately 21 outages (13 sustained , 8 momentary).
ATSI-2019-005 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Tangy-Delaware 138 kV line | The Delaware - Tangy 138 kV Line is an ~1.0 mile tie line between FirstEnergy and AEP. The line is operated normally open and has not been closed since 2014. Failing pilot wire relays and phone line communications are near or beyond their expected service life or obsolete.
ATSI-2019-006 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Elm 69 kV | Elm 138 kV Area: The contingency loss of the Ivanhoe-Packard 138 kV line followed by the loss of the Niles-Niles Central Muni 138 kV line results in the loss of approximately 137 MW and 28,600 customers at six (6) transmission service points. * Over the past five years, the Ivanhoe-Packard 138 kV line has experienced approximately 2 outages (1 sustained , 1 momentary). * Over the past five years, the Niles-Niles Central Muni 138 kV line has experienced approximately 4 outages (1 sustained , 3 momentary).
ATSI-2019-007 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Jackman 138 kV | Jackman 138 / 69 kV Area The Jackman 69 kV substation is electrically isolated from the Jackman 138 kV substation; it is sourced from Dixie 69 kV substation. The contingency loss of the DixieJackman 69 kV line or a stuck breaker at Dixie substation results in the loss of approximately 43 MW and 19,000 customers at three transmission service points. * Over the past five years, the Dixie-Jackman 69 kV line has experienced approximately 1 outage (1 sustained , 0 momentary).
ATSI-2019-008 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Kimberly 69 kV | Kimberly 69 kV Area The Kimberly 69 kV substation is served from a 3.6 mile radial transmission line from Salt Springs 138 / 69 kV substation with 19 MW and 5, 500 customers at risk. Additionally, the contingency loss of the nearby Berlin Lake-Boardman 69 kV line results in the loss of approximately 46 MW and 12,500 customers at four (4) transmission service points.
ATSI-2019-009 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Maroe-Malinta 34.5 kV Area | Maroe-Malinta 34.5 kV Area * The existing Richland-Maroe 34.5kV line is a radial line with limited capability of transferring load onto different circuits for emergency restoration and scheduling of routine maintenance. * The loss of the Richland-Maroe 34.5 kV radial line results in the loss of approximately 8 MW and 2,550 customers at two (2) sub-transmission service points. * The existing Weston-Malinta 34.5 kV line is a radial line with limited capability of transferring load onto a different circuits for emergency restoration and scheduling of routine maintenance. * The loss of the Weston-Malinta 34.5 kV radial line results in the of approximately 6 MW and 1,000 customers at two (2) sub-transmission service points. * The 138 / 34.5 kV transformer #1 at Richland substation is greater than 70 years old and is showing signs of end of life; including oil leaks, failing components, and increasing maintenance. * The 69 / 34.5 kV transformer #3 at Westin substation is greater than 74 years old and is showing signs of end of life; including oil leaks and deteriorating components. * Customers taking sub-transmission service on these two radial lines have requested additional reliability and operational flexibility. - The 34.5kV radial lines cannot be networked due to insufficient short circuit current. - The Westin 69 / 34.5 kV transformer #3 (end of life) does not have the capacity to carry the entire load on a networked 34.5 kV system for a path end outage at Richland substation.
ATSI-2019-010 | ATSI | PJM West | 2019-01-11 |  |  |  |  | Valley Substation | Valley & Thiess 138 kV Substation Area The Valley and Thiess 138 kV substations are presently owned by Cuyahoga Falls Municipality with transmission service from the ATSI Babb-Chamberlin 138 kV line. * A transmission line outage of the double circuit networked 138 kV tap (approximately 1 mile) to Valley substation could result in approximately 86 MW and 25,000 Customers interrupted for an extended period of time. * The loss of the Chamberlin-Thiess 138 kV line, followed by the loss of the Babb-Valley 138 kV line (N-1-1) could result in approximately 106 MW and 25,000 customers interrupted for an extended period of time. Evans & Darrow 138 kV Substation Area * The loss of the Babb-Evans 138 kV line, followed by the loss of the East Akron-Evans 138 kV line (N-1-1) results in approximately 25 MW and 4,834 customers interrupted. * The loss of the Chamberlin-Hudson Muni 138 kV line, followed by the loss of the Brady-Hanna 138 kV line (N-1-1), results in approximately 61 MW and 18,800 customers interrupted. Post-contingency voltage drops below 0.92 p.u. in the Darrow substation area. * Over the past five years, - The Chamberlin-Theiss 138 kV line has experienced five (5) outages (3 sustained, 2 momentary) - The Theiss-Valley 138 kV line has experienced one (1) outage (1 sustained, 0 momentary) - The Chamberlin-Hudson Muni 138 kV line has experienced four (4) outages (2 sustained, 2 momentary) - The Babb-Evans 138 kV line has experienced one (1) outage (1 sustained, 0 momentary)
ATSI-2019-011 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Evergreen Sub | Evergreen Substation 138 kV Equipment and Protection * BES bus protection is presently performed by a complex scheme that has a history of causing misoperations at other substations. The scheme uses distributed electromechanical relays to exclude a bus fault rather than detecting the bus fault directly.
ATSI-2019-012 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Frisco Sub | Frisco Substation 69 kV Protection * Line protection at Frisco substation consists of a single relay protection scheme. A recent relay failure during a fault at a nearby substation led to delayed fault clearing and a larger number of customers affected than necessary. There is not backup relay schemes to reduce customer exposure to a similar single point of failure.
ATSI-2019-013 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Maple Sub | Maple Substation 69 kV Protection * Line protection at Maple substation consists of a single relay protection scheme. A recent relay failure during a fault at a nearby substation led to delayed fault clearing and a larger number of customers affected than necessary. There is not backup relay schemes to reduce customer exposure to a similar single point of failure.
ATSI-2019-014 | ATSI | PJM West | 2019-01-11 |  |  |  | 2019-01-11
ATSI-2019-015 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Ashtabula 138 kV | Ashtabula 138 kV Substation Equipment and Protection * Two (2) 138 kV breakers (B143 & B149), lightning arresters and associated switches, and control wiring are showing degrading performance, increasing maintenance, age (46-63 years), and obsolescence of equipment and spare parts
ATSI-2019-016 | ATSI | PJM West | 2019-01-11 |  |  |  |  | Chamberlin 138 kV | Chamberlin 138 kV Substation * Two (2) 138 kV Oil Circuit Breaker (OCB) breakers (B86 & B69) and MOAB Switch A19 at Chamberlin are showing degrading performance, increasing maintenance, age (> 30 years), and obsolescence of equipment and spare parts.
ATSI-2019-017 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  | 2019-05-08 | Fowles-NASA 138 kV | Fowles – NASA Q16 138 kV Terminal Equipment * One (1) 138 kV breaker at Fowles (Q16), associated switches, relays, and CCVTs are showing degrading performance, increasing maintenance, age (60 years), and obsolescence of equipment and spare parts.
ATSI-2019-019 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | West Akron 138 kV | West Akron 138 kV Substation One (1) 138 kV Oil Circuit Breaker (OCB) breaker (B1) at West Akron, lightning arresters and associated switches, and CCVTs are showing degrading performance, increasing maintenance, age (30 years), and obsolescence of equipment and spare parts.
ATSI-2019-020 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Cloverdale 69 kV | Cloverdale 69 kV Substation Assessment The electromechanical relays and communication equipment at the 69 kV Cloverdale substation have been identified to be prone to misoperation. The disconnect switches have operation difficulty and are greater than 40 years of age. The 69 kV Bus PTs are nearing end of life with increased risk of failure.
ATSI-2019-021 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Longview 69 kV | Longview 69 kV Substation Assessment * The electromechanical relays and communication equipment at the 69 kV Longview substation have been identified to be prone to misoperation. The disconnect switches have operation difficulty and the 69 kV Bus PTs are nearing end of life with increased risk of failure.
ATSI-2019-022 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Hoytdale Transformer | Hoytdale Substation Transformer Assessment * The existing 345 / 138 kV Hoytdale transformer #1 is showing end of service life issues; including oil leaks, moisture ingress, problematic cooling controls, unreliable gauges / annunciators, failing pumps and relays that are prone to misoperations.
ATSI-2019-023 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | New Castle 138 kV | New Castle 138 kV and 69 kV Substation Assessment * One (1) 138 kV OCB breaker (B166) and five (5) 69 kV OCB breakers (B32, B86, B90, B96 and B106) at New Castle are showing end of life characteristics; including deteriorated bushings, mechanism, oil leaks, and age (> 30 years) with increasing maintenance and obsolescence of equipment and spare parts. Associate
ATSI-2019-024 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Coulter-Longview 69 kV | Coulter-Longview 69 kV Line Assessment * The poles and associated hardware on this line have reached end of life with 90% of the poles greater than 60 years. * Maintenance and repairs are trending upward in frequency and severity. * Four Air Break switches are obsolete and no longer supported for parts. * Conductor (1/0 and 2/0 Copper) dates to original construction System Performance * Over the past 5 years, the Coulter-Longview 69 kV line has experienced 10 outages (6 sustained , 4 momentary)
ATSI-2019-025 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Brush Wellman - Ottawa 69 kV | Brush Wellman-Ottawa 69 kV Line Assessment * The poles and associated hardware on this line have reached end of life with 92% of the poles greater than 60 years. * Maintenance and repairs are trending upward in frequency and severity. * Four Air Break switches are obsolete and no longer supported for parts. System Performance * Over the past 5 years, the Brush Wellman-Ottawa 69 line has experienced 4 outages (3 sustained , 1 momentary).
ATSI-2019-026 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Allen Junction-Vulcan 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-027 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Avery 138 / 69 kV Substation | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-028 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Bayshore-GM Powertrain 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-029 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Bayshore-Jeep 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-030 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Blue Jacket-Kirby 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-031 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Carlisle-Gates 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-032 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Cedar Street-New Castle 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-033 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | East Akron-West Ravenna 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-034 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | GM Defiance-Richland #1 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-035 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | GM Defiance-Richland #2 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-036 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Greenfield-New Departure 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-037 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Hanna-West Ravenna 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-038 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Hoytdale-Maple 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-039 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Hyatt-Tangy 345 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-040 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Ivanhoe-Mahoningside 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-041 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Ivanhoe-Packard 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-042 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Jennings-LTV West Q-12 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-043 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Jennings-LTV West Q-14 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-044 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Kirby-Tangy 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-045 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Midway-Levis Park 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-046 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | Midway-Napoleon 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-047 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  | 2019-03-25 |  | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Circuit is limited by Line Relay, CT, Substation Conductor / Drops to (SN/SE) 223 / 223MVA. Conductor rating is (SN/SE) 278 / 339 MVA.
ATSI-2019-048 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  | 2019-03-25 |  | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Circuit is limited by Substation Conductor / Drops to (SN/SE) 221 / 262MVA. Conductor rating is (SN/SE) 233 / 282 MVA.
ATSI-2019-049 | ATSI | PJM West | 2019-01-11 | 2019-03-25 |  |  |  | West Akron-Babb 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment.
ATSI-2019-050 | ATSI | PJM West | 2019-02-07 | 2019-03-07 |  |  |  | Ashtabula 345 kV | Perry-Ashtabula-Erie West 345 kV Line and Surrounding Areas * Perry-Ashtabula-Erie West 345 kV Line is a three terminal line. * Three terminal lines are prone to mis-operations, lengthy fault locating analysis and longer restoration efforts. * Existing transmission relay communication equipment is approaching end of life, is obsolete, and is difficult to maintain and repair. * Non-planning criteria violation voltage concerns on the > 100 kV system under contingency conditions. - Loss of the Perry-Ashtabula-Erie West 345 kV (or the Ashtabula 345/138kV TR) followed by the loss of Leroy Center-Stacy Q3 138 kV line. OR - Loss of Leroy Center-Ashtabula Q4 138 kV line followed by the loss of the Leroy Center-Stacy Q3 138 kV line. Results in low voltage and potential local voltage collapse at Stacy substation; load shed of approximately 75 MWs is necessary to maintain system voltages.
ATSI-2019-051 | ATSI | PJM West | 2019-02-20 | 2019-04-23 |  |  |  | Pine-Warrendale 69 kV | Pine-Warrendale 69 kV Condition Assessment * Warrendale-Richard segment of the line (approximately 3.6 miles of the 6.42 mile line) has been identified as having obsolete and deteriorated equipment. - Damaged conductor identified along the line. - Construction is mostly 42 year old construction; poor inspection results. * Customers and load at risk: 6,135 customers and 22 MWs of load. * The Pine-Warrendale 69 kV line has experienced 4 outages in the past five years.
ATSI-2019-052 | ATSI | PJM West | 2019-02-20 | 2019-04-23 |  |  |  | Bingham - Galion 69 kV Line | New Customer Connection - A customer requested 69 kV service for a load of approximately 1.3 MVA near the Bingham - Galion 69 kV Line.
ATSI-2019-053 | ATSI | PJM West | 2019-03-25 | 2019-05-20 |  |  |  | Chamberlin - Treat 69 kV line | Chamberlin- Treat 69 kV Line (Radial) * The Chamberlin-Treat 69 kV line (approximately 13.4 miles) is a radial line. * Customers and load at risk: Approximately 9,400 customers and 37 MWs of load. * Limited operational flexibility to maintain service under transmission maintenance and restoration efforts. * The Chamberlin-Treat 69 kV line has experienced four outages in the past five years.
ATSI-2019-054 | ATSI | PJM West | 2019-03-25 | 2019-05-20 |  |  |  | Ottawa-West Fremont No.2 138 kV line | Ottawa-West Fremont #2 138 kV Equipment and Tap Connection * The existing KPF switches A-13135 and A-13136 are obsolete and no longer supported by the manufacturer. The existing customer tap connection (tapped between switch A-13135 and switch A-13136) on the Ottawa-West Fremont #2 138 kV line requires a 270 degree turn and crosses under both the Ottawa-West Fremont #1 and Ottawa-West Fremont #2 138 kV lines which creates operational maintenance constraints.
BE-2019-0001 | BE | PJM MA | 2019-01-25 | 2019-03-25 |  |  |  |  | New distribution customer load on the Port Covington peninsula
BE-2019-0002 | BE | PJM MA | 2019-03-25 | [5 empty] | Westport to Center 115 kV underground transmission line requires relocation to support external customer work. The cables have also been identified for replacement for various issues including movement of splices, corrosion of parts, gassing, availability of spare materials and specialized resources.
COMED-2018-001 | COMED | PJM West | 2018-10-26 | 2019-01-11 | 2019-06-26 | S1828 |  |  | * New customer has requested transmission interconnection in the DeKalb area * 18MW * Customer has large motors
COMED-2018-002 | COMED | PJM West | 2018-10-26 | 2019-01-11 | 2019-06-26 | S1829 |  |  | Electromechnical relays on 138kV lines 13505 and 13506 at Elmhurst: * Thermally limiting the line * Does not allows real time data gathering of relay events * Replacements and spare parts are becoming scarce
COMED-2018-003 | COMED | PJM West | 2018-10-26 | 2019-01-11 | 2019-06-26 | S1830 |  |  | Devon TR72 needs to be replaced due to material condition * Transformer has internal arcing * Transformer is gassing * LTC headboard is cracking and leaking oil * Increasing maintenance costs The failure of TR72 causes the outage of 138kV line 8809
COMED-2019-001 | COMED | PJM West | 2019-02-20 | 2019-03-25 | 2019-04-15 | s1793 |  |  | Support of the DHS sponsored Resilient Electric Grid (REG) initiative with a new technical pilot project involving superconducting cable.
COMED-2019-002 | COMED | PJM West | 2019-03-25 | 2019-04-23 | 2019-09-03 | s1868 |  | Braidwood 345 kV Bus Tie 11-14 | * Station 20 Braidwood 345kV bus tie 11-14 * Replacement parts are difficult to acquire * Bushings are at end of life * Manufactured in 1978
COMED-2019-003 | COMED | PJM West | 2019-03-25 | 2019-07-24 |  |  |  | New Customer in Bradley Area | * New customer has requested new 138kV service in the Bradley area * 11MW in 2021, up to 45 MW by 2024
COMED-2019-004 | COMED | PJM West | 2019-03-25 | 2019-04-23 | 2019-09-03 | s1869 |  | Devon 138/12 kV station: Install 4th Transformer | * Distribution has asked for an additional 12kV transformer connection at Devon
COMED-2019-005 | COMED | PJM West | 2019-03-25 | 2019-04-23 | 2019-09-03 | s1870 |  | Des Plaines - Tonne Three Terminal line (4605) | * 138 kV line 4605 is a three-terminal line * TSS 46 Des Plaines * TSS 198 Des Plaines * TDC 207 Tonne (future Elk Grove) * Elk Grove project B2941 will cut into the line * The current configuration is very difficult to relay properly due to unequal lengths of the three legs
Dayton-2019-002 | Dayton | PJM West | 2019-02-20 | 2019-04-23 | 2019-09-05 | s1874 |  | Gebhardt Distribution Sub | - Significant load growth in the area east of I-75 and south of I-675 - Distribution Circuit RH1211 served from Yankee Substation exceeded its thermal rating this past summer and RH1204 from Yankee Substation is approaching its rated capacity. There are no ties in the vicinity of the load center with sufficient capacity to serve growing loads. - DP&L must develop a solution immediately to have capacity to serve distribution load in this load center or risk overloading existing equipment and not having sufficient distribution capacity to serve growing load. There is a need for a new distribution source closer to the load center. - DP&L must offload the Yankee and Normandy circuits to ensure sufficient capacity to serve growing load centers in Centerville and Waynesville.
Dayton-2019-003 | Dayton | PJM West | 2019-02-20 | 2019-04-23 | 2019-09-05 | s1875 |  | Urbana, Ohio | - The loads at the existing Urbana Substation have grown beyond the capacity of the existing distribution transformers and DP&L has utilized a mobile transformer at the Urbana substation to take load off of the distribution banks that would otherwise be pushed beyond their thermal limits. - The existing Urbana and Kingscreek substations are not centrally located to the growing load center which makes load transfers to and from either sub nearly impossible. - Distribution 12.47KV circuits DB1205 and DB1206 from Urbana Substation both reached their peak circuit capacities this past summer. - There is a need for a new distribution source closer to the load center to provide loading relief on the Urbana Substation transformers and circuits.
Dayton-2019-004 | Dayton | PJM West | 2019-02-20 | 2019-04-23 | 2019-09-05 | s1876 |  | South Dayton Metro | - The Dayton 138kV system regularly experiences real-time loading issues on the Hutching-Sugarcreek 138kV 13805 line during peak and shoulder peak times. Dayton System Operations works with PJM and frequently switches the Crown 138/69kV transformer out of service to avoid a PCLLRW but in some instances, this is not a possibility. Also, this switching and segmentation of the system is not a good practice for the equipment and reliability of the system. Dayton has a plan to help solve this issue by installing a 138/69kV transformer at Normandy Substation but we have concerns this could shift the operational loading issues from the Sugarcreek-Hutchings 138kV line to the Sugarcreek to Normandy 138kV line with the growth in this area. Also, Normandy Substation has space limitations for a 138kV transformer. If this issue is not addressed immediately, it could lead to more real-time issues and further degradation to the equipment that is switched out in this quickly growing load center. - In addition to the 138kV loading issues in this area, this growing load center is served by three 69kV sources with limited capacity and a performance issue. These factors make performing regular maintenance more difficult and puts the reliability of the system at risk. In the event of a single outage (planned for maintenance or unplanned due to system events) to one of the three sources, a subsequent 69kV outage would lead to severe reliability implications including loadings in excess of the emergency line ratings. The 6610 Yankee-Caesars-Trebein 69kV line is one of the three 69kV lines supplying the load center and it is a 31 mile line, three terminal line constructed in 1950 with wood poles that has experienced 7 permanent and 16 momentary outages the past 5 years.
Dayton-2019-005 | Dayton | PJM West | 2019-02-20 | [5 empty] | - Existing distribution 12.47KV circuits AZ1210 and AZ1205 from Vandalia Substation exceeded their thermal rating this past summer. There continues to be strong load growth in this area with multiple transmission and distribution customer requests. - Distribution circuits that supply the growing load center emanate from distant substations and end-use customers are beginning to see voltage issues. Specifically this has been an issue on distribution circuit OC1204 from West Milton. - There are critical customers served in this area and there is a need to supply sufficient capacity and diversity to ensure continued reliable operations amid the rapid load growth.
Dayton-2019-006 | Dayton | PJM West | 2019-02-20 | 2019-03-25 | 2019-08-15 | s1846 |  | Replace the existing Greenville 138/69kV transformer | - Greenville 138/69kV transformer was built in 1978 - Failed, repaired, and placed back in-service in 2009 - In the summer of 2018, this transformer experienced issues evidenced by rising transformer temperatures, generation had to be called on to relieve the loading constraint on several occasions. - This transformer is undersized and routinely approaches its nameplate ratings as evidenced by frequent PCLLRW’s issued on this facility. Due to the operational issues this past summer and regular loading near nameplate capacity, this transformer could fail or not be available during peak load conditions which potentially creates real-time issues. It is critical for real-time operations that this transformer issue be addressed in a planned manner to ensure reliability of the 138kV and 69kV system in this area. -The existing Greenville 138/69kV transformers is the only 150MVA transformer on the Dayton system, the standard 138/69kV transformer size is 200MVA. The extra capacity provided by a 200MVA transformer is needed in this area to account for the wide range of loading scenarios depending on the status of Greenville Generation.
Dayton-2019-007 | Dayton | PJM West | 2019-02-20 | 2019-03-25 | 2019-08-15 | s1847 |  | Tap new customer off Miami-New Carlisle 138kV line | - Customer requested a new delivery point in Miami County, Ohio, within Bethel Township. - Initial loading projected at ~5-7MW, with expected annual growth of 1.2%
Dayton-2019-008 | Dayton | PJM West | 2019-04-11 | 2019-06-13 | 2019-09-05 | s1877 |  | Killen Substation | * Killen generators retired 6/1/18 and the capacity injection rights expire 6/1/19. * After CIRs expire, Killen Substation will serve no purpose since there will be no generation or load serving facilities located at the substation. There is a dead-section of 345kV line that could be utilized to bypass the Killen Substation. * Point M and Point O serve as demarcation points between AEP and Dayton on the line and points where the Killen 345kV loop could be opened. * The 345kV line that loops in an out of the substation, along with the substation equipment will add exposure to the system that could decrease the reliability of the 345kV path between Stuart and Marquis Substations.
DEOK-2018-001 | DEOK | PJM West | 2018-11-29 | 2019-01-11 | 2019-06-26 | s1782 |  |  | Amazon Prime Air has requested distribution service (13kV) for a new air hub to be located at the Cincinnati/Northern Kentucky International Airport. Initial demand is projected to be 30 MW with phased growth to 80 MW.
DEOK-2018-002 | DEOK | PJM West | 2018-11-29 | 2019-01-11 | 2019-06-26 | s1783 |  |  | Large industrial customer (200+ MW) is supplied by two 138 kV circuits. Planned maintenance work on each circuit will require extended outages. The customer is at risk of complete interruption if the remaining circuit experiences an outage. Customer advises that complete interruption would have grave consequences on customer’s processes potentially leading to ceasing operations (closure of plant). Customer also advises that a minimum of 75MWs is required for a safe shutdown of equipment.
DEOK-2018-003 | DEOK | PJM West | 2018-11-29 | [5 empty] | New and existing industrial load growth in the area west of the Cincinnati/Northern Kentucky International Airport is predicted to exceed the capacity of the local distribution system. An additional 40MWs is requested.
DEOK-2019-001 | DEOK | PJM West | 2019-02-20 | [5 empty] | The distribution system feeding this area from Hebron and Limaburg is nearing its capacity limit. 70-90 MVA of load growth is expected in this area over the next five years. Duke Energy Distribution has requested a new transmission to distribution substation in the Petersburg, KY area.
DEOK-2019-002 | DEOK | PJM West | 2019-02-20 | 2019-04-23 |  |  |  | Beckjord | Beckjord 138kV buses 3 and 4 are 66 years old, are constructed of copper bus with cap and pin insulators, and in deteriorating condition. The breakers on these busses are oil filled and obsolete. Rebar is showing though the deteriorating structural and equipment foundations.
DEOK-2019-003 | DEOK | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | Technical Services continues to have problems with the mechanisms on three 345kV breakers at Foster. The manufacturer no longer makes the mechanism for these 1990 vintage breakers. The breakers also have an on-going problem leaking SF6 gas.
DEOK-2019-004 | DEOK | PJM West | 2019-03-25 | [5 empty] | The painted lattice tower that supports the Miami Fort – Clifty Creek 138kV line has deep rust exhibiting heavy pack-out including deformed members and missing bolts. Concrete foundations are spalling causing exposure of reinforcing steel resulting in the delamination of concrete. Anchor bolts are rusting and as a result are showing significant section loss causing a reduction in tensile strength. Subsequent to this 86 year old tower’s installation adjacent to Miami Fort generation station a fly ash pond was built near it. The tower now sits in/on the dike between the fly ash pond and the Ohio River. The owner of the fly ash pond considers this high risk and has asked that the tower be moved off the dike. The condition of the tower combined with its use is also a risk. This tower is one side of the Ohio River crossing.
DEOK-2019-005 | DEOK | PJM West | 2019-03-25 | [5 empty] | Duke Energy Distribution has requested a new delivery point at Aicholtz substation. The two 69/13kV 10.5MVA transformers at Aicholtz are currently loaded to 86%. There are plans for new subdivisions and a new Medical Center in this area. Distribution Planning projects the transformers at Aicholtz will be loaded to 95% by 2020. Subsequent commercial development is expected.
DEOK-2019-006 | DEOK | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Maineville substation. Loading on the single 138/13kV 22MVA transformer at Maineville has reached its nameplate rating.
DEOK-2019-007 | DEOK | PJM West | 2019-03-25 |  |  |  |  | Dry Ridge 69/13 kV Station | Duke Energy Distribution has requested a new delivery point at Dry Ridge substation. Dry Ridge has one 69/13kV 10.5MVA transformer. Grant substation has two 69/13kV 10.5MVA transformers. Due to loading at Dry Ridge and Grant (60% at Dry Ridge, 33% and 36% at Grant), Grant can no longer be tied out to Dry Ridge.
DEOK-2019-008 | DEOK | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Hamlet substation. Winter loading on the single 69/13kV 10.5MVA transformer at Hamlet has reached 96% of its nameplate rating. New residential subdivisions in this area are planned to be completed by 2021. Winter loading is expected to increase 10% since gas service in much of this area is not available.
DEOK-2019-009 | DEOK | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Allen substation. Loading on Allen’s single 69/13kV 22MVA transformer has reached the nameplate rating.
DEOK-2019-010 | DEOK | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Duke Energy Distribution has requested a new delivery point in the Mason Ohio area. New light industrial load growth requires 7MW of service by 2021 with and additional 15MW expected by 2022.
DEOK-2019-011 | DEOK | PJM West | 2019-03-25 | 2019-05-20 |  |  |  |  | Warren 138/69kV 100MVA TB1 showed a sharp increase in gassing in 2016. Over the past thee years the gas levels continue to increase. The main gasses of concern are ethane and ethylene, indicating a potential deterioration of insulation. Indications are trending towards a possible failure. There has also been an increase in power factor during routine testing indicating the transformer trending towards the end of its useful life. This 62 year old transformer is FOA rated. The capacity of the original cooling equipment has degraded with age. In the event of a failure, it would take an extended amount of time to replace this transformer with a spare (3-4 months). It would require foundation modifications, physical bus modifications, new conduits and control cables. This transformer supplies 69kV service to The City of Lebanon Electric Department.
DEOK-2019-012 | DEOK | PJM West | 2019-04-23 | 2019-05-20 |  |  |  | Trenton | An existing distribution customer is consolidating manufacturing to a facility served from Trenton substation. An additional 5 MW of service is required by 01-01-2021. There are two distribution 138/34 kV transformers at Trenton. A 22.4 MVA experiencing loads near 20 MVA and a 14.5 MVA seeing loads at 15 MVA.
DEOK-2019-013 | DEOK | PJM West | 2019-04-23 | 2019-05-20 |  |  |  | Mosteller | An automotive manufacturer in Sharonville, Ohio is currently supplied via a tap that extends from the 69kV Evendale - Port Union feeder. This tap is also the source for an adjacent Industrial plant. The Evendale - Port Union feeder is also a source for a distribution transformer at Port Union, which supplies commercial and industrial load in the vicinity of Port Union. The circuit has 7.7 miles of line exposure in a heavily commercialized and industrial area. The primary source for the automotive customer’s substation is the Evendale - Port Union feeder. The substation is also connected normally open to an alternate source from the Allen - Wyscarver feeder. There is an auto throw-over (ATO) scheme to transfer to the alternate source via air break switches. Faults on the primary source lead to momentary outages and outages up to 40 seconds if the primary source fault is permanent and restoration is accomplished via the ATO. This causes significant disruption to their operations. During heavy load or abnormal system conditions, the ATO to the alternate source must be disabled. Under such circumstances, an outage of the primary source would result in an extended outage to the automotive plant . The customer has advised that just a momentary outage causes major disruption to the plant’s production from which it takes up to 24 hours to recover. The disruptions have a ripple effect throughout their national production chain impacting other plants around the county. The adjacent industrial plant is also interrupted for events on the primary feeder. No ATO is available to restore service. Restoration must be performed by manual inspection to determine the problem and repair, and the operation of pole mounted switches to sectionalize the circuit. Any problem in the automotive customer’s substation results in the interruption of the Evendale - Port Union path. Disrupting supply to the adjacent industrial customer and to the distribution transformer that serves commercial and industrial load near Port Union. Any work in the automotive customer’s substation must be coordinated, resulting in operational constraints.
DEOK-2019-014 | DEOK | PJM West | 2019-05-20 | 2019-06-17 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Verona substation. Verona’s single 69/13kV 10.5MVA transformer is seeing loads at 9 MVA. An additional 5 MW of commercial and industrial load is expected in 2020.
DEOK-2019-015 | DEOK | PJM West | 2019-05-20 | 2019-06-17 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Longbranch substation. Loading on the single 138/13kV 22MVA transformer has reached the nameplate rating. Commercial and residential development continues in this area. Load growth has been trending at 7% per year.
DEOK-2019-016 | DEOK | PJM West | 2019-05-20 | 2019-06-17 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Amanda substation. Amanda has a single 69/4kV 2.5MVA transformer. A new commercial customer requires 4MW of service by 12-31-2020.
DEOK-2019-017 | DEOK | PJM West | 2019-05-20 | 2019-06-17 |  |  |  |  | Duke Energy Distribution has requested a new delivery point at Trade Port substation. An existing customer is renovating its operation and requires 5.5MW of additional service by 12-31-2020. Trade Port’s single 69/13kV 10.5MVA transformer is seeing loads at 6.5MVA.
DEOK-2019-018 | DEOK | PJM West | 2019-05-20 |  |  |  |  | Oakley 69/34 kV Station | Line inspection found a clearance between a distribution feeder and a transmission tower. Duke Energy Distribution is moving loads to others feeders in the area, and retiring the feeder. This feeder was the only load on Oakley 69/34kV 27MVA TB5. Oakley TB5 is 69 years old, is one of the last few of it’s design on the system.
DEOK-2019-019 | DEOK | PJM West | 2019-06-17 | 2019-07-24 |  |  |  | Port Union - Foster | Nine 138/13kV 22.4MVA transformers are located at four substations in a highly developed commercial and residential area along the feeder from Port Union to Foster (two each at Dimmick, Socialville, Twenty Mile, three at Simpson). Only the feeder terminals at Port Union and Foster are breaker connected. Any disruption to this 12 mile long feeder results in a 150MW load loss. During heavy load periods an automatic restoration scheme at Montgomery must be disabled to eliminate potential overloads.
DEOK-2019-020 | DEOK | PJM West | 2019-07-24 |  |  |  |  | Locust - Fairfield | Buckeye Power, on behalf of Butler Rural Electric Cooperative, has requested Duke Energy review options for improving the reliability of the 34 mile long, 69 kV circuit from Fairfield to Locust substations. The six BREC delivery points connected to the circuit serve 5,135 customers and experienced 7,015,437 customer minutes of interruption (CMI) in the 2009-2019 YTD period [data provided by Buckeye Power]. Duke Energy’s Stillwell and River Circle substations serve 3,130 customers and experienced 4,596,672 CMI in the 2009-2019 YTD period.
DEOK-2019-021 | DEOK | PJM West | 2019-08-29 |  |  |  |  | Beckjord 138 kV Station | Beckjord 138kV buses 5 and 6 are in deteriorating condition. Constructed with copper bus and with cap and pin insulators, they were put in service in 1962. Structural steel is rusting. Rebar is showing though the structural and equipment foundations. Three breakers are connect to each bus. These breakers are oil filled and obsolete. The installation dates for these breakers are: 1975, 1991, 1973, 1991, 1969, and 1973.
DEOK-2019-022 | DEOK | PJM West | 2019-08-29 |  |  |  |  | Beckjord 138 kV Station | Beckjord 138kV buses 1 and 2 are in deteriorating condition. Constructed with copper bus and with cap and pin insulators, they were put in service in 1952. Structural steel is rusting. Rebar is showing though the deteriorating structural and equipment foundations. Three breakers are connected at each bus. One, installed in 2004, uses SF6 gas. The four others are oil filled, obsolete and were installed in 1973.
DOM-2018-001 | DOM | PJM South | 2018-09-13 | 2018-10-11 | 2019-07-25 | s1750 |  | Evergreen Mills 230 kV Delivery | DEV Distribution has submitted a request to serve a new datacenter campus in Loudoun County with total load in excess of 100MW. Customer requests service by 9/1/2020. DEV Distribution does not have adequate distribution facilities to serve this customer load request.
DOM-2018-002 | DOM | PJM South | 2018-09-13 | 2018-10-11 |  | s1751 |  | Summit 230 kV Delivery | ODEC has submitted a delivery point request south of Fredericksburg to serve 10 year projected residential, commercial and industrial growth totaling over 30 MW. Customer requests service by 8/1/2019. ODEC does not have adequate distribution facilities to serve this customer load request.
DOM-2018-004 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1832 |  | Opal 230 kV Delivery | DEV Distribution has submitted a DP Request for a new substation (Opal) to accommodate two proposed datacenters in the Remington area and general load growth in the Rt. 17/Rt. 29 intersection area. The new substation will have an ultimate projected load less than 100 MVA. Requested in-service date is 07/15/2021.
DOM-2018-005 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1833 |  | Add 2nd TX – Cannon Branch 230 kV Delivery - DEV | DEV Distribution has submitted a DP Request to add a 2nd distribution transformer at Cannon Branch Substation in Prince William County. This transformer will support datacenter load growth in the area. Requested in-service date is 11/15/2019.
DOM-2018-006 | DOM | PJM South | 2018-09-13 | 2018-12-13 | 2019-07-25 | s1834 |  | Gant 230 kV Delivery - NOVEC | NOVEC has submitted a DP Request for a new substation (Gant) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100 MW. Requested in-service date is 11/01/2019.
DOM-2018-007 | DOM | PJM South | 2018-09-13 | 2018-12-13 | 2019-07-25 | s1835 |  | Innovation 230 kV Delivery - NOVEC | NOVEC has submitted a DP Request for a new substation (Innovation) to accommodate a new datacenter campus in Prince William County with a total load in excess of 100 MW. Requested in-service date is 08/15/2019.
DOM-2018-008 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1836 |  | Cumulus 230 kV Delivery - DEV | DEV Distribution has submitted a DP Request for a new substation (Cumulus) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100 MW. Requested in-service date is 10/15/2019.
DOM-2018-009 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1837 |  | Add 2nd TX – Davis Drive 230 kV Delivery - DEV | DEV Distribution has submitted a DP Request to add a 2nd distribution transformer at Davis Drive Substation in Loudoun County. The station loading is projected to exceed 100 MW by 2020. Requested in-service date is 11/15/2019.
DOM-2018-010 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1845 |  | Add 2nd TX – Shellhorn 230 kV Delivery - DEV | DEV Distribution has submitted a DP Request to add a 2nd distribution transformer at Shellhorn Substation in Loudoun County. The new transformer is being driven by projections that normal load on the existing Shellhorn transformer will exceed 84 MVA in 2020. Requested in-service date is 03/31/2020.
DOM-2018-011 | DOM | PJM South | 2018-09-13 | 2019-05-16 |  |  |  | Nimbus | DEV Distribution has submitted a DP Request for a new substation (Nimbus) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100 MW. Requested in-service date is 11/15/2022.
DOM-2018-012 | DOM | PJM South | 2018-09-13 | 2018-11-08 |  |  |  | Add 5TH TX – Beaumeade 230 kV Delivery - DEV | DEV Distribution has submitted a DP Request to add a 5th distribution transformer at Beaumeade Substation in Loudoun County. The new transformer is being driven by projections that normal load at Beaumeade will be near 255 MW in 2020. Requested in-service date is 03/31/2020.
DOM-2018-013 | DOM | PJM South | 2018-09-13 | 2019-05-16 |  |  |  | DTC | DEV Distribution has submitted a DP Request for a new substation (DTC) to accommodate a new datacenter campus in Loudoun County with a total load in excess of 100 MW. Requested in-service date is 11/15/2021.
DOM-2018-015 | DOM | PJM South | 2018-09-13 | 2018-11-08 | 2019-07-25 | s1839 |  | Midlothian | DEV Distribution has identified the need to install a third distribution transformer at Midlothian substation. The station load growth will call for a mobile transformer for a transformer contingency by winter 2020. By winter 2022 the transformer contingency will result in unserved load greater than the capacity of the mobile transformer. Requested in-service date is 11/15/2019.
DOM-2018-016 | DOM | PJM South | 2018-11-29 | 2019-01-17 | 2019-07-25 | s1840 |  | Remington | DEV Distribution has submitted a DP Request to replace their existing transmission to distribution transformer at Remington Substation in Fauquier County with a higher capacity bank to meet customer load. Requested in-service date is 11/15/2019.
DOM-2018-017 | DOM | PJM South | 2018-10-11 |  |  |  |  | Kingsboro | DENC Distribution has submitted a request for a new substation (Kingsboro) to serve two new customers located in Edgecombe County, North Carolina. DENC Distribution does not have distribution facilities in the area to serve this customer load request. The two customers request service, one by 7/1/2019 and the other by 1/15/2020.
DOM-2018-018 | DOM | PJM South | 2018-10-11 | 2019-01-10 | 2019-07-25 | s1841 |  | Lucky Hill | DEV Distribution has submitted a request for a new substation (Lucky Hill) to accommodate a new datacenter campus in Fauquier County with a total load in excess of 100 MW. Requested in-service date is Sept 15, 2020.
DOM-2018-019 | DOM | PJM South | 2018-10-11 | 2018-12-13 | 2019-07-25 | s1842 |  | Sandlot 230 kV Delivery - DEV | DEV has submitted a DP Request for a new substation (Sandlot) to accommodate the expansion of a manufacturing plant in the City of Manassas with a total load in excess of 100 MW. Requested in-service date is 10/15/2019.
DOM-2018-020 | DOM | PJM South | 2018-12-13 | 2019-04-11 |  |  |  | Genito | DEV Distribution has submitted a DP Request for a new substation (Genito). DEV has received load requests in Chesterfield County with a total load of 36MVA. One development request is in the area of Genito Place, west of Hwy 288 and north of Genito Road, another request is also in the close proximity. All existing substations are remote from the new developments and do not have adequate capacity. Requested in-service date is 05/15/2020.
DOM-2018-022 | DOM | PJM South | 2018-12-13 | 2019-03-07 |  |  |  | BECO | DEV Distribution has submitted a DP Request to add a 4th distribution transformer at BECO Substation in Loudoun County. The new transformer is being driven by data center growth and projections of normal summer load at BECO near 226 MW in 2020. Requested in-service date is 05/16/2020.
DOM-2018-023 | DOM | PJM South | 2018-12-13 | 2019-02-07 | 2019-07-25 | s1843 |  | Greenwich | DEV Distribution has identified the need to install a second distribution transformer at Greenwich substation. The station load growth has caused a transformer contingency to exceed the capacity of field switching plus a mobile transformer. Requested in-service date is 10/15/2019.
DOM-2018-024 | DOM | PJM South | 2019-01-10 | 2019-03-07 |  |  |  | Buttermilk | DEV Distribution has submitted a DP request to serve a new substation (Buttermilk) in Loudoun County with total load in excess of 100MW. Customer requests service by 12/30/2020.
DOM-2019-001 | DOM | PJM South | 2019-01-17 | 2019-02-20 | 2019-07-25 | s1844 |  | Copeland | ODEC has submitted a request on behalf of Community EC (COMM) for a new Delivery Point (Copeland) at Suffolk, VA, to support future load growth in the area. The customer requests service by May 1, 2019.
DOM-2019-002 | DOM | PJM South | 2019-02-07 | 2019-04-11 |  |  |  | Winterpock | DEV Distribution has submitted a DP request to add a 3rd distribution transformer at Winterpock Substation. The station load growth has caused a transformer contingency to exceed the capacity of field switching plus a mobile transformer. Requested in-service date is 09/15/2020.
DOM-2019-003 | DOM | PJM South | 2019-02-07 | 2019-04-11 |  |  |  | Rockville | DEV Distribution has submitted a DP request to add a second distribution transformer at Rockville Substation in Goochland County This transformer will support residential and commercial load growth in the area. Requested in-service date is 06/15/2020.
DOM-2019-004 | DOM | PJM South | 2019-02-07 | 2019-05-16 |  |  |  | Cumulus 2nd TX | DEV Distribution has submitted a DP Request to add a 2nd, 84 MVA distribution transformer at Cumulus Substation in Loudoun County. The new transformer is being driven by projections that load on the initial Cumulus transformer will exceed mobile transformer capability in 2020. Requested in-service date is 10/15/2020.
DOM-2019-005 | DOM | PJM South | 2019-02-07 | 2019-08-08 |  |  |  | Lockridge | DEV Distribution has submitted a DP Request for a new substation (Lockridge) to support a new datacenter campus in Loudoun County with a total load in excess of 100 MW. The new station will also support existing data center load in the immediate area. Requested in-service date is 7/31/2022. Date changed from 09/30/2021 as previously presented.
DOM-2019-006 | DOM | PJM South | 2019-02-07 | 2019-05-16 |  |  |  | Pacific 3rd TX | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Pacific Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing two transformers. Requested in-service date is 04/01/2020.
DOM-2019-007 | DOM | PJM South | 2019-02-07 | 2019-05-16 |  |  |  | Perimeter | NOVEC has submitted a DP Request for a new substation (Perimeter) to support a new datacenter campus in Loudoun County with a total load less than 100 MW; however NOVEC is developing a proposal for a second data center adjacent to Perimeter that will drive the projected load above 100 MW. Requested in-service date is 12/01/2020.
DOM-2019-008 | DOM | PJM South | 2019-02-07 | 2019-05-16 |  |  |  | Global Plaza | DEV Distribution has submitted a DP Request for a new substation (Global Plaza – formerly Relocation Road) to support a new datacenter campus in Loudoun County with a total load in excess of 100 MW. The new station will also support existing data center load in the immediate area. Requested in-service date is 12/15/2021 (previously 11/15/2021).
DOM-2019-009 | DOM | PJM South | 2019-02-20 | 2019-03-28 |  |  |  | Clifton Forge 138/13.2 kV station 2nd transformer | DEV Distribution has submitted a DP Request to add a second 138/13.2 kV distribution transformer at Clifton Forge Substation in Alleghany county. This transformer will support residential and commercial load growth. Requested in-service date is 06/15/2019.
DOM-2019-011 | DOM | PJM South | 2019-03-07 | 2019-05-16 |  |  |  | Paragon Park | DEV Distribution has submitted a DP Request for a new substation (Paragon Park) to support a new datacenter campus in Loudoun County with a total load in excess of 100 MW. The new station will also support existing data center load in the immediate area. Requested in-service date is 04/01/2021.
DOM-2019-012 | DOM | PJM South | 2019-03-07 | 2019-05-16 | 2019-08-21 | s1838 |  | Poland Road 3rd TX | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Poland Road Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the existing two transformers. Requested in-service date is 10/15/2020.
DOM-2019-013 | DOM | PJM South | 2019-02-20 | 2019-08-27 |  |  |  | Burkeville (Flat Creek) | DEV Distribution has submitted a DP Request for new Flat Creek Substation (initially presented 02/20/2019 as Burkeville) to support commercial and industrial load growth in Nottoway County. Requested in-service date is 09/15/2020.
DOM-2019-014 | DOM | PJM South | 2019-03-07 | 2019-04-11 |  |  |  | Chesterfield Tx#9 | Chesterfield Tx#9 is a 224MVA 230/115kV transformer originally manufactured by North American in 1990. This transformer is being identified for replacement based on the results of Dominion’s transformer health assessment (THA) process. Detailed drivers are: * Age * Reduced BIL ratings (1 level) * Transformers previously manufactured by Federal Pacific/North * American are considered highly suspect due to previous transformer failures * THA score less than 80
DOM-2019-016 | DOM | PJM South | 2019-03-07 | 2019-04-11 |  |  |  | Peninsula, VA | Equipment Condition: * Peninsula Tx#4 is a 224MVA 230/115kV transformer. This transformer is being identified for replacement based on the results of Dominion's transformer health assessment (THA) process.Â Detailed drivers are: â€“ Age â€“ Reduced BIL ratings (1 level) â€“ THA score less than 80 Operational Flexibility: * Peninsula 230/115kV network Tx, a distribution 230/34.5kV Tx, 230kV Line #288 (Peninsula to Yorktown), and Line #2004 (Peninsula to Shellbank) all share a single 230kV tie breaker. Fault on Line #288 trip both transformers, and fault on either transformer trip Line #288 and interrupt network flow. Breaker Failure contingency result in loss of all the 230kV at Peninsula and the two 230kV lines.
DOM-2019-017 | DOM | PJM South | 2019-04-11 | 2019-05-16 |  |  |  | Northampton Substation | DEV Distribution has submitted a DP request to add a second distribution transformer at Northampton Substation in Northampton County, NC. This transformer will support commercial load growth and contingency loading for the loss of the existing transformer. Requested in-service date is 09/01/2020. Initial In-Service: Summer: 26.2 MW Load Projected 2024 Load: Summer: 27.8 MW
DOM-2019-018 | DOM | PJM South | 2019-03-28 | 2019-04-23 |  |  |  | Virginia Beach Substation | DEV Distribution has identified the need to replace an existing 115/34.5kV distribution transformer at Virginia Beach substation. Currently there is no high side fault interrupting device for this transformer. Requested in-service date is 05/15/2020
DOM-2019-019 | DOM | PJM South | 2019-04-11 | 2019-06-13 |  |  |  | Chickahominy Substation | DEV Distribution has submitted a DP Request to add a 56 MVA distribution transformer at Chickahominy Substation in Charles City County. The new transformer is being requested for contingency support of Providence Forge substation. Requested in-service date is 5/31/2021. Initial In-Service: Summer: 10 MW Load Projected 2024 Load: Summer: 21 MW
DOM-2019-020 | DOM | PJM South | 2019-05-16 |  |  |  |  | Enterprise Substation | DEV Distribution has submitted a DP Request to add a 3rd, 84 MVA distribution transformer at Enterprise Substation in Loudoun County. The new transformer is being driven by continued datacenter load growth and alternate feed contract reservations. Requested in-service date is 07/15/2020. Note: Distribution’s Customer is also requesting 145 MVA of alternate capacity.
DOM-2019-022 | DOM | PJM South | 2019-05-16 |  |  |  |  | Poland Road Substation | DEV Distribution has submitted a DP Request to add a 4th, 84 MVA distribution transformer at Poland Road Substation in Loudoun County. The new transformer is being driven by continued load growth in the area and contingency loading for loss of one of the xisting transformers. Requested inservice date is 12/31/2021.
DOM-2019-023 | DOM | PJM South | 2019-05-16 |  |  |  |  | Brickyard | DEV Distribution has submitted a DP Request for a new substation (Brickyard) to support a new datacenter campus in Prince William County with a total load in excess of 100 MW. Requested in-service date is 12/15/2021.
DOM-2019-025 | DOM | PJM South | 2019-07-11 |  |  |  |  | Coleman Creek DP - Customer Load Request | ODEC has submitted a request on behalf of Mecklenburg Electric Coop (MEC) for a new delivery point (Coleman Creek) at Boydton, VA to support a new datacenter campus with a total load in excess of 100 MW. Requested in-service date is 04/01/2020
DOM-2019-026 | DOM | PJM South | 2019-08-27 |  |  |  |  | HEMC Dawsons Crossroads DP | NCEMC has submitted a request on behalf of Halifax EMC (HEMC) for a new Delivery Point (Dawsons Crossroads) at Halifax, NC, to replace an existing distribution Delivery Point due to poor reliability. The customer requests service by November 1, 2020.
DOM-2019-027 | DOM | PJM South | 2019-07-11 |  |  |  |  | Chickahominy TX #1 Replacement - THA | Chickahominy 500-230 kV 840 MVA transformer #1 needs to be replaced as a result of Dominion’s ongoing transformer health assessment (THA) process. This process considers design characteristics, past electrical test results, dissolved gas-in-oil test results, age, ongoing maintenance issues, and past failures of similar designed transformers. This transformer was manufactured in 1987 and is the last Westinghouse shell transformer on the Dominion System, these transformers have known issues. Drivers for replacement are: * Reduced BIL Ratings * Previously remanufactured following failure * Transformers of this manufacture are considered suspect due to previous transformer failures
DPL-2018-0001 | DPL | PJM MA | 2018-10-29 | 2018-12-07 |  |  |  |  | Customer has requested a new 69 kV interconnection point off the Harbeson - Millsboro 69 kV line due to deteriorating infrastructure at existing tap and load growth within the cooperative.
DPL-2018-0002 | DPL | PJM MA | 2018-10-29 | 2019-02-22 |  |  |  |  | Customer has requested a new point of interconnection at DPL’s Milford substation due to load growth within the cooperative. * Forecasted Load: 73 MW
DPL-2018-0003 | DPL | PJM MA | 2018-10-29 | 2018-12-07 |  |  |  |  | Customer has requested a new point of interconnection between DPL’s West Cambridge and Vienna 69 kV Substations to address reliability concerns.
DPL-2018-0004 | DPL | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  |  | Comprehensive inspection data revealed deterioration on Sharptown - Laurel 69 kV line.
DPL-2018-0005 | DPL | PJM MA | 2018-10-29 | 2019-01-25 |  |  |  |  | Comprehensive inspection data revealed deterioration on Vienna - West Cambridge 69 kV line.
DPL-2019-001 | DPL | PJM MA | 2019-01-25 | [5 empty] | Customer has requested a new 138 kV interconnection point off the Mt. Pleasant to Townsend 138 kV line due to load growth within the municipality.
DPL-2019-002 | DPL | PJM MA | 2019-06-28 |  |  |  |  | Grasonville Substation | Grasonville Substation is in a deteriorated condition and has experienced flooding issues
DUQ-2019-001 | DUQ | PJM West | 2019-02-20 | [5 empty] | The Pennsylvania Turnpike Commission (PTC) has informed Duquesne Light Company (DLC) that it plans to construct an expressway from Jefferson Hills Borough to I-376 in Monroeville. The initial construction phases of this expressway begin in Jefferson Hills and end in the city of Duquesne. The construction of this expressway will closely follow the DLC transmission corridor between the Wilson and Port Perry transmission stations and, as such, a number of DLC’s existing transmission structures will be impacted and/or displaced. The PTC has requested that all DLC modifications are completed prior to the start of the corresponding expressway construction phase, the last of which is 3/1/2023.
EKPC-2019-001 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | The Lancaster distribution substation is 64 years old, and does not meet current EKPC standards. The substation has limited space, and due to its current configuration requires a full station outage to replace the regulators. The transformer and regulators are located inside the high side box structure. There is little clearance around the low bay which makes it impossible to use equipment when replacing any of the reclosers. The station does not have a low side transfer bus/scheme or a bypass for metering equipment. Because of the short length of the station driveway, EKPC staff have to park on the roadway to open the station gate. This station drive is located in a slight curve, which make this access a safety concern. The station drive has also had water run-off issues, and has required repairs numerous times over the last several years.
EKPC-2019-002 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | Real time load levels on the Skaggs 138-69 kV autotransformer have exceeded the normal transformer rating on several occasions over the last five years. During extreme weather and other system issues on January 7, 2018, real time loading on the Skaggs transformer reached 136 MVA, over 120% of the normal rating. EKPC experienced operational issues, including loss of load, during this overload event.
EKPC-2019-003 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | Elizabethtown - KU Rogersville line section is on of the worst performing line sections on the EKPC system. There are a total of 7 distribution substations on this one circuit, and this is the largest number of distribution substations on a circuit on the EKPC system. These 7 distribution substations serve over 13,000 customers and almost 40% of the customers on the Nolin RECC system. Nolin has requested that EKPC develop a solution that minimizes the number of customers impacted during an outage.
EKPC-2019-004 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | Denny - Wayne County: The Denny - Wayne County 69 kV line section is one of the worst performing locations on the EKPC system. This line section has five distribution substations tapped off of the main 20.4 mile line section: Slat, Homestead, Monticello, Gap of the Ridge and Gregory Road. The line was originally constructed in 1953 with 4/0 ACSR conductor, and the line section was reconductored to 556 MCM in 1985. EKPC has had numerous recent issues with cross arm failures on this line section. Homestead (continued): The Homestead substation is the largest substation on the South Kentucky RECC system (# of customers). The Homestead substation serves Wayne County Hospital, some nursing homes, several factories, the Wayne County School system, and over 3,200 customers. The Homestead distribution substation is served from a radial transmission feed. This tap line is approximately 1.2 miles in length, and was originally built by TVA. The line section is at least 50 years old, and has several poles that are in poor condition. South Kentucky RECC (“SKRECC”) has very limited back-feed capabilities for the Homestead substation. Monticello: Issues identified at the Monticello distribution substation include: -The original Monticello distribution station was constructed in 1954 and does not meet EKPC current standards. -The current location is adjacent to a saw mill facility, and saw dust debris from this facility has caused contamination issues that have resulted in a paste build-up on equipment in the substation. Outages have been required for equipment cleaning. -The station has a mix of both 12.5 kV and 25 kV low side voltages, and the station has a non-standard wood structure that was constructed for the 25 kV auto transformer bank. This wood structure is in poor condition. Monticello (continued): -The station does not have the EKPC standard low bay transfer scheme, which causes additional outage time and creates a heightened safety risk when taking equipment out of service for maintenance activities. -The station does not have the EKPC standard metering bypass switching scheme, which causes additional outage time when replacing or working on the metering equipment. -SKRECC cannot back-feed all of the load on this station during an outage
EKPC-2019-005 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | The Boone County - Williamstown 69 kV line section is 60 years old. The LineVue robot from Kinectrics Corporation revealed the majority of the line section to be in below average or poor condition (static and conductor). The EKPC Reliability team has included this line section in their top 10 of line sections that should be addressed due to the condition assessment.
EKPC-2019-006 | EKPC | PJM West | 2019-02-20 | 2019-03-25 |  |  |  |  | The KU Wofford - Whitley City 69 kV line section is 67 years old. The LineVue robot from Kinectrics Corporation revealed that the majority of the line section is in poor condition (static and conductor). The EKPC Reliability team has included this line section in their top 10 of line sections that should be addressed due to the condition assessment.
EKPC-2019-007 | EKPC | PJM West | 2019-02-20 | 2019-04-23 |  |  |  |  | The Grants Lick to Griffin Junction line section is 62 years old. The LineVue robot from Kinectrics Corporation revealed that the majority of the line section is in poor condition (static and conductor). The EKPC Reliability team has included this line section in their top 10 of line sections that should be addressed due to the condition assessment.
EKPC-2019-008 | EKPC | PJM West | 2019-04-23 | 2019-06-17 |  |  |  | Elizabethtown | The EKPC-owned Kargle-LGE/KU Elizabethtown 69 kV tie-line was the most restrictive facility for scheduling of maintenance outages on the EKPC transmission system for the 2016-2017 period due to the conductor rating. Additionally, this facility restricts the ability of LGE/KU to schedule outages on the transmission system in the area. These restrictions are prevalent even during light load conditions, resulting in either inability to take maintenance outages or sectionalizing of the transmission system to shed load for subsequent outages in the area. Furthermore, this facility was constructed in 1958, and many of the wood poles are in marginal condition.
JCPL-2018-001 | JCPL | PJM MA | 2018-09-21 | 2018-11-28 |  |  |  |  | At Windsor for the event of a stuck 230 kV bus tie breaker, both 230 kV feeds are outaged, along with two 230-34.5 kV transformers feeding the Windsor area distribution load. In the current configuration, the 230 kV feeds the 34.5 kV bus via a 230-34.5 kV transformer. The 34.5 kV bus then feeds into the local 34.5 kV network. This arrangement creates a transmission path through lower voltage facilities.
JCPL-2018-002 | JCPL | PJM MA | 2018-09-21 | 2018-11-28 |  |  |  |  | In the event of a Pequest #1 115-34.5 kV transformer fault, the S919 line (3-terminal line) and the bus tie breaker are relied upon to clear the fault resulting in an additional loss of the Drakestown, Flanders, and Morris Park transformers. At Pequest River, in the event of a stuck 115 kV bus tie breaker, both 115 kV feeds into Pequest River are outaged, along with two 115-34.5 kV transformers feeding the Pequest River area 34.5 kV network, the Drakestown #1, Flanders #2, and Morris Park #1 transformers.
JCPL-2018-003 | JCPL | PJM MA | 2018-09-21 | 2018-11-28 |  |  |  |  | N-1-1 outages result in loss of the 34.5 kV lines serving the area impacting approximately 7,700 customers and approximately 33 MW of load. N-1-1 outage of the Traynor-Madison 34.5 kV and the Traynor-Livingston Switch Point 34.5 kV lines, thermal loading on the Traynor-Madison (N14) 34.5 kV line is greater than 105% of its 50 MVA limit.
JCPL-2018-004 | JCPL | PJM MA | 2018-09-21 | 2018-11-28 |  |  |  |  | At Morristown, in the event of a stuck 230 kV bus tie breaker, both 230 kV feeds are outaged, along with two 230-34.5 kV transformers feeding the Morristown area 34.5 kV network impacting approximately 23,100 customers and approximately 155 MW of load. In the current configuration, the 230 kV feeds the 34.5 kV bus via 230-34.5 kV transformers. The 34.5 kV bus then feeds into the local 34.5 kV network which is operated in a radial configuration due to overdutied 34.5 kV breakers.
JCPL-2018-005 | JCPL | PJM MA | 2018-09-21 | 2018-11-28 |  |  |  |  | Readington T774 34.5 kV line is radial. Line outage or contingency as well as 34.5 kV bus maintenance or outages result in loss of the T774 impacting approximately 1,700 customers and approximately 35 MW of load.
JCPL-2019-001 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Atlantic – Freneau 230 kV Lin | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. `
JCPL-2019-002 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Kittatinny – Pohatcong 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-003 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Kittatinny – Portland 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-004 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Lakewood – Leisure Village 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-005 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Leisure Village – Manitou 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-006 | JCPL | PJM MA | 2019-02-22 | [5 empty] | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-007 | JCPL | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Traynor – Whippany 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-008 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Red Bank (S1033) 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: substation conductor. * Before: 678 / 780 * After: 709 / 869
JCPL-2019-009 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Eaton Crest - Red Bank (T2020) 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: line relaying, line trap, substation conductor * Before: 678 / 780 * After: 709 / 869
JCPL-2019-010 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Pohatcong - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Line Relaying, Circuit Breaker, Line Trap, Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-011 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gillette - Traynor 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Line Relaying, Circuit Breaker, Line Trap, Substation Conductor * Before: 678 / 802 * After: 843 / 1011
JCPL-2019-012 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Greystone - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor, Current Transformer * Before: 678 / 813 * After: 709 / 869
JCPL-2019-013 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Raritan River - Werner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Circuit Breaker, Substation Conductor, Line Relaying, Current Transformer * Before: 652 / 739 * After: 709 / 869
JCPL-2019-014 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Greystone - Portland 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor, Current Transformer * Before: 830 / 1000 * After: 910 / 1077
JCPL-2019-015 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gillette - Traynor 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-016 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-017 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic - Smithburg 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 678 / 813 * After: 709 / 869
JCPL-2019-018 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment.
JCPL-2019-019 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Chester - Glen Gardner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 650 / 817 * After: 709 / 869
JCPL-2019-020 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Gilbert - Glen Gardner 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Wave Trap, Line Relaying, Current Transformer, Breaker and Terminal Switches, Line Metering * Before: 815 / 923 * After: 1136 / 1311
JCPL-2019-021 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Chester - West Wharton 230 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment: Substation Conductor * Before: 650 / 817 * After: 709 / 869
JCPL-2019-022 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 260 / 416 (63% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Bernardsville – Long Lines 34.5 kV Line ¦44 / 47 ¦44 / 53 ¦Line Relaying, Substation Conductor ¦5.3 ¦ ¦Long Lines – Greater Crossroads 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦3.2 ¦ ¦Greater Crossroads – Merck 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦6.2 ¦
JCPL-2019-023 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 275 / 346 (79% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Gilbert – Bridgeton 34.5 kV Line ¦37 / 45 ¦37 / 45 ¦- ¦3.9 ¦ ¦Bridgeton – Frenchtown 34.5 kV Line ¦37 / 45 ¦37 / 45 ¦- ¦2.3 ¦ ¦Frenchtown – Frenchtown Solar 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦4.6 ¦ ¦Frenchtown Solar – Rosemont 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦3.5 ¦ ¦Rosemont – Alexauken 34.5 kV Line ¦39 / 48 ¦39 / 48 ¦- ¦4.5 ¦ ¦Alexauken – Rocktown 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦Line Relaying ¦2.0 ¦
JCPL-2019-024 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 181 / 383 (48% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Greystone – Davis 34.5 kV Line ¦66 / 79 ¦70 / 85 ¦Substation Conductor ¦2.2 ¦ ¦Davis – Alderney 34.5 kV Line ¦46 / 58 ¦46 / 58 ¦- ¦0.3 ¦ ¦Alderney – Tabor Tap 34.5 kV Line ¦46 / 58 ¦46 / 58 ¦- ¦0.3 ¦ ¦Tabor Tap – Morristown Tap 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦1.1 ¦ ¦Morristown Tap – Morris Plains Tap 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦0.2 ¦ ¦Morris Plains Tap – Morristown 34.5 kV Line ¦34 / 43 ¦34 / 43 ¦- ¦3.6 ¦ ¦Morris Plains Tap – Morris Plains 34.5 kV Line ¦41 / 52 ¦83 / 100 ¦Disconnect Switches ¦1.5 ¦ ¦Morristown Tap – Whippany ¦41 / 50 ¦41 / 50 ¦- ¦6.2 ¦
JCPL-2019-025 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 182 / 257 (71% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Highlands – Sandy Hook 34.5 kV Line ¦37 / 38 ¦37 / 38 ¦- ¦1.1 ¦ ¦Sandy Hook Switch Point – Sandy Hook 34.5 kV Line ¦26 / 33 ¦37 / 38 ¦Substation Conductor ¦0.1 ¦ ¦Sandy Hook Switch Point – Sea Bright Switch Point 34.5 kV Line ¦37 / 38 ¦37 / 38 ¦- ¦2.4 ¦ ¦Sea Bright Switch Point – Monmouth Beach 34.5 kV Line ¦35 / 38 ¦35 / 38 ¦- ¦2.0 ¦ ¦Monmouth Beach – Long Branch 34. 5 kV Line ¦34 / 38 ¦34 / 38 ¦- ¦2.2 ¦
JCPL-2019-026 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 132 / 134 (99% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc. ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Gillette – Green Village 34.5 kV Line ¦41 / 50 ¦41 / 50 ¦- ¦5.7 ¦
JCPL-2019-027 | JCPL | PJM MA | 2019-03-25 | [5 empty] | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment * Identified Structures (end of life / total): 155 / 322 (48% Failure Rate) * Failure reasons: Age, bad/cut/missing grounds, rot/decay, woodpecker holes, etc ¦Transmission Line / Substation Locations ¦ Existing Circuit Rating (SN/SE) ¦Existing Conductor Rating (SN / SE) ¦Limiting Terminal Equipment ¦Length of Line (miles) ¦ ¦Traynor – Madison Switch Point 34.5 kV Line ¦39 / 50 ¦39 / 50 ¦- ¦1.5 ¦ ¦Madison Switch Point – Madison 34.5 kV Line ¦55 / 67 ¦55 / 67 ¦- ¦1.0 ¦ ¦Madison Switch Point – Academy 34.5 kV Line ¦35 / 44 ¦35 / 44 ¦- ¦3.6 ¦ ¦Academy – Okner 34.5 kV Line ¦44 / 53 ¦44 / 53 ¦- ¦2.2 ¦ ¦Okner – Mount Pleasant 34.5 kV Line ¦38 / 49 ¦38 / 49 ¦- ¦1.1 ¦ ¦Mount Pleasant – Whippany 34.5 kV Line ¦41 / 49 ¦46 / 58 ¦Substation Conductor ¦1.5 ¦
JCPL-2019-028 | JCPL | PJM MA | 2019-04-11 |  |  |  |  | Atlantic SVC | The Atlantic SVC has an increasing trend of outages and failures increasing maintenance needs.
ME-2018-001 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1761 |  |  | * New Customer Connection - A customer requested 69 kV service for load of approximately 17 MVA near the North Temple - Northkill 69 kV line. Requested in-service date is 12/2019.
ME-2018-002 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1762 |  | Hill-Tolna 115 kV line rehab | Maintenance/rehab work will be performed on the Hill-Tolna 115 kV line. Transmission line rating limited by terminal equipment. * Hill - Johnson Controls 115 kV line: Existing emergency line rating is 150 MVA. Existing conductor emergency rating is 223 MVA. * Johnson Controls - Tolna 115 kV line: Existing emergency line rating is 208 MVA. Existing conductor emergency rating is 223 MVA.
ME-2018-003 | ME | PJM MA | 2018-09-21 | 2018-11-28 | 2019-07-26 | s1811 |  | Pleasureville-Harley Davidson-York Solid Waste 115 kV line rehab | Maintenance/rehab work will be performed on the Pleasureville-Harley Davidson-York Solid Waste 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Harley Davidson 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 430 MVA. * Harley Davidson - York Inc. 115 kV line: Existing emergency rating is 263 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-004 | ME | PJM MA | 2018-09-21 | 2018-11-28 | 2019-07-26 | s1812 |  | Pleasureville-Mt. Rose-Violet Hill 115 kV line rehab | Maintenance/rehab work will be performed on the Pleasureville-Mt. Rose-Violet Hill 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Mt. Rose 115 kV line: Existing emergency line rating is the existing conductor emergency rating. * Mt. Rose - Violet Hill 115 kV line: Existing emergency line rating is 266 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-005 | ME | PJM MA | 2018-09-21 | 2018-11-28 | 2019-07-26 | s1813 |  | Smith Street-Westgate-York Solid Waste 115 kV line rehab | Segments of Smith Street-Westgate-York Solid Waste 115 kV line are at or beyond service life. Transmission line rating limited by terminal equipment. * Smith Street - Smith Street Tap 115 kV line: Existing emergency line rating is 152 MVA. Existing conductor emergency rating is 223 MVA. * Westgate - Smith Street Tap 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 282 MVA. * York Inc. - Smith Street Tap115 kV line: Existing emergency line rating is the existing conductor emergency rating.
ME-2018-006 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1763 |  | Windsor-Yorkana Tap 115 kV line rehab | Maintenance/rehab work will be performed on the Windsor-Yorkana Tap 115 kV line. Relays on Windsor - Yorkana 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or in a degraded condition. Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-007 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1764 |  | Hunterstown - Jackson 230 kV line relays | * Relays on Hunterstown - Jackson 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 678 MVA. Conductor normal rating is 709 MVA.
ME-2018-008 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1765 |  | Tolna - Windsor 115 kV line relays | * Relays on Tolna - Windsor 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Conductor emergency rating is 282 MVA.
ME-2018-009 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1766 |  | Mountain - P.P.G.I. 115 kV line relays | * Relays on Mountain - P.P.G.I. 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 159 MVA. Conductor normal rating is 184 MVA.
ME-2018-010 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1767 |  | Jackson - Yorkana 230 kV line relays relays | * Relays on Jackson - Yorkana 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 650 MVA. Conductor normal rating is 709 MVA.
ME-2018-011 | ME | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1768 |  | Middletown Junction - Smith Street (978) 230 kV line relays | * Relays on Middletown Junction - Smith Street (978) 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 103 MVA. Conductor normal rating is 129 MVA.
ME-2018-012 | ME | PJM MA | 2018-09-21 | 2018-11-28 | 2019-07-26 | s1812 |  | Pleasureville - Violet Hill 115 kV line relays | * Relays on Pleasureville - Violet Hill 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 204 MVA. Conductor normal rating is 232 MVA.
ME-2018-013 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1814 |  | Middletown Junction 230/69 kV transformer No.3 | Middletown Junction No,3 230/69 kV: Transformer is 55 years old There have been 44 maintenance orders since 2003 Multiple oil leaks in load tap changer Combustible gasses found in load tap changer oil
ME-2018-014 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1815 |  | Broad Street - West Lebanon 69 kV line relays | Relays on Broad Street - West Lebanon 69 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 71 MVA SN / 91 MVA SE. Existing conductor rating is 111 MVA SN / 134 MVA SE. (substation conductor and disconnect switches)
ME-2018-015 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1816 |  | Hokes - Smith St, Hokes - Lehigh Cement, & Hokes - Jackson 69 kV lines relays | Relays on Hokes - Smith St, Hokes - Lehigh Cement, & Hokes - Jackson 69 kV lines evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Hokes - Jackson 69 kV line: Existing line rating is 51 MVA SN / 56 MVA SE. Existing conductor rating is 53 MVA SN / 56 MVA SE. (substation conductor
ME-2018-016 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1817 |  | Hunterstown - North Hanover 115 kV line relays | Relays on Hunterstown - North Hanover 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 232 MVA SN / 277 MVA SE. Existing conductor rating is 232 SN / 282 MVA SE. (line trap)
ME-2018-017 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1818 |  | South Lebanon #1 and #2 230-69 kV Transformer Replacement and 230 kV Ring Bus | Relays on Jackson - Westgate 115 kV line evaluated and determined to be obsolete and/or degraded condition. Jackson - JE Baker 115 kV line: Existing line rating is 274 MVA SN / 344 MVA SE. Existing conductor rating is 373 MVA SN / 430 MVA SE. (substation conductor and disconnect switches) JE Baker - Taxville 115 kV line: Existing line rating is 274 MVA SN / 344 MVA SE. Existing conductor rating is 373 MVA SN / 430 MVA SE. (substation conductor and disconnect switch) Taxville - Westgate 115 kV line: Existing line rating is 232 MVA SN / 277 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE (line trap)
ME-2018-018 | ME | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1819 |  | Hunterstown - Gardners 115 kV line relays | Relays on Hunterstown - Gardners 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 163 MVA SN / 185 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE. (line trap, breaker, CTs, relay, and substation conductor)
ME-2018-019 | ME | PJM MA | 2018-11-28 | 2019-01-25 |  |  |  | Jackson 230/115 kV transformer No.5 | Jackson #5 230/115 kV: * Transformer is 48 years old * Dissolved gas in oil * History of oil leaks, compromising oil integrity
ME-2018-020 | ME | PJM MA | 2018-11-28 | 2019-01-25 |  |  |  | North Hershey 230-69 kV transformer No.1 | North Hershey #1 230-69 kV: * Transformer is over 40 years old * Critical role in operation of 69 kV * Transformer leaking
ME-2018-021 | ME | PJM MA | 2018-11-28 | 2019-01-25 |  |  |  | Hokes - Smith Street 69 kV Line Rehab/Rebuild | * Customer requested transmission service in the Stroudsburg, PA area due to multiple outages over past several years. * Limited outage restoration options in the area. * The area north of Shawnee substation has no transmission system * Customers in this area are served by three 34.5 kV circuits from Shawnee or from Walker substation which is radial 69 kV. * 6000 customers directly served by the 34.5 kV circuits * 7600 customers fed from substations sourced by the 34.5 kV system * Territory is a narrow corridor bounded by the Delaware river to the east
ME-2019-001 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Adamstown - South Reading 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-002 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Baldy - South Hamburg 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-003 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | North Temple - North Kill 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-005 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Carsonia - South Reading 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-006 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | East Topton - North Boyertown 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-007 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Alcoa - South Lebanon 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-008 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Bernville - South Hamburg 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-009 | ME | PJM MA | 2019-02-22 |  |  |  |  | Middletown Junction - Swatara Hill - Campbelltown 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-010 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Middletown Junction - Smith Street 115 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-011 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Allentown Cement - Lyons - South Hamburg 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-012 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | North Temple - South Hamburg 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-013 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Alcoa - Broad Street 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-014 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | North Hershey - Turf Club 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-015 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Birdsboro - South Reading 69 kV Line Rebuild/Rehab | The South Reading-Painted Sky-Lorane-Pioneer Crossing-Birdsboro 69 kV line is exhibiting deterioration resulting in increased maintenance. The Transmission line is approaching end of life * 28 out of 125 structures failed inspection (22% Failure Rate). * Failure reasons include bad/cut/missing grounds, static bayonet, broken guy, woodpecker damage, etc. * Total line distance is approximately 7.5 miles. Thermal loading on the Lorane-Pioneer Crossing 69 kV section is ~115% of the SE rating for loss of the N. Boyertown 230-69 kV transformer & S. Reading-Birdsboro 828 69 kV line. (2018 RTEP Model - 2023 Summer) Transmission line rating is limited by terminal equipment. South Reading-Painted Sky 69 kV line: (substation conductor) * Existing line rating is 88 / 114 MVA (SN / SE). * Existing conductor rating is 139 / 169 MVA (SN / SE). Painted Sky-Lorane 69 kV line: (substation conductor) * Existing line rating is 137 / 169 MVA (SN / SE). * Existing conductor rating is 139 / 169 MVA (SN / SE).
ME-2019-016 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | North Boyertown - Ringing Rocks 69 kV Line Rebuild/Rehab | The N. Boyertown-Cabot-County Line-Middle Creek-Ringing Rocks 69 kV line is exhibiting deterioration resulting in increased maintenance. The Transmission line is approaching end of life * 41 out of 147 structures failed inspection (28% Failure Rate). * Failure reasons include split top, cracking, etc. * Total line distance is approximately 7.7 miles. Thermal loading on North Boyertown-Cabot 69 kV section and Cabot-County Line 69 kV sections are loaded to approximately 112% and 100% of their SE ratings respectively for loss of the North Boyertown-West Boyertown 69 kV line & Birdsboro-West Boyertown 69 kV line. (2018 RTEP Model - 2023 Summer) Transmission line rating is limited by terminal equipment. North Boyertown - Cabot Tap 69 kV line: (relay and substation conductor) * Existing line rating is 62 / 72 MVA (SN / SE). * Existing conductor rating is 72 / 72 MVA (SN / SE). County Line - Middle Creek 69 kV line: (substation conductor) * Existing line rating is 132 / 158 MVA (SN / SE). * Existing conductor rating is 139 / 169 MVA (SN / SE). Middle Creek - Ringing Rocks 69 kV line: (relay, disconnect switch) * Existing line rating is 62 / 62 MVA (SN / SE). * Existing conductor rating is 99 / 99 MVA (SN / SE).
ME-2019-017 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Cleona - West Lebanon 69 kV Line Rebuild/Rehab | The N. Lebanon-Cleona-W. Lebanon 69 kV line is exhibiting deterioration resulting in increased maintenance. The Transmission line is approaching end of life * 58 out of 73 structures failed inspection (79% Failure Rate). * Failure reasons include top rot, voids, woodpecker holes, etc. * Total line distance is approximately 7.1 miles. Thermal loading on Cleona-West Lebanon 69 kV section is approximately 98% of the SE rating for loss of the South Lebanon 230-69 kV #1 & #2 transformers. (2018 RTEP Model - 2023 Summer) Transmission line rating is limited by terminal equipment. North Lebanon - Cleona 69 kV line: (relay and disconnect switches) * Existing line rating is 78 / 82 MVA (SN / SE). * Existing conductor rating is 111/134 MVA (SN / SE).
ME-2019-018 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | South Lebanon #1 and #2 230-69 kV Transformer Replacement and 230 kV Ring Bus | South Lebanon #1 230-69 kV: * Transformer is 49 years old * Experiencing dissolved gasses in oil * Analysis shows breaking down of paper insulation South Lebanon #2 230-69 kV: * Transformer is 50 years old and at end of life * History of oil leaks * Analysis shows breaking down of paper insulation * Broken fans and deteriorating bushings * Tank temp has to be read with a thermal gun
ME-2019-019 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Kittatinny - Portland 230 kV Relay Replacement | Relays on Kittatinny - Portland 230 kV line have been identified as protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * Kittatinny - Portland 230 kV line: Existing line rating: 1114 / 1195 MVA (SN / SE). Existing conductor rating: 1114 / 1285 MVA (SN / SE). (relaying)
ME-2019-020 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | South Lebanon - Myerstown 69 kV Line Rehab/Rebuild | * Line sections are exhibiting deterioration, increasing maintenance needs. Transmission line is approaching end of life * Transmission line ratings are limited by terminal equipment.
ME-2019-021 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | North Lebanon - Turf Club 69 kV Line Rehab/Rebuild | The North Lebanon - Turf Club 69 kV line is exhibiting deterioration resulting in increased maintenance. The Transmission line is approaching end of life * 236 out of 360 structures failed inspection. (66% Failure Rate) * Failure reasons include decay, woodpecker holes, cracking, bad/cut/missing ground wires, etc. * Total line distance is approximately 23 miles. Thermal loading on Turf Club - Indiantown Gap 69 kV and Indiantown Gap - Lickdale 69 kV line sections are approximately 97% and 86% of their SE ratings respectively for loss of North Lebanon - Fredericksburg 69 kV line section. (2018 RTEP Model - 2023 Summer) Transmission line ratings limited by terminal equipment. * North Lebanon - Fredericksburg 69 kV line: Existing line rating: 82 / 103 MVA (SN / SE). Existing conductor rating is 139 / 169 MVA (SN / SE). (disconnect switches)
ME-2019-022 | ME | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Hokes - Smith Street 69 kV Line Rehab/Rebuild | The Hokes - Smith St 69 kV is exhibiting deterioration resulting in increased maintenance. The Transmission line is approaching end of life. * 83 out of 122 structures failed inspection. (68% Failure Rate) * Failure reasons include contamination, sound, bad/cut/missing ground wires, etc. * Total line distance is approximately 5.4 miles. Thermal loading on Hokes-Smith Street 69 kV line is loaded to approximately 158% of the SE rating for loss of the Jackson-Hokes 69 kV line & the Violet Hill 69 kV transformer. (2018 RTEP Model - 2023 Summer) Transmission line rating is currently limited by the conductor: 43 / 44 MVA (SN / SE).
ME-2019-023 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Glendon 115 kV Ring Bus | * The loss of Glendon substation results in loss of approximately 40 MW of load and approximately 5500 customers. * Substation consists of: * Three networked 115 kV lines * Two distribution transformers connected to transmission with switches * No bus tie breaker
ME-2019-024 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Lincoln 115 kV Ring Bus | * The loss of Lincoln substation results in loss of approximately 40 MW of load and approximately 5700 customers. * Substation consists of: * Three networked 115 kV lines * Two distribution transformers in substation; one tapped off line * All transformers connected to transmission with switches * No bus tie breaker
ME-2019-025 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Westgate 115 kV Tie Breaker | * The loss of Westgate substation results in loss of approximately 30 MW of load and approximately 5800 customers. * Substation consists of: * Two networked 115 kV transmission lines * Two distribution transformers connected to transmission with switches
ME-2019-026 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Northwood 230 kV Ring Bus | * The loss of Northwood substation results in loss of approximately 150 MW of load and approximately 9000 customers. * Substation consists of: * Two networked 230 kV lines * One 230/115 kV transformer connected with circuit switcher * Two 230-34.5 kV distribution transformers connected with circuit switchers * One bus tie breaker
ME-2019-027 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Pleasureville Breaker-and-a-Half | * The loss of Pleasureville substation results in loss of approximately 40 MW of load and approximately 5800 customers. * Substation consists of: * Three networked 115 kV lines connected to a straight bus * No bus tie breaker
ME-2019-028 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Northwood 115 kV Ring Bus | * The Northwood 115 kV bus creates a three-terminal line consisting of two 115 kV lines and a 230/115 kV transformer. * An N-1 outage results in the loss of all three networked elements
ME-2019-029 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Fredericksburg 69 kV Ring Bus | * The North Lebanon – Turf Club – South Lebanon 69 kV line is operated normally opened at Frystown to prevent a 3-terminal line. * Substations impacted by normally open point are as follows: * Fredericksburg – 12 MW & 1433 Customers * Lickdale – 24 MW & 3302 Customers * Indiantown Gap – 7 MW & 1 Customer (Wholesale) * Frystown – 16 MW & 1696 Customers * Rehrersburg – 5 MW & 1217 Customers * These substations total to over 60 MW and approximately 7600 customers.
ME-2019-030 | ME | PJM MA | 2019-07-11 |  |  |  |  | New Customer on the Martins Creek - Siegfried #2 230 kV line | New Customer Connection – A customer requested 230 kV service; anticipated load of approximately 27 MVA; location is near the PPL Martins Creek – Siegfried #2 230 kV line. Requested in-service date is 6/1/2021
ME-2019-031 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Gitts Run substation results in loss of approximately 40 MW of load and approximately 2900 customers. * Substation consists of: * Four 115 kV transmission lines * Two distribution transformers connected to transmission with switches * One normally open bus tie switch
ME-2019-032 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Windsor 115 kV Tie Breaker | * System Performance Projects * Load at risk in planning and operational scenarios * Add/Expand Bus Configuration * Reduce the amount of exposed potential local load loss during contingency conditions * Eliminate simultaneous outages to multiple networked elements
ME-2019-033 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Hamilton substation results in loss of approximately 30 MW of load and approximately 3600 customers. * Substation consists of: * Two 115 kV lines. * Two distribution transformers connected with switches * One generator connected with a switch
ME-2019-034 | ME | PJM MA | 2019-05-31 | [5 empty] | * The loss of Campbelltown substation results in loss of approximately 40 MW of load and approximately 8800 customers. * Substation consists of: * Three networked 69 kV transmission lines * Two distribution transformers connected to bus with switches * No bus tie breaker
ME-2019-037 | ME | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Hill 115 kV Ring Bus | * The loss of Hill substation results in loss of approximately 30 MW of load and approximately 7800 customers. * Two 115 kV lines * Two distribution transformers connected to transmission with switches
ME-2019-038 | ME | PJM MA | 2019-05-31 | 2019-06-28 |  |  |  | Carpenter Technology-West Reading 69 kV line | New Customer Connection - A customer requested 69 kV service; anticipated load is 22 MVA; location is near the Carpenter Technology-West Reading 69 kV line.
ME-2019-039 | ME | PJM MA | 2019-07-31 |  |  |  |  | Campbelltown - Middletown - North Hershey 69 kV Line Rebuild | Campbelltown – Middletown – North Hershey 69 kV line sections are exhibiting deterioration. * Total line distance is approximately 19.7 miles. * 260 out of 407 structures failed inspection (64% failure rate). * Failure reasons include age, decay, woodpecker holes. * Transmission line ratings are limited by terminal equipment: * Campbelltown – Campbelltown Tap 69 kV line (substation conductor, disconnect switches, relaying) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE) * Middletown – Wood St Tap 69 kV line (disconnect switches, line relaying, substation conductor) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE)
ME-2019-040 | ME | PJM MA | 2019-07-31 |  |  |  |  | Carsonia - Lyons - North Boyertown 69 kV line | Carsonia – Lyons – North Boyertown 69 kV line is exhibiting deterioration. * Total line distance is approximately 22.8 miles. * 339 out of 447 structures failed inspection (76% failure rate). * Failure reasons include age, woodpecker holes, bayonet pole, top rot. Thermal loading on the Clousers Crossing – North Boyertown 69 kV section is ~105% of the SE rating for the N-1-1 loss of the East Topton – Huffs Church 69 kV line section (bus 204829 to bus 20867) & North Boyertown 230-69 kV transformer (ME-P1-2-230- 003) (2018 RTEP Model – 2023 Summer) Transmission line ratings are limited by terminal equipment Lyons – Lyons tap 69 kV line (line relaying) * Existing line rating: 167/167 MVA (SN/SE) * Existing conductor rating: 218/251 MVA (SN/SE)
ME-2019-041 | ME | PJM MA | 2019-07-31 |  |  |  |  | Lucent - Muhlenberg 69 kV line | Lucent – Muhlenberg 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker, disconnect switches, line relaying) due to obsolescence of equipment. Limited spare parts are available. * Circuit breakers are 50+ years old with Type U bushings and have a history of oil leaks * Lucent disconnect switch has bad contacts * Line relays have a history of overtripping Transmission line rating is limited by terminal equipment: Lucent – Spring Valley 69 kV line (substation conductor, disconnect switches) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) Spring Valley – MG Tap 69 kV line (substation conductor, disconnect switches) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) MG Tap – Muhlenberg 69 kV line (substation conductor, disconnect switches) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE)
ME-2019-042 | ME | PJM MA | 2019-07-31 |  |  |  |  | Middletown Junction - Olmsted - Middletown 69 kV Line Terminal Upgrades | Middletown Junction – Olmstead - Middletown 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker, disconnect switches, line relaying) due to obsolescence of equipment. Limited spare parts are available. * Circuit breakers are 50+ years old with Type U bushings * Circuit breakers have a history of failed compressor belt * Circuit breaker has failing dielectric strength Transmission line rating is limited by terminal equipment: Middletown Junction – Olmstead 69 kV line (line relaying) * Existing line rating: 71/91 MVA (SN/SE) * Existing conductor rating: 111/134 MVA (SN/SE) Wood Street Tap – Wood Street 69 kV line (substation conductor) * Existing line rating: 38/49 MVA (SN/SE) * Existing conductor rating: 53/64 (SN/SE) Wood Street Tap – Middletown 69 kV line (substation conductor, disconnect switches, relaying) * Existing line rating: 51/66 MVA (SN/SE) * Existing conductor rating: 139/169 MVA (SN/SE)
ME-2019-043 | ME | PJM MA | 2019-07-31 |  |  |  |  | Carpenter Technology - South Reading 69 kV line | Carpenter Technology – South Reading 69 kV line is exhibiting deterioration. * Total line distance is approximately 5.9 miles. * 125 out of 151 structures failed inspection (83% failure rate). * Failure reasons include age, woodpecker holes, and sound. Transmission line ratings are limited by terminal equipment Carpenter Technology – Glenside 69 kV line (disconnect switches) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 102/124 MVA (SN/SE) Glenside – South Reading 69 kV line (disconnect switches, substation conductor) * Existing line rating: 82/103 MVA (SN/SE) * Existing conductor rating: 102/124 MVA (SN/SE)
ME-2019-044 | ME | PJM MA | 2019-07-31 |  |  |  |  | North Boyertown - West Boyertown 69 kV line | North Boyertown – West Boyertown 69 kV line is exhibiting deterioration. * Total line distance is approximately 3.6 miles. * 42 out of 71 structures failed inspection (59% failure rate). * Failure reasons include age, sound, and bayonet pole. Thermal loading on the North Boyertown – West Boyertown 69 kV line is ~88% of the SE rating for loss of the North Boyertown – Cabot 69 kV line section (bus 204606 to bus 204834). (2018 RTEP Model – 2023 Summer) Transmission line ratings are limited by terminal equipment: (substation conductor, line relaying) * Existing line rating: 71/72 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE)
ME-2019-045 | ME | PJM MA | 2019-07-31 |  |  |  |  | Baldy - East Topton 69 kV Line Terminal Upgrade | Baldy – East Topton 69 kV line – Terminal equipment has an increased risk of failure (circuit breaker and line relaying) due to obsolescence of equipment. Limited spare parts are available. * East Topton circuit breaker is 40+ years old with Type U bushings and has a history of failed oil dielectric strength Transmission line rating is limited by terminal equipment: Baldy – Kutztown 69 kV line (substation conductor) * Existing line rating: 76/90 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE) Kutztown – East Topton 69 kV line (substation conductor, line relaying) * Existing line rating: 62/62 MVA (SN/SE) * Existing conductor rating: 80/96 MVA (SN/SE)
ME-2019-046 | ME | PJM MA | 2019-07-31 |  |  |  |  | Hamilton – Hunterstown 115 kV Line | Hamilton – Hunterstown 115 kV Line 221/263 232/282 Substation Conductor
ME-2019-047 | ME | PJM MA | 2019-07-31 |  |  |  |  | North Hanover – Gitts Tap 115 kV Line, Gitts Tap – Fairview 115 kV Line Relays and communication equipment | North Hanover – Gitts Tap 115 kV Line, 221/263, 232/282, Substation Conductor; Gitts Tap – Fairview 115 kV Line, 232/282, 232/282, -
ME-2019-048 | ME | PJM MA | 2019-07-31 |  |  |  |  | Jackson – Menges Mills 115 kV Line, Menges Mills – PH Glatfelter 115 kV Line Relays and communication equipment | Jackson – Menges Mills 115 kV Line, 163/185, 184/223, Line Trap; Menges Mills – PH Glatfelter 115 kV Line, 221/263, 232/282, Substation Conductor
ME-2019-049 | ME | PJM MA | 2019-07-31 |  |  |  |  | North Hanover – Gitts Run 115 kV Line, Gitts Run – PH Glatfelter 115 kV Line Relays and communication equipment | North Hanover – Gitts Run 115 kV Line, 232/282, 232/282, -; Gitts Run – PH Glatfelter 115 kV Line, 221/263, 232/282, Substation Conductor
ME-2019-050 | ME | PJM MA | 2019-07-31 |  |  |  |  | Caterpillar Tractor – Whiteford, Whiteford – Glades 115 kV Lines | Caterpillar Tractor – Whiteford 115 kV Line, 232/277, 232/282, Line Trap; Whiteford – Glades 115 kV Line, 184/223, 184/223, -
ME-2019-052 | ME | PJM MA | 2019-07-31 |  |  |  |  | Violet Hill – Queen Street, Queen Street – Springwood, Springwood – Yoe 115, Yoe – Redfront, & Redfront – Yorkana 115 kV Lines | Violet Hill – Queen Street 115 kV Line, 204/266, 232/282, Substation Conductor Queen Street – Springwood 115 kV Line, 232/282, 232/282, - Springwood – Yoe 115 kV Line, 232/282, 232/282, - Yoe – Redfront 115 kV Line, 184/223, 184/223, - Redfront – Yorkana 115 kV Line, 184/223, 184/223, -
ME-2019-053 | ME | PJM MA | 2019-06-28 |  |  |  |  | Raintree 115 kV substation | New Customer Connection – A customer requested 115 kV service; anticipated load is 28 MVA; location is near the Raintree 115 kV substation
ODEC-2019-001 | ODEC | PJM MA | 2019-05-31 | [5 empty] | The two 69kV lines serving Chincoteague (rated 36MW each) are nearing end of life (pole line installed 1983). Wood poles are exhibiting rot. * Both lines are co-located on several of the structures resulting in loss of all load on Chincoteague Island under single contingency. * Existing poles are difficult to access in Simoneaston Bay tidal marsh on Fish & Wildlife controlled land * Existing poles violate FAA glide path clearances for the Wallops Island NASA flight facility.
PE-2019-0001 | PE | PJM MA | 2019-01-25 | 2019-02-22 | 2019-08-08 | s1849 |  |  | Customer load growth in the Upland area of Delaware County PA.
PE-2019-0002 | PE | PJM MA | 2019-01-25 | [5 empty] | New customer has requested service in Chester County PA area.
PE-2019-0003 | PE | PJM MA | 2019-02-22 | 2019-04-26 | 2019-08-08 | s1850 |  | Island Road - Schuylkill 69 kV line | The portion of the Island Road to Schuylkill 69 kV transmission line that runs under the Schuylkill River is in a tunnel that is in deteriorating condition. (2/22/19)
PE-2019-0004 | PE | PJM MA | 2019-02-22 | 2019-04-26 | 2019-08-08 | s1850 |  | University - Schuylkill 69 kV line | The portion of the University to Schuylkill 69 kV transmission line that runs under the Schuylkill River is in a tunnel that is in deteriorating condition. (2/22/19)
PE-2019-0005 | PE | PJM MA | 2019-03-25 | 2019-04-26 | 2019-08-08 | s1850 |  | University City area of Philadelphia, PA | PECO distribution has requested transmission supply to serve 50 MVA of load in the University City area of the city of Philadelphia..(3/22/19)
PE-2019-0006 | PE | PJM MA | 2019-06-28 |  |  |  |  | Load Growth in South Philadelphia, PA | PECO Distribution Planning has been requested to support additional load growth in the South Philadelphia area of the City of Philadelphia Initial 2022 Load: Summer 20MVA Projected 2024 Load: Summer 65 MVA
PE-2019-0007 | PE | PJM MA | 2019-07-31 |  |  |  |  | Delaware County, PA | PECO Distribution Planning has been requested to support additional load growth in the Marcus Hook area of Delaware County PA. Initial 2019 Load: 88 MVA ;Projected 2022 Load: 174 MVA
PEP-2019-001 | PEP | PJM MA | 2019-05-31 | 2019-07-31 |  |  |  | Bells Mills Road Substation | Comprehensive inspection revealed deterioration of the following transformers at the Bells Mills Road Substation: Bells Mill Rd T6 230/138 kV (1978), Bells Mill Rd T4 230/138 kV (1962)
PN-2018-001 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1769 |  |  | * Maintenance/rehab work will be performed on the Dubois-Harvey Run-Whetstone 115 kV line. Transmission line rating limited by terminal equipment. * Dubois - Harvey Run 115 kV line: Existing emergency line rating is 179 MVA. Existing conductor emergency rating is 245 MVA. * Harvey Run - Whetstone 115 kV line: Existing emergency line rating is 172 MVA. Existing conductor emergency rating is 245 MVA.
PN-2018-002 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1770 |  |  | * Entire Penn Mar-Rockwood 115 kV line is at or beyond service life. Transmission line loading exceeds 90% under N-1 contingency. * Transmission line rating limited by terminal equipment. * Penn Mar - High Point 115 kV line: Existing emergency line rating is 174 MVA. Existing conductor emergency rating is 179 MVA. * High Point - Rockwood 115 kV line: Existing emergency line rating is the existing conductor emergency rating.
PN-2018-003 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1771 |  |  | * Relays on Garman - Glory 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing emergency line rating is 233 MVA. Conductor emergency rating is 282 MVA.
PN-2018-004 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1772 |  |  | * Planned maintenance on the Homer City - Hooverville 230 kV line results in the interruption of service for a large industrial customer served out of Quemahoning Substation. The line sectionalizing devices at Quemahoning are inadequate to interrupt charging current on the Homer City side of the substation. At Hooversville, the transformer breaker failure scheme utilizes a ground switch on the high side of the 230/115 kV transformer.
PN-2018-005 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1773 |  |  | * At Yeagertown, in the event of a stuck 230 kV bus tie breaker, both 230 kV feeds from Lewistown are outaged, along with two 230-46 kV transformers feeding a large industrial customer and a 230/34.5 kV transformer. * In the current configuration, the 230 kV feeds the 34.5 kV bus via a 230/34.5 kV transformer. The 34.5 kV bus then feeds the 46 kV system via a 46-34.5 kV transformer. This arrangement creates a transmission path through a distribution facility.
PN-2018-006 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1774 |  |  | * A fault on the Seward #9 230/115 kV transformer outages the Seward #11 230/115 kV transformer or a fault on the Seward #11 230/115 kV transformer outages the Seward #9 230/115 kV transformer. * Seward #9 230/115 kV transformer has an increased failure probability due to aging/deteriorating bushings, components and fluid. The transformer was manufactured in 1971.
PN-2018-007 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1775 |  |  | * In the event of a Summit #1 or #2 115-46 kV transformer fault, the line exit breakers and the bus tie breaker are relied upon to clear the fault. The corresponding section of the bus is cleared, creating transfer and thermal issues. * A stuck 115 kV bus tie breaker at Summit will clear the entire 115 kV station. * Summit #1 and #2 115-46 kV transformers have an increased failure probability due to aging/deteriorating bushings, components and fluid. The #1 transformer was manufactured in 1937. The #2 transformer was manufactured in 1971.
PN-2018-008 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1776 |  |  | * Tyrone North 115 kV switching station serves ~50 MW of radial load and relies on breakers at Eagle Valley and Westfall 115 kV substations for remote clearing of fault conditions. Transformer or line faults result in interruption of the entire network path and interruption of service to both the #1 and #2 115-46 kV transformers with limited network transfer capability. In the event of a #1 115-46 kV transformer fault, all load cannot be served by the #2 115-46 kV transformer (the transformer loads to 123% of its 41 MVA summer emergency rating during restoration efforts under peak conditions). * Tyrone North #2 115-46 kV transformer has an increased failure probability due to aging/deteriorating bushings, components and fluid. The transformer was manufactured in 1950.
PN-2018-009 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1777 |  |  | Farmers Valley 115 kV bus #1 does not have a transmission source, while Farmers Valley 115 kV bus #2 has two sources. Bus maintenance or outages result in loss of both 115-34.5 kV transformers impacting approximately 3,377 customers and approximately 10 MW of load.
PN-2018-010 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1778 |  |  | * New Customer Connection - A customer requested 115 kV service for load of approximately 16 MW near the Lenox - Tiffany 115 kV line. Requested in-service date is 7/2019.
PN-2018-011 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1779 |  |  | * Existing terminal equipment significantly derate the thermal capability of the Greenwood - Westfall 46 kV line. The line sectionalizing devices at East Altoona and Fairview are not capable of loop splitting. * Transmission line rating limited by terminal equipment. * Westfall - Fairview 46 kV line: Existing emergency line rating is 69 MVA. Existing conductor emergency rating is 81 MVA * Fairview - East Altoona 46 kV line: Existing emergency line rating is 69 MVA. Existing conductor emergency rating is 71 MVA. * East Altoona - Greenwood 46 kV line: Existing emergency line rating is 33 MVA. Existing conductor emergency rating is 81 MVA.
PN-2018-012 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1780 |  |  | * If both Altoona 230/46 kV transformers out of service (N-1-1), voltage on the surrounding 46 kV system is less than 0.80 p.u.
PN-2018-013 | PN | PJM MA | 2018-09-21 | 2018-10-29 | 2019-02-01 | s1781 |  |  | High voltage on the 230 kV system has been observed at Atlantic substation with either the SVC in-service or out-of-service. The 230 kV voltage at Atlantic substation with the SVC in-service has been measured as high as 1.06 per unit. With the SVC out-of-service the measured system voltage was as high as 1.07 per unit.
PN-2018-014 | PN | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1820 |  |  | Bus section circuit breaker at Edinboro South 115 kV evaluated and determined to be in degraded condition. Since 2006, there have been 10 maintenance orders on this breaker (interrupting media, compressor, and other issues) Transmission line rating limited by terminal equipment. Edinboro South - Erie South 115 kV line: Existing line rating is 163 MVA SN / 185 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE. (line trap, substation conductor, line relaying, CTs) Edinboro South - Venango Junction 115 kV line: Existing line rating is 163 MVA SN / 179 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE. (line trap, substation conductor, line relaying, CTs)
PN-2018-015 | PN | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1821 |  |  | Hill Valley #1 115/46 kV Transformer Transformer has Increased failure probability due to leaks, failed auxiliary equipment and damaged wiring. Transformer is 57 years old. Since 2004, there have been 25 maintenance orders on this transformer.
PN-2018-016 | PN | PJM MA | 2018-10-29 | 2018-11-28 | 2019-07-26 | s1822 |  |  | Lewistown #2 230/115-46 kV Transformer Transformer has an increased failure probability due to leaks and failed auxiliary equipment. Transformer is 65 years old. Since 2004, there have been 96 maintenance orders on this transformer.
PN-2019-001 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Replace East Towanda No.4 230/115 kV Transformer | East Towanda #4 230/115 kV Transformer * Transformer has an increased failure probability due to type “U” bushings, dielectric breakdown, and is exhibiting high ethylene gas. * Transformer is 45 years old. * Approximately $64,000 spent on maintenance orders since 2003. Transformer circuit rating is limited by terminal equipment. Existing transformer circuit rating is 190 / 226 MVA (SN / SE). Existing transformer rating is 195 / 244 MVA (SN / SE). (substation conductor)
PN-2019-002 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Replace Erie South No.6 230/115 kV Transformer | Erie South #6 230/115 kV Transformer * Transformer has an increased failure probability due to type “U” bushings, nitrogen leaks, and is exhibiting an increase in ethylene gas. Power factor test results show deterioration of insulation. * Transformer is 41 years old. * Approximately $821,000 spent on maintenance orders since 2003. Transformer circuit rating is the existing transformer rating of 262/ 326 MVA (SN / SE).
PN-2019-003 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Replace Lewistown No.1 230/115-46 kV Transformer | Lewistown #1 230/115-46 kV Transformer * Transformer has an increased failure probability due to high levels of combustible and ethylene gases and decrease in dielectric strength. * Transformer is 66 years old. * Approximately $137,000 spent on maintenance orders since 2003. Transformer circuit rating is limited by terminal equipment on 46 kV winding. Existing transformer circuit rating is 55 / 67 MVA (SN / SE). Existing transformer rating is 62 / 67 MVA (SN / SE). (disconnect switches, transformer relaying)
PN-2019-004 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Replace Westfall No.3 and No.4 115/46 kV Transformers | Westfall #3 115/46 kV Transformer * Power factor test results show deterioration of windings and bushings. * Transformer is 47 years old. * Approximately $79,000 spent on maintenance orders since 2004. Transformer circuit rating is the existing transformer rating of 38 / 41 MVA (SN / SE). Westfall #4 115/46 kV Transformer * Power factor test results show deterioration of type “U” bushings. * Transformer is 50 years old. * Approximately $18,000 spent on maintenance orders since 2003. Transformer circuit rating is the existing transformer rating of 31 / 34 MVA (SN / SE).
PN-2019-005 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Rebuild Loretto – Sankertown Bypass – Summit 46 kV Line | The Loretto – Sankertown Bypass – Summit 46 kV line is exhibiting deterioration resulting in increased maintenance. The transmission line is approaching end of life. * Total line distance is approximately 5.7 miles * 79 wood structures and 2 towers * Average age of failed structures is 51 years * 81 out of 122 structures failed inspection (66% failure rate) * Failure reasons include sound test, bad/cut/missing grounds, bayonet for static, woodpecker damage, etc. Transmission line rating is the existing conductor rating 32 / 32 MVA (SN / SE).
PN-2019-006 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | East Pike – Glory 115 kV Line terminal equipment | East Pike – Glory 115 kV Line – Terminal equipment is exhibiting an increase risk of failure and due to obsolescence of equipment, spare parts are limited. * At East Pike 115 kV substation – bus section breaker disconnect switches, CVTs, line trap, and surge arresters * At Glory 115 kV substation – line side breaker disconnect switches Transmission line rating is limited by terminal equipment. Existing line rating is 163 / 185 MVA (SN / SE). Existing conductor rating is 202 / 245 MVA (SN / SE). (line trap, substation conductor, CTs)
PN-2019-007 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Lenox – North Meshoppen 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * 1Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-008 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Ridgway – Whetstone 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * 1Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-009 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Union City – Titusville 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * 1Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-010 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Grandview – Titusville 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-011 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Cooper – Seward 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * 1Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-012 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  | Erie South – Union City 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. * 1Line has failed carrier equipment that cannot be repaired or replaced
PN-2019-013 | PN | PJM MA | 2019-02-22 | 2019-03-25 |  |  |  |  | – Titusville 115 kV substation serves approximately 45 MW of load to 5,300 customers. A stuck bus tie breaker at Titusville will outage both #1 and #2 115-34.5 kV transformers and 115 kV network path. Transmission line ratings are limited by terminal equipment. * Union City – Titusville 115 kV line: Existing line rating is 120 / 120 MVA (SN / SE). Existing conductor rating is 202 / 245 MVA (SN / SE) (line relaying, substation conductor, line trap) * Grandview – Titusville 115 kV line: Existing line rating is 147 / 149 MVA (SN / SE). Existing conductor rating is 202 / 245 MVA (SN / SE) (line relaying, substation conductor, line trap)
PN-2019-014 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Rosebud Mining - Twin Rock 46 kV Line Rebuild | Loss of the Garman - Spangler 115 kV (PN-P1-2-PN-115-048) and Ashville - Summit 46 kV line (PN-P1-2-PN-46-014) overloads the Rosebud Mining - Twin Rock 46 kV to 138% of its 32 MVA SE rating. (2018 RTEP Model - 2023 Summer) Operations has performed pre-contingency switching to mitigate overloads on this line during peak summer conditions. Line loading is worsened when Shawville generation is offline or reduced. The overloaded line places approximately 15 MW and 1,600 customers at risk.
PN-2019-015 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Philipsburg 115 kV Ring Bus | Philipsburg 115 kV substation serves approximately 42 MW of load and 18,600 customers. A stuck bus tie breaker at Philipsburg will outage both 115-34.5 kV transformers and 115 kV network path. A fault on the Philipsburg - Shawville 115 kV line outages the #2 115-34.5 kV transformer. Over the past five years, the Philipsburg - Shawville 115 kV line has experienced six sustained outages. Transmission line ratings are limited by terminal equipment. * Philipsburg - Shawville 115 kV line: Existing line rating is 163/185 MVA (SN/SE). Existing conductor rating is 167/202 MVA (SN/SE). (line trap, circuit breaker) * Philipsburg - Eagle Valley 115 kV line: Existing line rating is 137/174 MVA (SN/SE). Existing conductor rating is 201/244 MVA (SN/SE). (CTs, substation conductor / drop, circuit breaker)
PN-2019-016 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Clark Summit 115 kV Ring Bus | Clark Summit 115 kV substation serves approximately 42 MW of load and 11,200 customers. Substation has two transformers and no breakers. A fault on the Eclipse-Clark Summit-Grandview 115 kV line results in loss of line and both distribution transformers. Transmission line ratings are limited by terminal equipment. * Clark Summit - Grandview 115 kV line: Existing line rating is 147/190 MVA (SN/SE). Existing conductor rating is 202/245 MVA (SN/SE). (substation conductor)
PN-2019-017 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Lilly 46 kV Ring Bus | A three terminal line exists at Lilly substation (46 kV) with line exits to Summit, Bethlehem 33 and Jackson Road (normally open at Portage). There is approximately 13 MW of load and 3,200 customers served radially from Jackson Road 46 kV substation. Transmission line ratings are limited by terminal equipment. * Jackson Road - Ampfire Mining 46 kV line: Existing line rating is 24/24 MVA (SN/SE). Existing conductor rating is 67/81 MVA (SN/SE). (line relaying, substation conductor, disconnect switches) * Kokomo Road - Summit 46 kV line: Existing line rating is 25/25 MVA (SN/SE). Existing conductor rating is 32/32 MVA (SN/SE). (line relaying) * Bethlehem 33 - Lilly 46 kV line: Existing line rating is 25/33 MVA (SN/SE). Existing conductor rating is 53/64 MVA (SN/SE). (substation conductor, line relaying)
PN-2019-018 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | 17th Street Substation | Loss of the substation bus at Collinsville substation interrupts ~22 MW of load and 3,290 customers and opens the network connecting sources into the Altoona 46 kV load pocket.
PN-2019-019 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Warrior Ridge 46 kV Expansion | * Warrior Ridge Substation is currently configured as a straight bus. Loss of the bus interrupts ~25 MWs of load with limited transfer capability. * Normally open points exist at Williamsburg, ABW tap, and MacLane (D-Tap) that are established to prevent network flows from Lewistown, Tyrone North, and Altoona. * The system is unable to be networked due to thermal limits of line conductor, terminal equipment, and antiquated directional relaying. * ABW tap is an established three terminal line between Altoona 46 kV, Warrior Ridge 46 kV, and Tyrone North 46 kV substations. * Line switch interrupters are not capable of operational switching such as loop splitting and/or interrupting line charging current. Transmission line ratings are limited by terminal equipment. * Tyrone North - Birmingham 46 kV line: Existing line rating is 33/33 MVA (SN/SE). Existing conductor rating is 53/64 MVA (SN/SE). (line relaying, substation conductor) * Birmingham - Sinking Valley 46 kV line: Existing line rating is 34/44 MVA (SN/SE). Existing conductor rating is 53/64 MVA (SN/SE). (substation conductor) * Alexandria - ABW Tap - Warrior Ridge 46 kV line: Exiting line rating is 55/69 MVA (SN/SE). Existing conductor rating is 59/71 MVA (SN/SE). (disconnect switches) * Williamsburg - ABW Tap - Warrior Ridge 46 kV line: Existing line rating is 25/25 MVA (SN/SE). Existing conductor rating is 49/50 MVA (SN/SE). (line relaying, substation conductor) * Williamsburg REC - Williamsburg 46 kV line: Existing line rating is 25/25 MVA (SN/SE). Existing conductor rating is 49/50 MVA (SN/SE). (line relaying, substation conductor) * Williamsburg - Altoona 46 kV line: Existing line rating is 26/28 MVA (SN/SE). Existing conductor rating is 53/64 MVA (SN/SE). (substation conductor, line relaying) * Warrior Ridge - Center Union 46 kV line: Existing line rating is 17/17 MVA (SN/SE). Existing conductor rating is 59/71 MVA (SN/SE). (line relaying, substation conductor, disconnect switches) * Warrior Ridge - WRH Tap- OC1 Tap - Huntingdon 46 kV: Existing line rating is 22/22 MVA (SN/SE). Existing conductor rating is 93/113 MVA (SN/SE). (line relaying, disconnect switches, substation conductor)
PN-2019-021 | PN | PJM MA | 2019-04-26 | 2019-05-31 |  |  |  | Buffalo Road 115 kV Ring Bus | Buffalo Road 115 kV substation serves approximately 106 MW of load and 3,500 customers. A stuck bus tie breaker at Buffalo Road will outage both 115-34.5 kV transformers and three 115 kV lines. Transmission lines are limited by terminal equipment. * Buffalo Road - Four Mile Junction BRFM2 115 kV Line: Existing line rating is 190/226 MVA (SN/SE). Existing conductor rating is 202/245 MVA (SN/SE). (substation conductor)
PN-2019-022 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Lucerne – Edgewood 115 kV Line, Edgewood – Shelocta 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Lucerne – Edgewood 115 kV Line Edgewood – Shelocta 115 kV Line
PN-2019-023 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | East Pike – Lucerne 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: East Pike – Lucerne 115 kV Line
PN-2019-024 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Jackson Road – Seward 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Jackson Road – Seward 115 kV Line
PN-2019-025 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Armstrong – New Bethlehem 138 kV Line, New Bethlehem – Brookville 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Armstrong – New Bethlehem 138 kV Line New Bethlehem – Brookville 138 kV Line
PN-2019-026 | PN | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  | Shawville – Shingletown 230 kV Line Relays | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Shawville – Shingletown 230 kV Line Exiting line rating: 489/554
PN-2019-027 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Hooversville – Scalp Level 115 kV Line, Scalp Level – Rachel Hill 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Hooversville – Scalp Level 115 kV Line Scalp Level – Rachel Hill 115 kV Line
PN-2019-028 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Penn Tech – Ridgway 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Penn Tech – Ridgway 115 kV Line
PN-2019-029 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Gore Junction – Rolling Meadows 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Gore Junction – Rolling Meadows 115 kV Line
PN-2019-030 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Hill Valley – Shade Gap 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Hill Valley – Shade Gap 115 kV Line
PN-2019-031 | PN | PJM MA | 2019-06-28 | 2019-07-31 |  |  |  | Garman – Spangler 115 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. Transmission Line: Garman – Spangler 115 kV Line
PN-2019-032 | PN | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  | Homer City North 345/230-23 kV Transformer | Homer City North 345/230-23 kV Transformer Transformer has increased failure probability due to: Type “U” bushings High level heating gases and moisture Deteriorated control cabinet components Obsolete parts Leaks Transformer is 51 years old.
PN-2019-033 | PN | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  | Armstrong – Homer City 345 kV line | The Armstrong – Homer City 345 kV line is exhibiting deterioration resulting in increased maintenance. The structures are approaching end of life. The line was originally constructed in 1967. Total line distance is approximately 34.5 miles 167 out of 204 structures failed inspection (82% failure rate) Failure reasons include age, woodpecker damage, top rot, bayonet top, and weatherization.
PN-2019-034 | PN | PJM MA | 2019-07-11 | 2019-08-08 |  |  |  | Elko – Shawville 230 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault. In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. Elko – Shawville 230 kV Line Exiting line rating: 489/554
PPL-2019-001 | PPL | PJM MA | 2019-02-22 |  |  |  |  | Macungie 69 kV Tap | The Macungie 69kV Tap line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1951
PPL-2019-002 | PPL | PJM MA | 2019-02-22 |  |  |  |  | Fairfield 69 kV Tap | The Fairfield 69kV Tap line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1954.
PPL-2019-003 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Beavertown 69kV Tap line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets that were installed in 1962.
PPL-2019-004 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Hauto-Frackville #1 69kV line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1923.
PPL-2019-005 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Sunbury-Lock Haven 69kV line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1949
PPL-2019-006 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Lycoming 2-Muncy Tie 69kV line is a reliability risk due to poor asset health. The line is in poor condition with the majority of the original assets installed in 1954
PPL-2019-007 | PPL | PJM MA | 2019-02-22 | [5 empty] | The Lycoming-Williamsport 1&2 and South Williamsport Tap 1&2 69kV line is a reliability risk due to aging infrastructure and poor asset health. The line is in poor condition with the majority of the original assets installed in 1930.
PPL-2019-008 | PPL | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Long Pond 69/12 kV Substation | PPL Distribution has submitted a request for a second 69 kV transmission source to their Long Pond 69/12 kV substation. Currently there is only one transmission source. The substation serves 12.5 MVA with an expected load addition of 13 MVA in 2020. This load increase will result in dropping customer load to perform maintenance outages.
PPL-2019-009 | PPL | PJM MA | 2019-02-22 | [5 empty] | PPL Distribution has submitted a request for a second 69 kV transmission source to their Cando 69/12kV substation. Currently there is only one transmission source. The substation serves 13.6 MVA with an expected load addition of 3.6 MVA in 2020. This load increase will result in dropping customer load to perform maintenance outages.
PPL-2019-010 | PPL | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Blooming Glen 69/12 kV Substation | PPL Distribution has submitted a request for a second 69 kV transmission source to their Blooming Glen 69/12kV substation. Currently there is only one transmission source. The substation load has increased by 3 MVA and now serves 19.3 MVA. This load increase will result in dropping customer load to perform maintenance outages.
PPL-2019-011 | PPL | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | South Farmersville 69/12 kV Substation | PPL Distribution has submitted a request for a second 69 kV transmission source to their South Farmersville 69/12 kV substation. Currently there is only one transmission source. The substation serves 16.4 MVA with an expected load addition of 3 MVA in 2019. This load increase will result in dropping customer load to perform maintenance outages
PPL-2019-012 | PPL | PJM MA | 2019-02-22 | [5 empty] | PPL Distribution has submitted a request for a second 69 kV transmission source to their Kinzer 69/12 kV substation. Currently there is only one transmission source. The substation load has increased by 2 MVA and now serves 27.3 MVA. This load increase will result in dropping customer load to perform maintenance outages
PPL-2019-013 | PPL | PJM MA | 2019-02-22 | [5 empty] | PPL Distribution has submitted a request for a 69 kV transmission source to their new Gamma 69/12kV substation.
PPL-2019-014 | PPL | PJM MA | 2019-02-22 | [5 empty] | PPL Distribution has submitted a request for a 69 kV transmission source to their new Delta 69/12kV substation
PPL-2019-015 | PPL | PJM MA | 2019-02-22 |  |  |  |  | Ringtown 69 kV Tap | PPL Distribution has submitted a request for a 69 kV transmission source to their new Epsilon 69/12kV substation.
PPL-2019-016 | PPL | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Zeta 69/12 kV Substation | PPL Distribution has submitted a request for a 69 kV transmission source to their new Zeta 69/12kV substation.
PPL-2019-017 | PPL | PJM MA | 2019-02-22 | 2019-04-26 |  |  |  | Eta 138/12 kV Substation | PPL Distribution has submitted a request for a 69 kV transmission source to their new Eta 69/12kV substation.
PPL-2019-018 | PPL | PJM MA | 2019-02-22 |  |  |  |  | Theta 69 kV Tap | PPL Distribution has submitted a request for a 69 kV transmission source to their new Theta 69/12kV substation
PSEG-2018-001 | PSEG | PJM MA | 2018-09-21 | 2018-10-29 | 2018-12-14 | s1752 |  | Hackensack Station Upgrade | Hackensack is supplied by 26kV circuits with increasing performance problems. Over the past decade, the 26 kV supply circuits have seen significant momentary and extended outages, with total duration of hundreds of hours. Station equipment at Hackensack has been in service for over 60 years. This equipment has been identified as being in poor condition and needs to be addressed. Hackensack serves roughly 5,000 customers and 30 MVA of load.
PSEG-2018-002 | PSEG | PJM MA | 2018-09-21 | 2018-10-29 | 2018-12-14 | s1753 |  | Plauderville Station Upgrade | Plauderville is supplied by 26 kV circuits with increasing performance problems: Over the past decade, the 26 kV supply circuits have seen significant momentary and extended outages, with total duration of hundreds of hours. Station equipment at Plauderville has been in service for over 60 years. This equipment has been identified as being in poor condition and needs to be addressed. The station has outdoor metal clad switchgear that has resulted in rust and leaks over time, which causes bus failures. Plauderville serves roughly 3,000 customers and 15 MVA of load. Stations around Plauderville are at or near capacity. There is a need for additional capacity in the area.
PSEG-2018-003 | PSEG | PJM MA | 2018-09-21 | 2019-01-25 | 2019-05-23 | s1823 |  | Reconfigure Walnut Ave 69 kV Substation | Clark is supplied by 26 kV circuits with increasing performance problems: Over the past decade, the 26 kV supply circuits have seen significant momentary and extended outages, with total duration of hundreds of hours, Station equipment at Clark has been in service for over 60 years. This equipment has been identified as being in poor condition and needs to be addressed. The station has outdoor metal clad switchgear that has resulted in rust and leaks over time, which causes bus failures, Clark serves roughly 2,300 customers and 16 MVA of load, Stations around Clark are at or near capacity. There is a need for additional capacity in the area.
PSEG-2018-004 | PSEG | PJM MA | 2018-10-29 | 2018-11-28 | 2019-03-14 | s1787 |  | Reconfigure Lawnside 69 kV Station: | Lawnside is a straight bus fed by four 69 kV lines that serves roughly 24,000 customers and 113 MVA of load: A stuck breaker condition on any of the 69 kV bus section breakers causes the loss of three 69 kV lines and two transformers, leaving the station with only a single 69 kV supply. This results in an unacceptable voltage drop of roughly 7%. Poor circuit performance on the Lawnside-Maple Shade 69 kV circuit: Over the past five years, the Lawnside-Maple Shade 69kV circuit has experienced 11 extended outages and 13 momentary outages, with total duration of over 113 hours.
PSEG-2018-005 | PSEG | PJM MA | 2018-10-29 | 2018-11-28 | 2019-03-14 | s1788 |  | Reconfigure Mount Rose 69 kV station | Poor station reliability at Mount Rose: Mount Rose serves roughly 11,000 customers and 60 MVA of load, Mount Rose experienced station shutdowns due to loss of all 69 kV supply in 2016 and 2018, Over the past decade, the three 69 kV supply circuits at Mount Rose have experienced 21 extended outages and 9 momentary outages, with total duration of over 207 hours. Mount Rose is a straight bus fed by three 69 kV lines. There are several contingencies that would result in unacceptable voltage drops: An N-1-1 condition on 69 kV supplies in the network leaves Mount Rose and several customer substations in the area with only long distance, daisy-chained paths to 230 kV sources. The voltage drops by roughly 7%, A stuck breaker condition on the capacitor bank breaker causes the loss of two 69 kV lines and the capacitor bank, leaving the station with only a single 69 kV supply. The voltage drops by roughly 6%, A stuck breaker condition on the bus section breaker results in the loss of the entire station.
PSEG-2018-006 | PSEG | PJM MA | 2018-11-28 | 2019-01-25 | 2019-05-23 | s1824 |  | Build a new 69kV Substation in North Brunswick | Stations in the New Brunswick area are at or near capacity. There is a need for additional capacity in the area. Adams serves roughly 22,000 customers and 83 MVA of load. Bennetts Lane serves roughly 21,000 customers and 83 MVA of load. Brunswick serves roughly 10,000 customers and 46 MVA of load. Station capacity for each station is 60 MVA, excluding the value of inter-station ties.
PSEG-2018-007 | PSEG | PJM MA | 2018-11-28 | 2019-01-25 | 2019-05-23 | s1825 |  | Build a new 69 kV Substation at Texas Ave. | Stations around Texas Ave are at or near capacity. There is a need for additional capacity in the area. Lawrence: serves roughly 26,000 customers and 121 MVA of load. Texas Ave: a unit substation supplied by two 26 kV circuits with increasing performance problems, Over the past decade, the two 26 kV supply circuits at Texas have experienced 10 extended outages and 32 momentary outages, with total duration of over 82 hours, Station equipment at Texas Ave has been in service for over 60 years. This equipment has been identified as being in poor condition and needs to be addressed. Texas Ave serves roughly 1,000 customers and 5 MVA of load.
PSEG-2019-001 | PSEG | PJM MA | 2019-01-25 | 2019-02-22 | 2019-07-19 | s1831 |  | Build a new 230 kV Substation in Mansfield | Crosswicks and Bustleton are stations at capacity. There is a need for additional capacity in the area. Crosswicks serves roughly 14,900 customer and projected load of 66 MVA in 2024. Bustleton serves roughly 16,400 customers and projected load of 77 MVA in 2024. Station capacity for each station is 60 MVA.

## RevisionHistory
Revision History
12/13/2019 -- V2 -- Corrected the 34 records as indicated below.
09/06/2019 -- V1 -- Original posting
Need Number | Project Name (Correct) | Project Description (Correct) | Project Name (originally posted) | Project Description (originaly posted)
AEP-2018-OH016 | Strasburg, Ohio | The Beartown- West Wilmont 69kV section 10.5 miles long and serves 1 AEP Ohio distribution station and 2 1 Holmes-Wayne Co-op station in northeast Ohio. Over the past several years, the circuit has experienced below-average reliability. For the 2017-2018 YTD period, it has experienced 7 sustained outages, an additional 8 momentary interruptions, and 2 emergency repair incidents on the entire circuit. The majority of the outages were due to T-Line structural issues and forestry. The line section consists of primarily 336 ACSR (1962-64 vintage); it is entirely wood pole construction, with the majority being installed in the 1960’s. The section has a reported CMI of 2.0M between 2014 – 2018 and currently has 52 open conditions (25 Category A, 25 Category B, 5 Forestry). Examples of the conditions include: rotted poles, missing ground-leads, and damaged conductor. During the 2010-2018 period, 112 prior conditions were repaired/addressed on the circuit as a whole. | Roseville, Ohio | The Beartown- West Wilmont 69kV section 10.5 miles long and serves 1 AEP Ohio distribution station and 2 1 Holmes-Wayne Co-op station in northeast Ohio. Over the past several years, the circuit has experienced below-average reliability. For the 2017-2018 YTD period, it has experienced 7 sustained outages, an additional 8 momentary interruptions, and 2 emergency repair incidents on the entire circuit. The majority of the outages were due to T-Line structural issues and forestry. The line section consists of primarily 336 ACSR (1962-64 vintage); it is entirely wood pole construction, with the majority being installed in the 1960’s. The section has a reported CMI of 2.0M between 2014 – 2018 and currently has 52 open conditions (25 Category A, 25 Category B, 5 Forestry). Examples of the conditions include: rotted poles, missing ground-leads, and damaged conductor. During the 2010-2018 period, 112 prior conditions were repaired/addressed on the circuit as a whole.
AEP-2019-IM035 | South Bend, Indiana & Michigan Area | South Bend – Niles 69 kV Line (~11.47 Miles) •1968 vintage wood pole construction •Forced Momentary outages: 5 •Forced Permanent outages: 3 •Total structure related open conditions – 47 •Unique structure count with open conditions – 44 •Insect Damage, Rotten Poles, Broken/Burnt cross-arm, Woodpecker holes, broken/burnt insulators, stolen/broken ground wires, broken guy strain insulators and cracked stub pole. •More than three in-line sectionalizing MOABS |  | South Bend – Niles 69 kV Line (~11.47 Miles) *1968 vintage wood pole construction *Forced Momentary outages: 5 *Forced Permanent outages: 3 *Total structure related open conditions – 47 *Unique structure count with open conditions – 44 *Insect Damage, Rotten Poles, Broken/Burnt cross-arm, Woodpecker holes, broken/burnt insulators, stolen/broken ground wires, broken guy strain insulators and cracked stub pole. *More than three in-line sectionalizing MOABS
BG-2019-0003 | Edgewood-Perryman 115 kV circuits | The Edgewood-Perryman 115 kV circuits 110620, 110621 have three lattice towers with deteriorating pile and cap foundation and significant contamination of insulators, conductors, tower steel and foundations. | Theta 69kV Tap | The Edgewood-Perryman 115kV circuits 110620, 110621 have three lattice towers with deteriorating pile and cap foundation and significant contamination of insulators, conductors, tower steel and foundations.
ME-2018-013 | Middletown Junction 230/69 kV transformer No.3 | Middletown Junction No,3 230/69 kV: Transformer is 55 years old There have been 44 maintenance orders since 2003 Multiple oil leaks in load tap changer Combustible gasses found in load tap changer oil | North Hershey - Turf Club 69 kV Line Rehab/Rebuild | Middletown Junction #3 230-69 kV: Transformer is 55 years old There have been 44 maintenance orders since 2003 Multiple oil leaks in load tap changer Combustible gasses found in load tap changer oil
ATSI-2019-073 | Eastlake-Lloyd 138 kV Q12 Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -73 ¦ Eastlake-Lloyd 138 kV Q12 Line ¦ 103 / 132 ¦ 148 / 151 ¦ Substation Conductor, Relay, CTs @ Lloyd ¦ | Eber-Swanton 138 kV Line | FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. Proper operation of the protection scheme requires all the separate components perform adequately during a fault In many cases the protection equipment cannot be repaired due to a lack of replacement parts and available expertise in the outdated technology. Transmission line ratings are limited by terminal equipment. ¦ATSI-2019 ¦ Transmission Line / Substation Locations ¦ Existing Line/Terminal Equipment MVA Rating (SN / SE) ¦ Existing Conductor/Transformer MVA Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ -73 ¦ Eastlake-Lloyd 138 kV Q12 Line ¦ 103 / 132 ¦ 148 / 151 ¦ Substation Conductor, Relay, CTs @ Lloyd ¦
ATSI-2019-083 | Harding - Jennings 138 kV lines | Existing Customer Connection - Service Modification - The existing customer requested modification to their current 138 kV transmission service. - The request is to move some of their existing load from the Harding - Jennings Q13 138 kV line to the Harding - Jennings Q11 138 kV line. This request is not for a load increase, but will result in a system topology change. Requested In-Service Date: 02/01/2020 | LTV East Steel Customer- Need | Existing Customer Connection - Service Modification - The existing customer requested modification to their current 138 kV transmission service. - The request is to move some of their existing load from the Harding - Jennings Q13 138 kV line to the Harding - Jennings Q11 138 kV line. This request is not for a load increase, but will result in a system topology change. Requested In-Service Date: 02/01/2020
ME-2018-002 | Hill-Tolna 115 kV line rehab | Maintenance/rehab work will be performed on the Hill-Tolna 115 kV line. Transmission line rating limited by terminal equipment. * Hill - Johnson Controls 115 kV line: Existing emergency line rating is 150 MVA. Existing conductor emergency rating is 223 MVA. * Johnson Controls - Tolna 115 kV line: Existing emergency line rating is 208 MVA. Existing conductor emergency rating is 223 MVA. | Baldy - South Hamburg 69 kV Line Rehab/Rebuild | Maintenance/rehab work will be performed on the Hill-Tolna 115 kV line. Transmission line rating limited by terminal equipment. * Hill - Johnson Controls 115 kV line: Existing emergency line rating is 150 MVA. Existing conductor emergency rating is 223 MVA. * Johnson Controls - Tolna 115 kV line: Existing emergency line rating is 208 MVA. Existing conductor emergency rating is 223 MVA.
ME-2018-003 | Pleasureville-Harley Davidson-York Solid Waste 115 kV line rehab | Maintenance/rehab work will be performed on the Pleasureville-Harley Davidson-York Solid Waste 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Harley Davidson 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 430 MVA. * Harley Davidson - York Inc. 115 kV line: Existing emergency rating is 263 MVA. Existing conductor emergency rating is 282 MVA. | North Temple - North Kill 69 kV Line Rehab/Rebuild | Maintenance/rehab work will be performed on the Pleasureville-Harley Davidson-York Solid Waste 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Harley Davidson 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 430 MVA. * Harley Davidson - York Inc. 115 kV line: Existing emergency rating is 263 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-004 | Pleasureville-Mt. Rose-Violet Hill 115 kV line rehab | Maintenance/rehab work will be performed on the Pleasureville-Mt. Rose-Violet Hill 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Mt. Rose 115 kV line: Existing emergency line rating is the existing conductor emergency rating. * Mt. Rose - Violet Hill 115 kV line: Existing emergency line rating is 266 MVA. Existing conductor emergency rating is 282 MVA. | Carsonia - South Reading 69 kV Line Rehab/Rebuild | Maintenance/rehab work will be performed on the Pleasureville-Mt. Rose-Violet Hill 115 kV line. Transmission line rating limited by terminal equipment. * Pleasureville - Mt. Rose 115 kV line: Existing emergency line rating is the existing conductor emergency rating. * Mt. Rose - Violet Hill 115 kV line: Existing emergency line rating is 266 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-005 | Smith Street-Westgate-York Solid Waste 115 kV line rehab | Segments of Smith Street-Westgate-York Solid Waste 115 kV line are at or beyond service life. Transmission line rating limited by terminal equipment. * Smith Street - Smith Street Tap 115 kV line: Existing emergency line rating is 152 MVA. Existing conductor emergency rating is 223 MVA. * Westgate - Smith Street Tap 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 282 MVA. * York Inc. - Smith Street Tap115 kV line: Existing emergency line rating is the existing conductor emergency rating. | East Topton - North Boyertown 69 kV Line Rehab/Rebuild | Segments of Smith Street-Westgate-York Solid Waste 115 kV line are at or beyond service life. Transmission line rating limited by terminal equipment. * Smith Street - Smith Street Tap 115 kV line: Existing emergency line rating is 152 MVA. Existing conductor emergency rating is 223 MVA. * Westgate - Smith Street Tap 115 kV line: Existing emergency line rating is 263 MVA. Existing conductor emergency rating is 282 MVA. * York Inc. - Smith Street Tap115 kV line: Existing emergency line rating is the existing conductor emergency rating.
ME-2018-006 | Windsor-Yorkana Tap 115 kV line rehab | Maintenance/rehab work will be performed on the Windsor-Yorkana Tap 115 kV line. Relays on Windsor - Yorkana 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or in a degraded condition. Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Existing conductor emergency rating is 282 MVA. | Alcoa - South Lebanon 69 kV Line Rehab/Rebuild | Maintenance/rehab work will be performed on the Windsor-Yorkana Tap 115 kV line. Relays on Windsor - Yorkana 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or in a degraded condition. Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Existing conductor emergency rating is 282 MVA.
ME-2018-007 | Hunterstown - Jackson 230 kV line relays | * Relays on Hunterstown - Jackson 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 678 MVA. Conductor normal rating is 709 MVA. | Bernville - South Hamburg 69 kV Line Rehab/Rebuild | * Relays on Hunterstown - Jackson 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 678 MVA. Conductor normal rating is 709 MVA.
ME-2018-008 | Tolna - Windsor 115 kV line relays | * Relays on Tolna - Windsor 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Conductor emergency rating is 282 MVA. | Middletown Junction - Swatara Hill - Campbelltown 69 kV Line Rehab/Rebuild | * Relays on Tolna - Windsor 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing emergency line rating is 277 MVA. Conductor emergency rating is 282 MVA.
ME-2018-009 | Mountain - P.P.G.I. 115 kV line relays | * Relays on Mountain - P.P.G.I. 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 159 MVA. Conductor normal rating is 184 MVA. | Middletown Junction - Smith Street 115 kV Line Rehab/Rebuild | * Relays on Mountain - P.P.G.I. 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 159 MVA. Conductor normal rating is 184 MVA.
ME-2018-010 | Jackson - Yorkana 230 kV line relays relays | * Relays on Jackson - Yorkana 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 650 MVA. Conductor normal rating is 709 MVA. | Allentown Cement - Lyons - South Hamburg 69 kV Line Rehab/Rebuild | * Relays on Jackson - Yorkana 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 650 MVA. Conductor normal rating is 709 MVA.
ME-2018-011 | Middletown Junction - Smith Street (978) 230 kV line relays | * Relays on Middletown Junction - Smith Street (978) 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 103 MVA. Conductor normal rating is 129 MVA. | North Temple - South Hamburg 69 kV Line Rehab/Rebuild | * Relays on Middletown Junction - Smith Street (978) 230 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 103 MVA. Conductor normal rating is 129 MVA.
ME-2018-012 | Pleasureville - Violet Hill 115 kV line relays | * Relays on Pleasureville - Violet Hill 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 204 MVA. Conductor normal rating is 232 MVA. | Alcoa - Broad Street 69 kV Line Rehab/Rebuild | * Relays on Pleasureville - Violet Hill 115 kV line evaluated by Transmission Planning and Protection and determined to be obsolete and/or degraded condition. * Transmission line rating limited by terminal equipment. Existing normal line rating is 204 MVA. Conductor normal rating is 232 MVA.
ME-2018-014 | Broad Street - West Lebanon 69 kV line relays | Relays on Broad Street - West Lebanon 69 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 71 MVA SN / 91 MVA SE. Existing conductor rating is 111 MVA SN / 134 MVA SE. (substation conductor and disconnect switches) | Birdsboro - South Reading 69 kV Line Rebuild/Rehab | Relays on Broad Street - West Lebanon 69 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 71 MVA SN / 91 MVA SE. Existing conductor rating is 111 MVA SN / 134 MVA SE. (substation conductor and disconnect switches)
ME-2018-015 | Hokes - Smith St, Hokes - Lehigh Cement, & Hokes - Jackson 69 kV lines relays | Relays on Hokes - Smith St, Hokes - Lehigh Cement, & Hokes - Jackson 69 kV lines evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Hokes - Jackson 69 kV line: Existing line rating is 51 MVA SN / 56 MVA SE. Existing conductor rating is 53 MVA SN / 56 MVA SE. (substation conductor | North Boyertown - Ringing Rocks 69 kV Line Rebuild/Rehab | Relays on Hokes - Smith St, Hokes - Lehigh Cement, & Hokes - Jackson 69 kV lines evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Hokes - Jackson 69 kV line: Existing line rating is 51 MVA SN / 56 MVA SE. Existing conductor rating is 53 MVA SN / 56 MVA SE. (substation conductor
ME-2018-016 | Hunterstown - North Hanover 115 kV line relays | Relays on Hunterstown - North Hanover 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 232 MVA SN / 277 MVA SE. Existing conductor rating is 232 SN / 282 MVA SE. (line trap) | Cleona - West Lebanon 69 kV Line Rebuild/Rehab | Relays on Hunterstown - North Hanover 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 232 MVA SN / 277 MVA SE. Existing conductor rating is 232 SN / 282 MVA SE. (line trap)
ME-2018-018 | Hunterstown - Gardners 115 kV line relays | Relays on Hunterstown - Gardners 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 163 MVA SN / 185 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE. (line trap, breaker, CTs, relay, and substation conductor) | Kittatinny - Portland 230 kV Relay Replacement | Relays on Hunterstown - Gardners 115 kV line evaluated and determined to be obsolete and/or degraded condition. Transmission line rating limited by terminal equipment. Existing line rating is 163 MVA SN / 185 MVA SE. Existing conductor rating is 232 MVA SN / 282 MVA SE. (line trap, breaker, CTs, relay, and substation conductor)
ME-2018-019 | Jackson 230/115 kV transformer No.5 | Jackson #5 230/115 kV: * Transformer is 48 years old * Dissolved gas in oil * History of oil leaks, compromising oil integrity | South Lebanon - Myerstown 69 kV Line Rehab/Rebuild | Jackson #5 230/115 kV: * Transformer is 48 years old * Dissolved gas in oil * History of oil leaks, compromising oil integrity
ME-2018-020 | North Hershey 230-69 kV transformer No.1 | North Hershey #1 230-69 kV: * Transformer is over 40 years old * Critical role in operation of 69 kV * Transformer leaking | North Lebanon - Turf Club 69 kV Line Rehab/Rebuild | North Hershey #1 230-69 kV: * Transformer is over 40 years old * Critical role in operation of 69 kV * Transformer leaking
ME-2019-037 | Hill 115 kV Ring Bus | * The loss of Hill substation results in loss of approximately 30 MW of load and approximately 7800 customers. * Two 115 kV lines * Two distribution transformers connected to transmission with switches | Delaware County PA Area | * The loss of Hill substation results in loss of approximately 30 MW of load and approximately 7800 customers. * Two 115 kV lines * Two distribution transformers connected to transmission with switches
PN-2019-006 | East Pike – Glory 115 kV Line terminal equipment | East Pike – Glory 115 kV Line – Terminal equipment is exhibiting an increase risk of failure and due to obsolescence of equipment, spare parts are limited. * At East Pike 115 kV substation – bus section breaker disconnect switches, CVTs, line trap, and surge arresters * At Glory 115 kV substation – line side breaker disconnect switches Transmission line rating is limited by terminal equipment. Existing line rating is 163 / 185 MVA (SN / SE). Existing conductor rating is 202 / 245 MVA (SN / SE). (line trap, substation conductor, CTs) | Upgrade Terminal Equipment on the East Pike – Glory 115 kV Line | East Pike – Glory 115 kV Line – Terminal equipment is exhibiting an increase risk of failure and due to obsolescence of equipment, spare parts are limited. * At East Pike 115 kV substation – bus section breaker disconnect switches, CVTs, line trap, and surge arresters * At Glory 115 kV substation – line side breaker disconnect switches Transmission line rating is limited by terminal equipment. Existing line rating is 163 / 185 MVA (SN / SE). Existing conductor rating is 202 / 245 MVA (SN / SE). (line trap, substation conductor, CTs)
PN-2019-036 | Eagle Valley – Westfall 115 kV line Rehab | The Eagle Valley – Westfall 115 kV line is exhibiting deterioration resulting in increased maintenance. The structures are approaching end of life. The line was originally constructed in 1956. * Total line distance is approximately 20.7 miles * 147 out of 154 structures failed inspection (95% failure rate) * Failure reasons include age, woodpecker damage, cracking, and decay. | Queenstown area | The Eagle Valley – Westfall 115 kV line is exhibiting deterioration resulting in increased maintenance. The structures are approaching end of life. The line was originally constructed in 1956. * Total line distance is approximately 20.7 miles * 147 out of 154 structures failed inspection (95% failure rate) * Failure reasons include age, woodpecker damage, cracking, and decay.
PN-2019-037 | Seward –Tower 51 115 kV Line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ PN-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ 037 ¦ Seward –Tower 51 115 kV Line ¦ 147/185 ¦ 201/244 ¦ Circuit Breaker, Line Relaying, Line Trap, Substation Conductor ¦ | Eagle Valley – Westfall 115 kV line | * FirstEnergy has identified protection schemes using a certain vintage of relays and communication equipment that have a history of misoperation. * Proper operation of the protection scheme requires all the separate components perform adequately during a fault. * In many cases the protection equipment cannot be repaired due to a lack of replacement part and available expertise in the outdated technology. * Transmission line ratings are limited by terminal equipment. ¦ PN-2019- ¦ Transmission Line / Substation Locations ¦ Existing Line Rating (SN / SE) ¦ Existing Conductor Rating (SN / SE) ¦ Limiting Terminal Equipment ¦ ¦ 037 ¦ Seward –Tower 51 115 kV Line ¦ 147/185 ¦ 201/244 ¦ Circuit Breaker, Line Relaying, Line Trap, Substation Conductor ¦
PPL-2019-009 |  | PPL Distribution has submitted a request for a second 69 kV transmission source to their Cando 69/12kV substation. Currently there is only one transmission source. The substation serves 13.6 MVA with an expected load addition of 3.6 MVA in 2020. This load increase will result in dropping customer load to perform maintenance outages. | Long Pond 69/12 kV Substation | PPL Distribution has submitted a request for a second 69 kV transmission source to their Cando 69/12kV substation. Currently there is only one transmission source. The substation serves 13.6 MVA with an expected load addition of 3.6 MVA in 2020. This load increase will result in dropping customer load to perform maintenance outages.
AEP-2018-AP021 | Baltimore/Lancaster, Ohio | Baltimore 69kV CBs E and F are oil type breakers (vintage 1951) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB E (5), CB F (5). Baltimore currently has 20 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Lancaster 69kV CBs B and D are oil type breakers (vintage 1989) and have been identified for replacement due to lack of spare part availability, historical reliability, and lack of vendor support. Oil breakers are difficult to maintain due to oil handling requirements. Oil spills can occur during maintenance and fixes. The breakers have experienced the following fault operations: CB B (4), CB D (18). Lancaster currently has 46 electro-mechanical relays employed. EM relays have limited vendor support, lack SCADA functionality, and don’t offer fault data collection. | Floyd County, Kentucky | 69 kV circuit breakers ‘B’ and ‘E’ at Morehead are CF-48 oil type breakers that were manufactured in 1967. These are oil breakers that have become more difficult to maintain due to the required oil handling. There is an increased potential for oil spills during routine maintenance and failures with these types of breakers. Other drivers include damage to bushings and an excessive number of fault operations exceeding the manufacturers recommendations. Morehead breakers ‘B’ and ‘E’ have experienced 42 and 97 fault operations respectively. The manufacturer’s recommendation for this type of breaker is 10. From 2013-2018 the Morehead – Morgan County 69 kV circuit (~ 20 miles) has experienced 29 momentary and permanent outages. The 21 mile 69 kV line section between Morehead and Index has 255 category A open conditions associated with the structures and conductors that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. The majority of this circuit utilizes 1950s wood structures and 3/0 ACSR conductor
AEP-2018-AP022 | Coshocton, Ohio | Cyclops 69kV circuit switcher A is currently being used as a line CB. This model has limited spare parts availability and reliability concerns. This circuit switcher has also experienced 41 fault operations. Cyclops 69kV CB B is an oil type breaker (vintage 1955) that has exceeded the manufacturers recommended number of fault operations (36 total faults). Oil breakers are difficult to maintain due to oil handling requirements. Oil spill can occur during maintenance and fixes. Cyclops station currently has 19 electro-mechanical relays employed. EM relays have limited spare part availability, a lack vendor support, no SCADA functionality, and no fault data collection ability. Cyclops station is currently built upon a four-pole wooden bay that is progressively deteriorating. |  | From 2013-2018 the Prestonsburg - Thelma 46 kV circuit (~ 16 miles) has experienced 22 momentary and permanent outages. The circuit has 34 category A open conditions associated with the structures that make up the line. These conditions include damaged/rotted poles and damaged guy wires, cross arms. The majority of this circuit utilizes 1960s wood structures and 336.4 ACSR conductor
AEP-2019-IM037 | South Bend, Indiana Area | Torrington Tap 34kV Line (~1 mile): wood pole line, 2 open conditions. This trend is expected to increase as the structures and conductor age. | Torrington Tap 34kV Line (~1 mile) * Wood pole line * 2 open conditions. This trend is expected to increase as the structures and conductor age. | Equipment Material Condition, Performance and Risk;
AEP-2019-AP032 | Pike County, Kentucky | Equipment Material/Condition/Performance/Risk: The 46 kV transmission Cedar Creek – Elwood 46kV circuit (~15.5 miles) is 1966 Vintage and has 81 open conditions. The majority of open conditions are structure related including rot top/shell, woodpecker and burnt damage. The two permanent outages on this circuit have caused 176,728 CMI over the past five years. Also over this time span, there have been 18 momentary outages. | Pike County, Kentucky | Medford – Blaine Street (~3.3 Miles) 1940’s vintage wood crossarm construction with cap and pin insulators There are currently 40 open conditions on this line. This trend is expected to increase as the structures and conductor age. Medford – Haymond (section in question is Medford – near 21st Street ~3.3 miles) 1940’s vintage wood crossarm construction with cap and pin insulators There are currently 29 open conditions on this segment of the line. This trend is expected to increase as the structures and conductor age. Haymond – Blaine Street (~3.7 miles) 1950’s vintage wood crossarm construction with cap and pin insulators There are currently 7 open conditions on this segment of the line. This trend is expected to increase as the structures and conductor age.
COMED-2019-006 | Quad Cities | 345 kV Line 0402 (Quad Cities – Cordova) has obsolete relays. Becoming difficult to service REL352 phase comparison relays. They are being phased out of our system. Line is an intertie between PJM/MISO. | Quad Cities | * 138 kV line 4605 is a three-terminal line * TSS 46 Des Plaines * TSS 198 Des Plaines * TDC 207 Tonne (future Elk Grove) * Elk Grove project B2941 will cut into the line * The current configuration is very difficult to relay properly due to unequal lengths of the three legs
COMED-2019-007 | Kendall - Lockport | Network project n5144 is rebuilding 345 kV Kendall – Lockport double circuit towers for 16 miles in 2022 to increase line 10805 rating. New conductor will be T2-1113 (1448 MVA SN/1863 MVA SE). 345 kV Line 10806 runs in parallel on the same towers. Existing conductor is 2156 kcm(1334 MVA SN/1726 MVA SE). The disconnect switch at Lockport is a non-standard 1600 A switch. 138 kV lines 0908 (Joliet – Shorewood) and 9117 (Shorewood – Cargo Court) run along the same ROW for 10.5 miles on wood poles. The wood poles are 59-60 years old. ComEd intends to eliminate wood poles on the transmission system. | Kendall - Lockport | * 138 kV line 4605 is a three-terminal line * TSS 46 Des Plaines * TSS 198 Des Plaines * TDC 207 Tonne (future Elk Grove) * Elk Grove project B2941 will cut into the line * The current configuration is very difficult to relay properly due to unequal lengths of the three legs