## Setup and context links
Enter Stakeholder Group Name in cell A2:
MIC Special Session
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Distributed Energy Resources
Link to Problem Statement
http://www.pjm.com/~/media/committees-groups/committees/mrc/20160526/20160526-item-10-distributed-battery-storage-problem-statment-proposed-revision.ashx
Link to Issue Charge
http://www.pjm.com/~/media/committees-groups/committees/mrc/20160418-special/20160418-item-02a-distributed-battery-storage-issue-charge-revised-1,-d-,28,-d-,16-clean.ashx
Link to IssueTracking
http://www.pjm.com/committees-and-groups/issue-tracking/issue-tracking-details.aspx?Issue={FCADF6DC-FA84-4F5E-9B33-DE2428F47A2B}

## WORK PLAN
DER Subcommittee | [10 empty] | 2017 2017 2017 | [20 empty] | 2018
Wholesale DER (W-DER)
Ancillary Services
Energy
Capacity
Non-wholesale DER observability
Review of Utility-owned Microgrids
Triennial Review Timing | 2012-07-01 | 2012-08-01 | 2012-09-01 |  | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01
üProvide Education
üProblem Investigation
üProposal Development
üBuild Consensus
üFirst Read @ MRC | [5 empty] | 2012-11-29
üVote at MRC | [6 empty] | 2012-12-20
üVote at MC
Multi-Year Pricing Mechanism | 2012-07-01 | 2012-08-01 | 2012-09-01 |  | 2012-10-01 | 2012-11-01 | 2012-12-01 | 2013-01-01 | 2013-02-01 | 2013-03-01
üProvide Education
üRefine Interests
üDevelop & Refine Design Components
üDevelop & Refine Component Options
üDevelop & Refine Solution Packages
üBuild Consensus
üFirst Read @ MRC | [7 empty] | 2013-01-31
Vote at MRC | [8 empty] | 2013-02-28
Vote at MC | [8 empty] | 2013-02-28
FERC Filing | [9 empty] | 2013-03-01
Updated: December 15, 2017
Detailed Work Plan -- Wholesale DER | 6.26 | 7.17 | 7.31 | 8.9 | 8.26 | 8.28 | 9.9 | 9.18 | 9.24 | 9.26 (MRC) | Special MRC 6.17.16 | Special MRC 8.24.16 | Special MRC 10.12.16 | Special MIC 12.16.16 | Special MIC 2.01.17 | Special MIC 3.02.17 | Special MIC 4.10.17 | Special MIC 5.01.17 | Special MIC 5.19.17 | Special MIC 6.01.17 | Special MIC 6.20.17 | Special MIC 7.07.17 | Special MIC 8.01.17 | Special MIC 8.18.17 | Special MIC 8.31.17 | Special MIC 9.18.17 | Special MIC 10.04.17 | Special MIC 10.18.17 | Special MIC 11.3.17 | Special MIC 11.17.17 | DERS 12.15.17 | DERS 01.5.18 | DERS 01.31.18 | DERS 03.02.18 | DERS 04.25.18 | DERS 06.08.18 | DERS 06.29.18 | DERS 07.30.18 | DERS 08.27.18 | DERS 10.4.18 | DERS 10.31.18 | DERS 11.30.18
Create Subcommittee Charter and Approval |  | x | x | x |  | x | x | [19 empty] | x | x | x | x |  | Start Capacity
Provide Education |  |  | x | [7 empty] | x | x | x | x | x |  |  |  |  | x |  | x |  |  | x | x | x |  |  |  |  | x | x
Document Interests |  |  |  | x |  | x | x | [6 empty] | x
Develop & Refine Design Components | [5 empty] | x | x |  | x |  |  |  |  | x | x | x | [9 empty] | x | x |  |  |  |  | x | x | x
Develop & Refine Component Options | [15 empty] | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
Develop & Refine Solution Packages | [21 empty] | x | x | x |  |  |  | x | x | x | x |  |  |  |  | x | x | x
Build Consensus | [35 empty] | x | x | x
Subcommittee Vote | [38 empty] | x
Detailed Work Plan -- non-Wholesale DER Observability | [31 empty] | DERS 01.5.18 | DERS 01.31.18 | DERS 03.02.18 | DERS 04.25.18 | DERS 06.08.18 | DERS 06.29.18 | DERS 07.30.18 | DERS 08.27.18 | DERS 10.4.18 | DERS 10.31.18 | DERS 11.30.18
Provide Education | [31 empty] | x | x
Document Interests | [32 empty] | x
Develop & Refine Design Components | [32 empty] | x | x | x
Develop & Refine Component Options | [33 empty] | x | x
Develop & Refine Solution Packages | [35 empty] | x | x
Build Consensus | [37 empty] | x
Subcommittee Vote | [38 empty] | x
Detailed Work Plan -- Utility-owned Microgrids | [31 empty] | DERS 01.5.18 | DERS 01.31.18 | DERS 03.02.18 | DERS 04.25.18 | DERS 06.08.18 | DERS 06.29.18 | DERS 07.30.18 | DERS 08.27.18 | DERS 10.4.18 | DERS 10.31.18 | DERS 11.30.18
Provide Education | [35 empty] | x | x
Document Interests | [35 empty] | x | x
Develop & Refine Design Components
Develop & Refine Component Options
Develop & Refine Solution Packages
Build Consensus
Subcommittee Vote

## Definitions
Defining “Distributed Energy Resource” for the Purposes of the MIC Special Session on DER The purpose of these definitions is to establish a common understanding of the term for this stakeholder group and its proceedings. It is not to codify the term in PJM governing documents or business manuals. This definition is PJM-specific, and will likely differ from other definitions established by FERC, NERC, and other industry organizations. Distributed Energy Resource is a generation or electric energy storage resource connected at distribution voltages and/or connected behind a load meter*. Aggregation: "bringing together multiple separate DER units into one resource”. Wholesale DER (W-DER): a DER unit participating in PJM markets under the (to be determined) “W-DER” ruleset. *Note: for the purposes of the MIC sessions on DER, this definition does not include load reduction. This exclusion may be revisited as necessary.

## 1. Interest Identification
MIC Special Session
Distributed Energy Resources
Interest Identification
| Category | Addressed by solution package? Y/N/Partially | Interests
1 | Access to Markets / Barrier Removal |  | Fair and open access to markets
2 | Access to Markets / Barrier Removal |  | Design components to address issues with DER retail customer participation in any PJM wholesale market, e.g., interconnection studies, requirements, etc., should reflect an appropriate size threshold that would exclude individual retail customers with non-significant loads, e.g., less than 100kW, unless included in an aggregation.
3 | Access to Markets / Barrier Removal |  | Participation in any PJM wholesale market should only be the result of a voluntary and/or affirmative choice of each participating individual retail customer.
4 | Access to Markets / Barrier Removal |  | DERs can participate in all PJM markets to the limits of their technical capability.
5 | Access to Markets / Barrier Removal |  | Clear, non-discriminatory rules for determining energy and capacity injection rights.
6 | Access to Markets / Barrier Removal |  | Support for the widest possible variety of ownership arrangements.
7 | Access to Markets / Barrier Removal |  | Clear and efficient processes and requirements for resources to enter PJM markets.
8 | Grid Ops |  | Safe and reliable operations of grid
9 | Grid Ops |  | Efficient use of assets
10 | Grid Ops |  | Blindly dispatching resources without seeing all constraints should be carefully considered as it could impact system reliability and safety.
11 | Grid Ops |  | Visibility of system constraints and coordination around them is critical to bulk transmission dispatch and it should not be ignored when dispatching resources on the distributions system.
12 | Grid Ops |  | Many distribution companies are currently evaluating the benefits/cost of grid modernization with their respective state regulators. Regional differences should be respected as close coordination between entities is required to ensure the delivery of safe and reliable electricity.
13 | Jurisdiction of DER |  | Any results from this stakeholder process should not interfere or alter the jurisdictional authority of state or local regulatory commissions over individual retail customers and/or their transactions with public utilities that are regulated by a state or local jurisdictional regulatory authority.
14 | Jurisdiction of DER |  | Any FERC–state/local regulatory conflicts arising from any results from this stakeholder process must be resolved before implementation.
15 | Jurisdiction of DER |  | Any results from this stakeholder process should not interfere or alter the privacy of retail customers as customers of public utilities regulated by a state or local regulatory authority.
16 | Jurisdiction of DER |  | Participation should be subject to relevant state or local rules and regulations.
17 | Jurisdiction of DER |  | PJM rules limited to enforcing wholesale market provisions while coordinating with non-wholesale state laws and regulations.
18 | Jurisdiction of DER |  | Clear delineation between EDC and PJM responsibilities in whatever rules are developed.
19 | Jurisdiction of DER |  | DER must observe all jurisdictional boundaries including interconnection standards.
20 | Market Rules & Req's |  | Framework that is capable of working with future market products.
21 | Market Rules & Req's |  | Comparable requirements and obligations of DER to existing supply-side generation and storage.
22 | Market Rules & Req's |  | Rules made with awareness of open FERC DER NOPR: https://www.ferc.gov/whats-new/comm-meet/2016/111716/E-1.pdf
23 | Market Rules & Req's |  | Administrative simplicity.
24 | Market Rules & Req's |  | Resources should be rewarded for their value (and costs) to the system which requires dispatch incentive tied to local constraints. Resources should be compensated for services they provide to the grid. Conversely, if resources consume grid services, they should pay for services consumed.
25 | Miscellaneous |  | Agree on a consistent definition of DER
26 | Settlements / Accounting |  | Appropriate accounting
27 | Settlements / Accounting |  | Design components to implement aggregation should rely on metered versus estimated values of service(s) provided.
28 | Settlements / Accounting |  | Capturing retail end-use kWh for proper retail energy accounting.

## 2. Options Matrix- Design Comp.
|  | Updated: December 13, 2017 Print Format: 11 x 17" | MIC Special Session--Distributed Energy Resources--OPTIONS MATRIX
|  | Design Components |  | Status Quo |  |  | Solution Options
| # | Phase I Scope: DER providing ancillary services and/or wholesale energy | Priority | Demand Response framework: "behind the customer meter DER" | Generation framework: "Front of meter DER" (see Figure 1 in Tab 2a) | Generation framework: "behind the customer meter DER" (See Figure 2 in Tab 2a) | A | B | C | D | E | F | G
| 1 | Market participation and engineering study requirements for injections beyond the POI to the distribution or transmission system for participation in PJM markets. (This requirement applies only for wholesale DER that inject. Does not apply to retail-only net energy metering)
Physical Interconnection and Wholesale Market Participation Agreement | 1.1 | DER market participation approval process |  | Approved Curtailment Service Provider registration for aggregation or single resource | Wholesale Market Participation Agreement (WMPA) or Interconnection Service Agreement (ISA) per-unit | WMPA or ISA per-unit | New market participation agreement for DER aggregation or single resource, analogous to WMPA or ISA. Agreement gets filed with FERC. Not tied to network cost/engineering study. EDC signatory to agreement. Meet requirements in 1.2 | Assuming no transmission impacts, new DER registration process analogous to CSP registration today under "Status Quo Demand Response". Not filed with FERC. Meet requirements in 1.2
| 1.2 | Network engineering study |  | No PJM study. Possible EDC study per-unit. | On a per-location basis: WMPA: PJM studies all transmission and some distribution, EDC studies some transmission and all distribution. ISA: PJM studies all transmission and all distribution. | On a per-location basis: WMPA: PJM studies all transmission and some distribution, EDC studies some transmission and all distribution. ISA: PJM studies all transmission and all distribution. | PJM queue process that is separated from the market agreement process. Queue process handles necessary network upgrades. State interconnection agreement required for state-jurisdiction connection facilities | Retail customers that are allowed to inject power under applicable retail tariffs need no further interconnection studies to participate in PJM markets, consistent with retail customer injection rights. | State-jurisdictional interconnection agreement with PJM study of transmission impacts
| 2 | Wholesale market measurement, accounting, and associated metering points. |  | behind the customer meter | Auxiliary connection from generator to load, with appropriate metering and physical switching of generator and load. (E.g., transfer switches for operation only during grid outage). | behind the customer meter. Meter at delivery point.
Behind the customer meter only | 2A.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail |  | Synch Reserve: Customer baseline Regulation: Direct reading of load meter, or submeter where approved | N/A | Injections at the POI measured for performance | Option to directly meter DER (i.e. Sub-meter). TBD rules to ensure performance is zeroed out if disconnected from grid. | Existing Demand Response measurement method extended to include negative loads.
| 2A.2 | PJM Energy Market: Method to measure wholesale energy vs ordinary end-use retail energy (e.g. kWh / MWh) |  | Customer Baseline layers wholesale on top of retail (no exports allowed) | N/A | Withdrawals are retail, injections are wholesale | Withdrawals are retail, injections are wholesale | Virtual separation w/ EDC approval: Single retail and wholesale connection to DER with meters at the POI and DER. Virtual separation of wholesale and retail activity via meter add-backs. | Existing DR measurements extended to include negative loads. | Existing DR measurements for load reductions, existing Gen measurements for injections | Generator output is always metered as an injection regardless of whether its DER or DR (always submeter the generator) | Option for no wholesale settlement of injected energy. Customers with retail meters that record injections, and customers that have retail compensation for injected energy, will not be settled at wholesale for injected energy. This option would apply to Ancillary Service-only resources.
| 2A.3 | Method to measure self-supplied station power vs. retail-purchased station power. |  | None | N/A | No remote or interremopral self-supply of station power unless specially arranged with EDC. | No remote or interremopral self-supply of station power unless specially arranged with EDC.
| 2A.4 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot |  | Customer Baseline layers wholesale on top of retail (no exports allowed) | N/A | Imports are retail, exports are wholesale
Front of meter | 2B.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail |  | N/A | Point of interconnection meter | N/A | Directly meter DER. For DER behind the customer meter, this looks like a sub-meter. TBD rules to ensure performance is zeroed out if disconnected from grid. | Existing Demand Response measurement method extended to include negative loads.
| 2B.2 | Method to measure retail vs. wholesale energy for primarily front of the meter resources that occasionally serve load |  | N/A | Station Power, provided that on-site non-station power load only served during grid outage | N/A | Station Power given compliance with restrictions on PJM Capacity and Energy resources serving loads | Non-fleet Station Power: fleet netting is not allowed for Front of Meter DER with a pigtail that can directly serve adjacent load. If it meets the PJM definition of Station Power (e.g., power used for plant equipment), monthly net consumption at DER POI is a retail purchase of station power. Front of meter DER with a pigtail may not directly serve adjacent load using power withdrawn from the grid. DER may only directly serve load if consistent with state rules and laws. | Physical Separation: Physically separate retail and wholesale connections to DER with meters on each connection. | Virtual separation: Single retail and wholesale connection to DER with meters at the POI and DER. Virtual separation of wholesale and retail activity via meter add-backs. | Not applicable, measurement of retail energy is not in PJM's jurisdiction.
| 2B.3 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot |  | N/A | Appropriate metering and physical switching from wholesale connection to retail connection | N/A
| 3 | Aggregation rules (per-unit size = "maximum market offer quantity" as implied in Section 2A/B.1 and 2A/B.2)
| 3.1 | Size-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) |  | No minimum DER size. Max of one 100+ kW DER per aggregate. Minimum aggregate size of 100 kW. | No minimum DER size. No maximum aggregate size. Minimum aggregate size of 100 kW. | No minimum DER size. No maximum aggregate size. Minimum aggregate size of 100 kW. | For behind the customer meter resources, as current DR rules extended to cover injections. | Similar to DR except in front of meter if injecting. Size component corresponds to injection capability
| 3.2 | Size-related rules for aggregation related to maximum market size limit |  | No maximum aggregate size | No maximum aggregate size. | No maximum aggregate size. | As determined by distribution system operator based on the limitations of the facilities | 5MW | 10MW | 1MW
| 3.3 | Location-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) |  | Generally follows locational features of market. Generally by EDC, in some cases by LSE or by node | Same electrical location | Same electrical location | Same as Demand Response for both DER wired separate from load and DER behind the customer meter | Same as DR for DER behind the customer meter | If injecting then same electrical location (POI), if not injecting then same as DR | If injecting then same transmission/PJM electric location (POI), EDC may have aggregation location rules of its own for DER connected to their distribution system. If not injecting then same as DR | EDC determines geographic location/boundaries of aggregation. | Has to be within same EDC
| 3.4 | Ancillary Services: rules for aggregation for PJM market Performance Compliance purposes |  | SR: measured across the RTO based on what was dispatched (i.e., MAD, non-MAD, RTO). Reg: option to use generic rules for market (e.g., resource specific or Performance Group), or use Dispatch Group (limited to TO boundary and energy price point) | SR: <description pending> Reg: generic rules for market (e.g., resource specific or Performance Group) | SR: <description pending> Reg: generic rules for market (e.g., resource specific or Performance Group)
| 4 | Approval processes
| 4.1 | DER unit approval process |  |  |  |  | For any retail jurisdiction(s) that provides for, and/or requires, the injections of energy from electric vehicles to be credited as net energy metering, the metering configuration must be provided to the RERRA for review and acceptance and a certification of the RERRA’s response must be provided to PJM by the owner/operator/aggregator of the DER. | For new DER units: EDC confirms basic site details are correct when DER can serve a retail customer account (either directly or through pigtail(s) or both) for each retail customer served. 10 business days to confirm. | For changes to existing DER units: EDC confirms basic site details are correct when DER can serve a retail customer account (either directly or through pigtail or both) for each retail customer served. 10 business days to confirm. DER unit details can only be changed with EDC approval. DER unit must continue to meet market obligations even if changes are declined. | For new DER units that intend to sell PJM Regulation, or existing DER units that intend to start selling PJM Regulation for the first time, EDC reliability approval is required. EDC has 30 days to provide reliability approval or decline. New DER units that announce their intent to sell Regulation in their interconnection application, and are approved for interconnection, are deemed to have EDC reliability approval for providing Regulation.
| 4.2 | Aggregation approval process |  |  |  |  | For new DER aggregations: EDC approves aggregations when multiple DER units are on the same or adjacent feeder. | For changes to existing DER aggregations: EDC approves aggregations when multiple DER units are on the same or adjacent feeder. DER aggregation must continue to meet market obligations even if changes are declined.
| 4.3 | Who ensures each site is properly implemented for metering configuration and meter data arithmetic? Which jurisdiction oversees appropriate metering configuration, implementation, and meter data arithmetic? |  | PJM responsibility | N/A | Interconnecting TO (or EDC) ensures each site is properly implemented under jurisdictional oversight as per the interconnection agreement. | Where retail and wholesale load/services occur at the same point of interconnection, the metering configuration must be provided to the RERRA for review and acceptance, and a certification of the RERRA’s response must be provided to PJM by the owner/operator of the DER. | For Energy and Capacity Interconnecting TO (or EDC) ensures each site is properly implemented under jurisdictional oversight as per the interconnection agreement. PJM ensures each site is properly implemented and has oversight over Ancillary Services.
| 5 | Delegation of market relationship: unit owner<> PJM (presence of intermediary) |  | Curtailment Service Provider always represents DR in market | Marketer may represent DER in market through commercial arrangements | Marketer may represent DER in market through commercial arrangements | DER Provider always represents DER in market (analogous to Status Quo Demand Response) | EDC acts as intermediary
| 6 | Hardware requirements for meter and related hardware (for market participation) |  | Existing retail meter, except where approved, a PJM-spec sub meter. Reg requires real-time metering and comms. | Meter that meets PJM spec; SCADA that meets TO spec. Reg and Capacity requires real-time metering and comms. | Meter that meets PJM spec; SCADA that meets TO spec. Reg and Capacity requires real-time metering and comms. | Existing DR requirements by market, extended to properly meter negative loads. | For DER aggregates: telemetry, if required, is a single stream for the entire aggregate representing the sum of the associated values. Market Seller is responsible for maintaining 2 years of per-unit telemetry data of at least a 10-second sample rate for auditing purposes. | To be eligible for wholesale energy settlement, Behind the Customer Meter DER must have unidirectional wholesale metering that records only the sum of power injections, and must have unidirectional retail metering that records only the sum of power withdrawals. | For Behind The Customer Meter DER with retail settlements for energy injections that do not participate in the capacity market, PJM requirements for metering related to energy and Capacity are waived. Only PJM requirements for ancillary services metering and telemetry are applicable. | For DER aggregates: telemetry, if required, is a single stream for the entire aggregate representing the sum of the associated values. Market Seller is responsible for maintaining 6 months of per-unit telemetry data of at least a 10-second sample rate for auditing purposes.
| 7 | Framework (participation model) |  | DR | Generation | Generation | DER (If not otherwise specified, use Generation rules, e.g. for telemetry) | DER Mobile
| 8 | Wholesale DER observability requirements when performing non-wholesale activity |  | <<DAILY?>> Report curtailment for emergency DR | None | None | Schedule non-wholesale activity DA and intraday, minimum 20 min lead time, telemetry
| 9 | Solution Implementation Details |  | N/A | N/A | N/A
| 10 | RERRA (Relevant Electric Retail Regulatory Authority) coordination |  |  |  |  | State opt-out only for behind the customer meter | As set by interconnection tariff
| 11 | EDC Coordination |  | Via TO coordination and PJM Emergencies Procedures page | By telephone via TO or via Market Seller | By telephone via TO or via Market Seller | DER day-ahead schedules are shared with EDC upon request | DER telemetry, if it is required by PJM, is shared with EDC upon request (if EDC does not already have telemetry). | List and basic details for DER in EDC territory is available to EDC
| 12 | Miscellaneous Market Rules |  | NA | NA | NA | For settlements of injected energy, DER in aggregate must all use retail or all use wholesale. | For Aggregations: ex ante MW weighting across nodes for the energy offers is adjustable with offer. Ex post, settlements are based on actual PowerMeter submissions per DER unit. | For Wholesale DER that directly serve load at one or more customers, either BTCM or via pigtail(s) or both, the load reduction at each respective customer must be measured at hourly intervals to 1% accuracy and provided to PJM post-facto. For Wholesale DER <= 10kW, the load reduction may be estimated rather than directly measured. PJM will add back the load reduction for the purposes of planning. PJM will also make the load reduction available to EDCs for potential add back in allocation Network Service Peak Load charges (aka, 1CP) and Capacity charges (aka, 5CP). | DER must be online when providing Synchronized Reserve and otherwise follow the rules of Generators providing Synch Reserve, including resource-specific rules for availability for Tier I estimates. | No energy offer and no lost opportunity cost for DER that are submetered for ancillary services. | No energy offer, self scheduling to sell energy, and no lost opportunity cost for DER that settle injected energy at retail. | No Estimated Tier I Synch for submetered DER or DER settled at retail for injected energy. (They may offer as a Tier II Synch resource).
|  | Non-wholesale DER observability requirements |  | Some operational and planning related requirements for certain types of gen (e.g. BTMG >10MW, must have telemetry) | Some operational and planning related requirements for certain types of gen (e.g. BTMG >10MW, must have telemetry) | Some operational and planning related requirements for certain types of gen (e.g. BTMG >10MW, must have telemetry)
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.
This item has been deferred. PJM will address with stakeholders later in 2017 at the appropriate venue.

## 2a. Design Component Details
MIC Special Session
Distributed Energy Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Header |  | Detailed Description
| Status Quo generation (including storage): DER wired separate from load (see Figure 1 in Tab 2a) "dedicated wholesale generator" | A DER that is connected to the grid separately from any retail load. All retail activity runs through a dedicated retail meter that generally does not register any DER activity. E.g., see Figure 1 at right.
| Status Quo generation (including storage): DER wired with load behind metering (See Figure 2 in Tab 2a) "behind the meter wholesale generator" | A DER that shares a connection to the grid with retail load. The output of such a DER would first offset retail load, and then any excess would be injected past metering hardware onto the grid. See Figure 2 at right.
Design Component |  | Detailed Description
1 | Market participation and engineering study requirements for injections beyond the POI to the distribution or transmission system for participation in PJM markets. (This requirement applies only for wholesale DER that inject. Does not apply to retail-only net energy metering) | What type of interconnection approval process is required to participate in the market.
1.1 | DER market participation approval process | What type of market participation agreement contract (and under what jurisdiction) is entailed as part of the resource set-up process (incl. the interconnection process if applicable). Options for this design component could specify whether the market participation agreement covers a single DER or an aggregate of DERs.
1.2 | Network engineering study | What type of engineering study is entailed as part of the resource set-up process (incl. the interconnection process if applicable). Options for this design component could specify whether the engineering study covers a single DER or an aggregate of DERs; who has jurisdiction to handle disputes, set deadlines, set screening processes, and determine cost allocation procedures; and/or whether the jurisdiction over the study will vary based on a transmission vs. distribution interconnection point?
2 | Wholesale market measurement, accounting, and associated metering points. | Some wholesale DER are configured to be able to serve retail load. If so, this describes the method.
2A.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail | PJM Ancillary Services are Regulatoin and Synch Reserve. There are no retail equivalents--they are transmission-only services.
2A.2 | PJM Energy Market: Method to measure wholesale energy vs ordinary end-use retail energy (e.g. kWh / MWh) | If the DER can serve both wholesale and retail purposes, this describes the method for measuring and accounting for the different activities.
2A.3 | Method to measure self-supplied station power vs. retail-purchased station power. | Station power is either purchased (at retail) or self supplied. In general, station power self supply can be both interremporal (via monthly netting) and/or remote (via fleet netting). OATT: “Station Power” shall mean energy used for operating the electric equipment on the site of a generation facility located in the PJM Region or for the heating, lighting, air-conditioning and office equipment needs of buildings on the site of such a generation facility that are used in the operation, maintenance, or repair of the facility. Station Power does not include any energy (i) used to power synchronous condensers; (ii) used for pumping at a pumped storage facility; (iii) used for compressors at a compressed air energy storage facility; (iv) used for charging an Energy Storage Resource or a Capacity Storage Resource; or (v) used in association with restoration or black start service.
2A.4 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot
2B.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail | PJM Ancillary Services are Regulatoin and Synch Reserve. There are no retail equivalents--they are transmission-only services.
2B.2 | Method to measure retail vs. wholesale energy for primarily front of the meter resources that occasionally serve load | If the DER can serve both wholesale and retail purposes, this describes the method for measuring and accounting for the different activities.
2B.3 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot
3 | Aggregation rules (per-unit size = "maximum market offer quantity" as implied in Section 2A/B.1 and 2A/B.2) | Aggregation means: bringing together multiple separate units into one resource.
3.1 | Size-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) | Describes the size rules associated with aggregating multiple DER into a single, effectively indivisible market entity, especially for the purposes of meeting the 100 kW minimum size threshold for participating in PJM markets.
3.2 | Size-related rules for aggregation related to maximum market size limit | Describes the size rules associated with aggregating multiple DER into a single, effectively indivisible market entity, especially for the purposes of meeting the 100 kW minimum size threshold for participating in PJM markets.
3.3 | Location-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) | Describes the rules and limits to the locational breadth associated with aggregating multiple DER into a single, effectively indivisible market entity, especially for the purposes of meeting the 100 kW minimum size threshold for participating in PJM markets.
3.4 | Ancillary Services: rules for aggregation for PJM market Performance Compliance purposes | Performance Group rules for Reg (via Manual 12 Section 4.5.7) Resources may elect to use a performance group for performance score evaluation. Performance groups can only be created for resources that satisfy one of the following criteria: • Resources not eligible for LOC and total to less than or equal to 10 MWs across Transmission Owner boundaries. • A performance group can be any number of resources not eligible for LOC inside a transmission owner’s boundary. • Resources within a fleet with equivalent applicable offers and point of interconnection.
4 | Approval processes | Approval steps in addition to the network engineering-related items in the interconnection process.
4.1 | DER unit approval process | Approval for each individual DER unit, i.e. at a single site.
4.2 | Aggregation approval process | Approval for an aggregation of multiple DER units
4.3 | Who ensures each site is properly implemented for metering configuration and meter data arithmetic? Which jurisdiction oversees appropriate metering configuration, implementation, and meter data arithmetic?
5 | Delegation of market relationship: unit owner<> PJM (presence of intermediary) | If it is possible to have an intermediary between the DER owner/operator and the PJM markets, who is that intermediary?
6 | Hardware requirements for meter and related hardware (for market participation) | What rules govern the hardware specifications for meters and telemetered communications for use in PJM markets and operations?
7 | Framework (participation model) | For any rules that are not explicitly stated in a package: rules from which market access framework should govern? E.g., rules from the generation framework vs. the demand response framework.
8 | Wholesale DER observability requirements when performing non-wholesale activity
9 | Solution Implementation Details
10 | RERRA (Relevant Electric Retail Regulatory Authority) coordination
11 | EDC Coordination
12 | Miscellaneous Market Rules
Figure 1
Figure 2
"Pigtail": Potential Connection To Adjacent Load (PCTAL)
DER BEHIND THE CUSTOMER METER

## 2b. Option Details
MIC Special Session
Distributed Energy Resources
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description

## 3. Packages
|  | Updated: November 8, 2017 Print Format: 11 x 17" | MIC Special Session--Distributed Energy Resources--OPTIONS MATRIX
|  | Design Components |  | Status Quo |  |  | Packages
| # | Phase I Scope: DER providing ancillary services and/or wholesale energy | Priority | Demand Response framework: "behind the customer meter DER" | Generation framework: "Front of meter DER" (see Figure 1 in Tab 2a) | Generation framework: "behind the customer meter DER" (See Figure 2 in Tab 2a) | A (PJM Strawman) | B | C | D
| 1 | Market participation and engineering study requirements for injections beyond the POI to the distribution or transmission system for participation in PJM markets. (This requirement applies only for wholesale DER that inject. Does not apply to retail-only net energy metering)
| 1.1 | DER market participation approval process |  | Approved Curtailment Service Provider registration for aggregation or single resource | Wholesale Market Participation Agreement (WMPA) or Interconnection Service Agreement (ISA) per-unit | WMPA or ISA per-unit | Status Quo Generation framework: "behind the customer meter DER"
| 1.2 | Network engineering study |  | No PJM study. Possible EDC study per-unit. | On a per-location basis: WMPA: PJM studies all transmission and some distribution, EDC studies some transmission and all distribution. ISA: PJM studies all transmission and all distribution. | On a per-location basis: WMPA: PJM studies all transmission and some distribution, EDC studies some transmission and all distribution. ISA: PJM studies all transmission and all distribution. | Status Quo Generation framework: "behind the customer meter DER"
| 2 | Wholesale market measurement, accounting, and associated metering points. |  | behind the customer meter | Auxiliary connection from generator to load, with appropriate metering and physical switching of generator and load. (E.g., transfer switches for operation only during grid outage). | behind the customer meter. Meter at delivery point.
Behind the customer meter only | 2A.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail |  | Synch Reserve: Customer baseline Regulation: Direct reading of load meter, or submeter where approved | N/A | Injections at the POI measured for performance | Option A: Either measure at POI, or option to directly meter DER (i.e. Sub-meter). TBD rules to ensure performance is zeroed out if disconnected from grid due to a distribution system outage.
| 2A.2 | PJM Energy Market: Method to measure wholesale energy vs ordinary end-use retail energy (e.g. kWh / MWh) |  | Customer Baseline layers wholesale on top of retail (no exports allowed) | N/A | Withdrawals are retail, injections are wholesale | Option A: Withdrawals are retail, injections are wholesale
| 2A.3 | Method to measure self-supplied station power vs. retail-purchased station power. |  | None | N/A | No remote or interremopral self-supply of station power unless specially arranged with EDC. | Option A: No remote or interremopral self-supply of station power unless specially arranged with EDC.
| 2A.4 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot |  | Customer Baseline layers wholesale on top of retail (no exports allowed) | N/A | Imports are retail, exports are wholesale | PARKING LOT
Front of meter | 2B.1 | PJM Ancillary Services: Method to measure wholesale activity and performance Note: PJM Ancillary Services are wholesale only, no need to distinguish wholesale from retail |  | N/A | Point of interconnection meter | N/A | Option A: Either measure at POI, or option to directly meter DER (i.e. Sub-meter). TBD rules to ensure performance is zeroed out if disconnected from grid.
| 2B.2 | Method to measure retail vs. wholesale energy for primarily front of the meter resources that occasionally serve load |  | N/A | Station Power, provided that on-site non-station power load only served during grid outage | N/A | Option B: All energy is either wholesale or station power. Non-fleet Station Power: fleet netting is not allowed for Front of Meter DER with a pigtail that can directly serve adjacent load. If it meets the PJM definition of Station Power (e.g., power used for plant equipment), monthly net consumption at DER POI is a retail purchase of station power. Front of meter DER with a pigtail may not directly serve adjacent load using power withdrawn from the grid. DER may only directly serve load if consistent with state rules and laws.
| 2B.3 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot |  | N/A | Appropriate metering and physical switching from wholesale connection to retail connection | N/A | PARKING LOT
| 3 | Aggregation rules (per-unit size = "maximum market offer quantity" as implied in Section 2A/B.1 and 2A/B.2)
| 3.1 | Size-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) |  | No minimum DER size. Max of one 100+ kW DER per aggregate. Minimum aggregate size of 100 kW. | No minimum DER size. No maximum aggregate size. Minimum aggregate size of 100 kW. | No minimum DER size. No maximum aggregate size. Minimum aggregate size of 100 kW. | Same as Status Quo Demand Response: No minimum DER size. Max of one 100+ kW DER per aggregate. Minimum aggregate size of 100 kW.
| 3.2 | Size-related rules for aggregation related to maximum market size limit |  | No maximum aggregate size | No maximum aggregate size. | No maximum aggregate size. | Option D: 1 MW
| 3.3 | Location-related rules for aggregation to meet minimum market size threshold of 100 kW (many to one) |  | Generally follows locational features of market. Generally by EDC, in some cases by LSE or by node | Same electrical location | Same electrical location | Option F: has to be within same EDC
| 3.4 | Ancillary Services: rules for aggregation for PJM market Performance Compliance purposes |  | SR: measured across the RTO based on what was dispatched (i.e., MAD, non-MAD, RTO). Reg: option to use generic rules for market (e.g., resource specific or Performance Group), or use Dispatch Group (limited to TO boundary and energy price point) | SR: <description pending> Reg: generic rules for market (e.g., resource specific or Performance Group) | SR: <description pending> Reg: generic rules for market (e.g., resource specific or Performance Group) | Same as Status Quo Generation
| 4 | Approval processes
| 4.1 | DER unit approval process |  |  |  |  | Options B+C+D
| 4.2 | Aggregation approval process |  |  |  |  | Options A+B
| 4.3 | Who ensures each site is properly implemented for metering configuration and meter data arithmetic? Which jurisdiction oversees appropriate metering configuration, implementation, and meter data arithmetic? |  | PJM responsibility | N/A | Interconnecting TO (or EDC) ensures each site is properly implemented under jurisdictional oversight as per the interconnection agreement. | Option B: For Energy and Capacity Interconnecting TO (or EDC) ensures each site is properly implemented under jurisdictional oversight as per the interconnection agreement. PJM ensures each site is properly implemented and has oversight over Ancillary Services.
| 5 | Delegation of market relationship: unit owner<> PJM (presence of intermediary) |  | Curtailment Service Provider always represents DR in market | Marketer may represent DER in market through commercial arrangements | Marketer may represent DER in market through commercial arrangements | Status quo Generation
| 6 | Hardware requirements for meter and related hardware (for market participation) |  | Existing retail meter, except where approved, a PJM-spec sub meter. Reg requires real-time metering and comms. | Meter that meets PJM spec; SCADA that meets TO spec. Reg and Capacity requires real-time metering and comms. | Meter that meets PJM spec; SCADA that meets TO spec. Reg and Capacity requires real-time metering and comms. | Options B+C+D
| 7 | Framework (participation model) |  | DR | Generation | Generation | Option A: DER (If not otherwise specified, use Generation rules, e.g. for telemetry)
| 8 | Wholesale DER observability requirements when performing non-wholesale activity |  | <<DAILY?>> Report curtailment for emergency DR | None | None | TBD
| 9 | Solution Implementation Details |  | N/A | N/A | N/A | TBD
| 10 | RERRA (Relevant Electric Retail Regulatory Authority) coordination |  |  |  |  | TBD
| 11 | EDC Coordination |  | Via TO coordination and PJM Emergencies Procedures page | By telephone via TO or via Market Seller | By telephone via TO or via Market Seller | Options A+B+C
| 12 | Miscellaneous Market Rules |  | NA | NA | NA | Options A+B+C+D+E+F+G
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 3a. Package Details
MIC Special Session
Distributed Energy Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
MIC Special Session
Distributed Energy Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description
Special study for regulation resources on the distribution system (Dave Pratzon)
Add design component on eligibility
Size or cutoff
Sites with multiple connections to the grid and with islanding optionality (including "microgrids") can introduce significant complexity.
"Wired with load" might be construed to include "virtual load" in the case of community solar or virtual net metering.
2.3 | Method to measure retail vs. wholesale energy for primarily front of the meter resources that occasionally serve load (Parking Lot) | N/A | Station Power, provided that on-site non-station power load only served during grid outage | N/A | Station Power given compliance with restrictions on PJM Capacity and Energy resources serving loads | Monthly net consumption is retail (similar to Station Power, but no "remote self supply"). | Physical Separation: Physically separate retail and wholesale connections to DER with meters on each connection. | Virtual separation: Single retail and wholesale connection to DER with meters at the POI and DER. Virtual separation of wholesale and retail activity via meter add-backs. | Not applicable, measurement of retail energy is not in PJM's jurisdiction.
2.4 | Method to separate and measure retail vs. wholesale activity (CAPACITY) Parking Lot | Customer Baseline layers wholesale on top of retail (no exports allowed) | Appropriate metering and physical switching from wholesale connection to retail connection | Imports are retail, exports are wholesale
10/18/2017 - Air permits consideration
11/6/2017 - Need to understand how deviation charges might be impacted

## Revision History
MIC Special Session
Distributed Energy Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1 | 2016-11-21 | First draft for initial consideration by stakeholders
2 | 2016-12-16 | Second draft after discussion at Dec 16 stakeholder meeting
3