## Proposal Matrix
Order 2222 Compliance Proposal Matrix This matrix will be used to track PJM's preferred solutions and alternative options to comply with the directives in Order 2222.
| Updated: September 15, 2021 | Area Dependencies | Order 2222 - DER Aggregation Participation Model | [5 empty] | Demand Response (DR) (No Injection) | Generation (Small Gen) | Dual Model (DR+DER, with injection)
| High level requirement | Column1 | Draft Proposal | Alternate Approach 1 | Alternate Approach 2 | Alternate Approach 3 | Alternate Approach 4 | Alternate Approach 5 | Status Quo | Status Quo | Status Quo
| Model Overview |  | The DER Aggregation (DERA) market participation model will augment existing small generation and demand response participation models in order to comply with FERC Order 2222 and enhance wholesale market access options for small DER that will not inject onto the transmission system. Distributed energy resources participating as part of a DERA will not go through the PJM queue, will be allowed to aggregate with other resources who share a common primary transmission node to form a single market unit, and will be eligible to participate in capacity, energy, and ancillary services where technically feasible. |  |  |  | The model should also have a participation option for all forms of DER technologies. Right now, it seems that behind the meter solar would not have a participation option. PJM should include a participation option for this fast growing resource. |  | Allows all technologies and methods that can change load to participate in the wholesale markets (Gen, Batteries, arc furnace curtailment, residential load control, etc.). The DR model only allows payment for change in load and does not compensate for injection past the retail meter (or in the case of a muni, the muni meter(s)) | Traditional model where all units go through the interconnection queue prior to participation in the wholesale markets. Units receive CIRs and may be a Capacity unit or an Energy Only unit. Some Capacity resources have capacity market must offer requirements. All capacity resources have energy market must offer requirements, market mitigation and are modelled in the EMS (state estimator). Some interconnection provisions allow for expedited processing in the queue. | DER that is oversized for the customer's retail load can participate as both DR and Gen at the same time. The portion used to offset load is handled with the DR model and the portion that injects is handled with the Generation model. One caveat- Regulation market, once interconnection study is done for the injection, the entire amount is handled under the DR rules.
1 | Interconnection Jurisdiction: the Commission declined to exercise its jurisdiction over the interconnections of DERs to distribution facilities for the purpose of participating in RTO/ISO markets exclusively as part of a DER Aggregation. | State/Local/Utility DER Interconnection tariffs and process | State/local interconnection agreement (IA) process only; FERC's "first use" test to determine jurisdiction of an interconnecting wholesale generator does not apply to DER using the DERA model; DER owner must have a valid IA with distribution utility which allows for wholesale market participation; Only DER that require an interconnection agreement per RERRA / utility requirements will need this validated during the DER registration process; DER must not inject onto the transmission system; PJM queue process still available for DER who will inject onto transmission or who would prefer existing generation/storage model. | [5 empty] | No PJM Interconnection study process for DR, study process/requirements are at the utility/state level. DR in PJM needs to go through registration process. | Must go through PJM Interconnection queue. All capacity resources are Att N; 5MW or less inverter based and 2 MW or less synchronous are Att Y, and 10kW or less are Att BB | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
2 | Jurisdiction: the Commission declined to exercise its jurisdiction over the interconnections of DERs to distribution facilities for the purpose of participating in RTO/ISO markets exclusively as part of a DER aggregation. Transmission System Planning | DERA Registration/ DER data collection process | The impact of DER interconnected solely through state interconnection processes must be adequately represented in PJM power flow models for transmission planning purposes. As such, PJM will need the following information for each DER within a DER Aggregation: – Address – Technology (solar, battery, landfill gas, wind, hybrid, etc.) – Maximum AC output (gross nameplate capability) – Interconnected distribution line identification (used for Quality Assurance only, not modeling of distribution system). - PJM Planning Model Bus ID distribution line is fed from – Ride through capability enabled? Y/N – Voltage control enabled? Y/N • Both Aggregator and Electric Distribution Company will verify data annually | [5 empty] | Jurisdiction over interconnection is at state level. | Sign WMPA or ISA | Portion that is Gen (Injection) would sign WMPA or ISA
3 | Opt-in for Small Utilities: do not accept bids for aggregators in utilities < 4millon MWh/year unless utility allows opt-in. | REERA | All small utility DERs wanting to participate in a DERA will need to provide opt-in evidence from RERRA. Order 2222 Opt-in process would apply to the following resources: FTM generator, energy storage, and energy efficiency resources All resources within a heterogeneous aggregation. | [5 empty] | All DR goes through EDC review process where each EDC is defined as "small" or "large" based on 4 million threshold. The EDC is responsible to interpret RERRA to approve or deny participation in the market. PJM publically posts all RERRA evidence used to approve, qualify or deny. | No opt-in review for generation resources. | Dual Model will go through the EDC review process.
3a | Resources subject to opt-in/opt-out under DR rules | REERA | DR Opt-in/Opt-out process would apply to the following resources: - Demand Response (load curtailment) resources participating in a DERA - Resources participating with load curtailment and injections in PJM Markets - Demand Response participating in a heterogeneous DERA
4 | Participation Model: all DER Aggregation to participate in markets under 1 or more participation model and accommodate physical and operational impacts. |  | Existing Demand Response participation model remains unchanged, and can accommodate DER behind a load customer's meter that will not inject beyond the customer's load meter. New DERA participation model will expand aggregation opportunities to one or more small individual DER (e.g., <5MW) connected to the distribution system both behind a load meter and in front of the meter. |  |  |  | First, the model will also allow a DER that has both on-site load curtailment and injection (e.g. a customer who has a low PLC due to solar and the ability to reduce load and that injects when they reduce load) to participate under one continuous model that compensates for both on-site load curtialment and injection, as FERC has approved in NYISO and ISO-NE. Second, residential DR is not accomodated under PJM's current DR participation rules. The requirement that each resource be matched to its utility account number creates a barrier to participation, contrary to the intent of Order No. 2222. Submetering or direct metering is critical to residential DER participation. However, it is unclear if PJM's existing DR model rules or its current proposal allows for this flexibility. |  | DR (behind the meter DER, no injection) | Generator market rules, and ESR participation model | Behind the meter/DER that has the capability to inject can go through the interconnection process and have the injection amount treated as front of the meter generation (must offer, etc.). Regulation solely operates under DR model
5 | Distribution Factors & Bidding Parameters: distributed energy resource aggregators give to the RTO/ISO the total distributed energy resource aggregation response that would be provided from each DER resource in the aggregation, and incorporate appropriate bidding parameters into its participation models. | Locational Requirements | PJM will not be using weighting factors for DERAs. | [5 empty] | CSPs have flexibility to aggregate to a resource and such aggregation opportunities vary a little by market. CSPs provide the individual customers that will be participating in the market prior to operations. Distribution factors provided to PJM after the fact. During the settlement process data is provided to detail how much load response was provided by each customer. To address bidding parameters, CSPs can use multi-point curve of aggregate offers. | Aggregation beyond the plant level is typically not allowed. Telemetry on each individual resource at the plant (distribution factor) is required. Bidding parameters available for resources in gen model. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
6 | Double Counting Services: limit the participation of resources in RTO/ISO markets through a distributed energy resource aggregator that are receiving compensation for the same services as part of another program. | Retail programs/retail rates; Settlements | Retail Net-Energy Metering (NEM): Wholesale market participation of DER located at a NEM customer's location will need to be reviewed by EDC/utility after evaluation of resource(s) participation in NEM program and the associated NEM tariff. This review will be part of the DERA registration/Utility Review process, and will be on a utility-by-utility basis to capture differences in NEM tariffs. Wholesale / Retail Market Coordination: An example of this scenario would be flagging for normal DR activity while Peak-shaving for Capacity. Any such activity would need to be monitored and flagged. For situations such as the example above, resources would be scheduled for retail, and they would not be paid for wholesale. |  |  |  | Allow DERs participating in NEM programs to fully participate in PJM capacity and ancillary services markets unless a state has issued a specific determination that doing would result in double counting of services. |  | End use customers may only be with one CSP in one market at any moment in time. Duplicate logic and automated dispute logic in place. Rules are set up to avoid double counting of retail cost savings vs wholesale revenue. | Only allow generator to participate as 1 market resource. | Demand response portion and injection portion accounted for separate
7 | Information & Data Requirements: (1) Information and data that a distributed energy resource aggregator must provide about the physical and operational characteristics of its aggregation; (2) require distributed energy resource aggregators to provide a list of the individual resources in its aggregation; and (3) establish any necessary information that must be submitted for the individual distributed energy resources. |  | All DERs will be mapped individually in PJM network model. The location of each DER will be based on electrical impact and determined during the DERA registration process. Aggregator will submit location of DERs, EDC will verify and work with PJM for the proper mapping in EMS. | [5 empty] | DR is required to provide which customer will provide the response, their load reduction capability and how they will provide the response (HVAC. Gen, Lighting, etc). | Physical and Operational data provided to PJM, aggregation data N/A at this time | DR is required to provide which customer will provide the response, how much response and how they will provide the response.
8 | Metering & Telemetry: determine necessary metering for settlements and performance and telemetry for real-time situational awareness and dispatch. | Market Participation | Telemetry = data being provided to PJM in real-time Telemetry values for the DERA sent to PJM - MW telemetry values sent in all cases - No MVAR data required to be sent to PJM - Use Internet-based SCADA (Jetstream) or ICCP Scan rate frequency determined by chosen market participation: Regulation: 2 second (Reg-D), 10 second (Reg-A) Energy: 10 second Individual DER telemetry data will be needed for certain resource types. Meter data - provided by the aggregator for the DERA next business day after operating day, per existing submission deadlines. -Required at the aggregate level -Data may need to be broken out by individual DER in some instances where settlement rules differ by underlying resource type (e.g., Demand Response). - Real-time (RT) meter data is required to be submitted into PowerMeter either on a 5 minute or hourly basis in accordance with Manual 28, sections 1A and 3 |  |  |  | Telemetry for DERAs same as PJM proposal. Telemetry for DERs: Telemetry requirements for energy are tiered on the basis of size where: • The largest DERs have telemetry and 10 second updates. • Smaller (placeholder - less than 2MW) DERs have telemetry but updates on a less frequent cycle, perhaps every 15 minutes. Regulation telemetry and scan is same as status quo. SR for "Smallest" DERs is same as DR (one minute interval, next day reporting) • The smallest (placeholder - less than 500kW) DERs do not have telemetry requirements while allowing for aggregations to estimate performance. Settlements Same as PJM except that adjustments to next day submittals will be permitted up to 45days after initial submittal. (same as DR status quo) |  | Metering: Capacity (end of 2 months after the event) and Energy (60days after event)- require hourly load data after the fact (DR Hub) for settlement and performance calculations. SR requires 1min data 2 business days after the event. Telemetry: Regulation participation requires RT telemetry. Hourly meter data is required upon request. Requirements found in M11 | Metering: Hourly data required in Power Meter for capacity, energy and ancillary services. Telemetry: Required for ancillary services and capacity resources and required for energy resources >10MW. Requirements found in M01 | DR portion participates under DR rules, Gen (injection) portion participates under generation rules. Requirements found in M11, M01
9 | Locational Requirements: establish locational requirements for distributed energy resources to participate in a distributed energy resource aggregation that are as geographically broad as technically feasible, multi-node or single node aggregation. |  | Single, primary location model (“nodal” from FERC Order) for DERA eligibility. Aggregators may create a DERA where individual DER share a common primary transmission node as identified through the registration process. This is the mapping that the EDC/Aggregator provides for transmission location(s) (all DERs in aggregation sharing primary node), during registration process. This will not be updated unless reviewed and approved by PJM/EDC. | A multi-location (“multi-nodal”) model. PJM Staff believes this model introduces inefficiencies in dispatch and LMP formation. This approach would still model DERs nodally and restrict aggregations to utility footprints; this would be an improvement over a zonal aggregation model with respect to operational and pricing concerns. |  |  | PJM will identify groupings of zip codes/price nodes in each EDC that can be aggregated into a single DERA based on low likelyhood of constraints within the group. |  | Aggregation across geographic footprint based on market specific requirements and process (participation(min threshold), market offer, settlement and compliance). Energy market can be aggregated by zone by LSE (registration) and by zone (residual zonal aggregate) for the market offer. | Generating units that are connected to the system at the same electrical location may be aggregated and offered into the PJM market as a single unit. All individual nodes are studied and modeled with applicable resources. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
10 | Minimum & Maximum Size of Aggregation: Minimum size = 100 kW, determine max capacity size if one is needed. | distribution system reliable operations | Max: No max size for a DERA. Min: 100 kW DERA requirement | [5 empty] | 100kw min size, no max size requirements | 100kw min size, no max size requirements | 100kw min size, no max size requirements
11 | Maximum Capacity Requirements: propose a maximum capacity requirement for individual distributed energy resources participating in its markets through a distributed energy resource aggregation or, alternatively, to explain why such a requirement is not necessary. | state interconnection process | Max: No individual DER maximum size Local interconnection requirements and DERA participation requirements allow a flexible approach while still maintaining reliability. – Maximum size will be determined by the EDC/TSO based on system characteristic of the interconnected facility. | Individual DER >5MW may participate in a DERA, given they satisfy the other DERA participation requirements, but would be subject to providing individual telemetry/metering on the resource and/or participating as an aggregation of 1. | Individual DER with >5MW of injection capability are ineligible to participate in DERA. DER with only load reduction capability behind a customer's load meter would not be subject to a maximum size requirement. | Max: Individual DER <= 5MW will be eligible to participate in a DERA, given they satisfy the other DERA participation requirements. |  |  | 1 site over 100kw in an aggregation (no capacity size max on that 1 site), with exception process | No Max Capacity Size | 1 site over 100kw in an aggregation (no capacity size max on that 1 site)
12 | Single Resource Aggregation: allow a single qualifying distributed energy resource to avail itself of the proposed distributed energy resource aggregation rules by serving as its own distributed energy resource aggregator. Can set size requirements for these resources. |  | A single DER can be a DERA | [5 empty] | Single customer may participate but would need to be a PJM member. | Single resources are allowed to participate in the market | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
13 | Modifications to List of Resources in Aggregation: develop rules for modifying the list of resources in an aggregation and how they would be reported to PJM. | Utility Review Process | Aggregators that are modifying an existing DERA will need to submit modifications for utility and PJM review. Adding/Removing a DER to/from a DERA: - 60 day review process; same review process as origination on DERA which is still an abbreviated process in comparison to generation changes - If DERA is part of a DERA CP resource, these aggregations will be active for the full delivery year and will not be able to be modified. - DERA changes can be made on a quarterly basis such that any necessary updates can be reflected in the PJM model update process. | [5 empty] | All customers are "registered" and then CSP can modify their offers or their aggregation (via Dispatch groups). Some modification (such as a change in customers providing service) will require a re-registration process. | All modifications (adding generation) need to go through PJM queue for study. Modeling or aggregation of resources in Markets is able to be performed during quarterly model updates (e.g. combined cycles). Unit modeling changes in the PJM Markets Gateway system (unit type, aggregation level), not including changes based on physical changes at the plant, can be made at the beginning of each quarter. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
14 | Types of Technology: make sure participation is technology neutral, allow heterogeneous and homogeneous aggregations. | Market Participation | Resources within an aggregation will inherit existing market rules associated with the underlying technology type (e.g. gas, solar, battery, demand response). | [5 empty] | DR can participate with anything that will reduce load - we do not differentiate based on how the load is reduced. For example, we treat batteries, mass market AC cycling and arc furnace curtailments the same | Aggregation currently only homogenous (hydro or combined cycle). | DR can participate with anything that will reduce load - we do not differentiate based on how the load is reduced. For example, we treat batteries, mass market AC cycling and arc furnace curtailments the same
15 | Market Participation Agreements: new agreement in Tariff for aggregators. Attestation that the DER aggregator’s aggregation is compliant with the Tariff and operating procedures of the utility. |  | Further details to come as part of Tariff redline review Likely will have parallels to existing Wholesale Market Participation Agreement; However, will be a pro forma agreement under the Tariff. Attestation that DER Aggregator is compliant with tariffs/operating procedures/rules of distribution utility and RERRA. | [5 empty] | CSP must be a PJM member but does not sign a market participation agreement. - Certification (or provide attestations) is required for different market participation (e.g. for regulation with the capability to inject we require CSP to coordinate and get approval from the EDC that they meet the EDCs requirements). | Resources signs WMPA or ISA. Market Seller can sign a DOA to market the resource. Resource owner does not need to be a PJM Member, but Market Seller does. | DR portion participates under DR rules, Gen (injection) portion participates under generation rules.
16 | Market Rules to address coordination between all parties (DO/TO/RTO/RERRA) - Distributed Utility Review: develop a process for utilities to review the individual DERs in the aggregation, if they can participate (double counting checks) and safe and reliable operations. - Coordinate Operations: data flows, line faults, outages, dispatch control - Role of RERRA |  | DERA Registration / Utility Review Process: Still evolving, but likely to leverage a "demand response-like" process for reviewing/verifying DER and DERA information between Aggregator, Utility, and PJM, with notable differences for DERA regarding the information gathered, the verification steps, utility review of interconnection and potential reliability issues, and the timeline. Operational Coordination Framework: Still evolving | [5 empty] | PJM has an automated process built to coordinate across all parties - this was expanded as part of 719A. We have detailed rules on how this works and who is responsible for what. This coordination has been active since 2007.
17 | Implementation timing and other considerations | Market Design; FERC; RERRAs |  |  |  |  | PJM should generally exempt DER aggregations from the requirement to submit cost-based energy offers. The submission of cost-based offers is intended to address the potential exercise of market power, but DER aggregations will overwhelmingly be smaller resources that generally pose no market power risk. Applying cost-based offer requirements designed for larger resources would result in barriers to participation contrary to Order No. 2222's requirements. PJM could consider establishing a size threshold (based on the size of an aggregator's overall portfolio) above which the risk of exercising market power is sufficient to warrant a requirement to submit cost-based offers.

## Parking Lot Items
Item | Notes/Response
Additional information about DERA and capacity rights - why no CIRs?
Roles and responsibilities around meter data submission through Power Meter - timing has been a problem today, how is PJM considering this for DERA?
Sizing requirements - additional explanation needed around the 5MW cutoff in the PJM straw proposal
What is the "DER" that is registering in a DERA for electric vehicles - the car or charging station? | PJM response: primarily it is the location of charging station, but additional information would be needed around the capability of the vehicle.
Data reporting (DER or DERA level data necessary) - where is each needed and why? Aggregate vs individal and if it is aggregate, how does the individual data need to update in regard to that?
Request for clarity on the interconnection data requests - slide 23 of April straw proposal | Status: PJM working this issue through offline conversations with utilities
Can the utility serve as the dispatch agent for a DERA and not run afoul of Order 888 code of conduct requirements? Verification needed in response to the PJM 'alternate' Ops Coordination model presented on 5/19/2021.
Additional information about the TPS test and small resource data that was presented by the IMM on 5/19/2021 | In each State of the Market report, there is a section on TPS test results and offer capping. In the first quarter 2021 report, the pages are 201-210 in Section 3: Energy Market. http://www.monitoringanalytics.com/reports/PJM_State_of_the_Market/2021.shtml For each annual report, additional information can be found in the appendices. You can find the TPS information in appendix B, pages 25-28, and all of appendix C. http://www.monitoringanalytics.com/reports/PJM_State_of_the_Market/2019.shtml The Technical Reference for PJM Markets includes a detailed explanation of the TPS test on pages 38-49. http://www.monitoringanalytics.com/reports/Technical_References/references.shtml
Additional detail on how PAI calculations will be applied to DERAs, especially in the case of potential utility override
PJM analysis of constraints and frequency of constraints related to nodal vs. multi-nodal discussion to help inform judgement of aggregation of nodes.
Develop business rules when a scheduled resource does not deliver related to utility overrides recognizing that utility overrides for a number of reasons.