## Examples
EXAMPLE 1 | Registration | Pmax (MW): |  | 350 | Voltage Schedule (kV): | 525
|  | Pmin (MW): |  | 50 | Bandwidth (kV): | +/- 5
|  | ISA Required Lagging PF: |  | 0.9 | AVR Equipped: | Yes
|  | ISA Required Leading PF: |  | 0.95 | Model in EMS: | LSG
|  | Expected Qmax (MVAR): |  | 169.5127 | Telemetry Verified: | Yes
|  | Expected Qmin (MVAR): |  | -115.0394
| Testing | Tested Qmax @Pmax: |  | 190
|  | Tested Qmin @Pmax: |  | -190
|  | Tested Qmax @Pmin: |  | 250
|  | Tested Qmin @Pmin: |  | -250
| D-curve | MW Points | Qmin | Qmax
|  | 50 | -250 | 250 | Pmin
|  | 100 | -240 | 240
|  | 150 | -230 | 230
|  | 200 | -220 | 220
|  | 250 | -210 | 210
|  | 300 | -200 | 200
|  | 350 | -190 | 190 | Pmax
|  | 375 | -180 | 180
| Compensation | Eligible? | Yes
Compensated Capability:
|  | Qmin_Avg | Qmax_Avg | Total
|  | -220 | 220 | 440
| Performance |  | Actual kV | Actual MW | Expected MVAR | Actual MVAR | Performance
|  | 0:00 | 525 | 300 | N/A | 20 | N/A
|  | 0:05 | 524 | 300 | N/A | 30 | N/A
|  | 0:10 | 523 | 300 | N/A | 40 | N/A
|  | 0:15 | 522 | 300 | N/A | 50 | N/A
|  | 0:20 | 521 | 300 | N/A | 60 | N/A
|  | 0:25 | 520 | 300 | N/A | 70 | N/A
|  | 0:30 | 515 | 300 | 180 | 80 | N/A
|  | 0:35 | 516 | 300 | 180 | 100 | Fail
|  | 0:40 | 517 | 300 | 180 | 150 | Fail
|  | 0:45 | 518 | 300 | 180 | 200 | Pass
|  | 0:50 | 519 | 300 | 180 | 200 | Pass
|  | 0:55 | 520 | 300 | N/A | 200 | N/A
| Revised D-curve | MW Points | Qmin | Qmax | New Qmax
|  | 50 | -250 | 250 | 175
|  | 100 | -240 | 240 | 165
|  | 150 | -230 | 230 | 155
|  | 200 | -220 | 220 | 145
|  | 250 | -210 | 210 | 135
|  | 300 | -200 | 200 | 125
|  | 350 | -190 | 190 | 115
|  | 375 | -180 | 180 | 105
New Compensated Capability:
|  | Qmin_Avg | Qmax_Avg | Total
|  | -220 | 145 | 365
EXAMPLE 2 | Registration | Pmax: |  | 70 | Voltage Schedule (kV): | 138
|  | Pmin: |  | 0 | Bandwidth (kV): | +/- 5
|  | ISA Required Lagging PF: |  | 0.95 | AVR Equipped: | Yes
|  | ISA Required Leading PF: |  | 0.95 | Model in EMS: | HSN
|  | Expected Qmax: |  | 23.0079 | Telemetry Verified: | Yes
|  | Expected Qmin: |  | -23.0079
| Testing | Tested Qmax @Pmax: |  | 40
|  | Tested Qmin @Pmax: |  | -25
|  | Tested Qmax @Pmin: |  | 40
|  | Tested Qmin @Pmin: |  | -40
| D-curve | MW Points | Qmin | Qmax
|  | 0 | -40 | 40 | Pmin
|  | 10 | -40 | 40
|  | 20 | -40 | 40
|  | 30 | -40 | 40
|  | 40 | -40 | 40
|  | 50 | -40 | 40
|  | 60 | -40 | 40
|  | 70 | -25 | 40 | Pmax
| Compensation | Eligible? | Yes
Compensated Capability:
|  | Qmin_Avg | Qmax_Avg | Total
|  | -32.5 | 40 | 72.5
| Performance |  | Actual kV | Actual MW | Expected MVAR | Actual MVAR | Performance
|  | 0:00 | 138 | 10 | N/A | -5 | N/A
|  | 0:05 | 138.5 | 10 | N/A | -6 | N/A
|  | 0:10 | 139 | 10 | N/A | -7 | N/A
|  | 0:15 | 139.5 | 10 | N/A | -8 | N/A
|  | 0:20 | 140 | 10 | N/A | -8 | N/A
|  | 0:25 | 140.5 | 10 | N/A | -8 | N/A
|  | 0:30 | 141 | 10 | N/A | -10 | N/A
|  | 0:35 | 141.5 | 10 | N/A | -20 | N/A
|  | 0:40 | 144 | 10 | -36 | -30 | N/A
|  | 0:45 | 144 | 10 | -36 | -40 | Pass
|  | 0:50 | 144 | 10 | -36 | -40 | Pass
|  | 0:55 | 140 | 10 | N/A | 200 | N/A
| Revised D-curve | MW Points | Qmin | Qmax
| (no change) | 0 | -40 | 40
|  | 10 | -40 | 40
|  | 20 | -40 | 40
|  | 30 | -40 | 40
|  | 40 | -40 | 40
|  | 50 | -40 | 40
|  | 60 | -40 | 40
|  | 70 | -25 | 40
New Compensated Capability:
|  | Qmin_Avg | Qmax_Avg | Total
|  | -32.5 | 40 | 72.5