## Setup
Enter Stakeholder Group Name in cell A2:
SRDTF
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Synchronized Reserve Event Actions and Expectations

## 1. Interest Identification
SRDTF
Synchronized Reserve Event Actions and Expectations
Interest Identification
Instructions: List interests of all parties on this page.
1 | Prompt recovery of ACE following a disturbance event
2 | Maintaining existing PJM and NERC BAL compliance requirements, and grid reliability
3 | Controlled deployment of reserve MWs
4 | Honoring of transmission constraints (don't violate limits pre- or post-contingency)
5 | Making sure the operators know what resources are responding
6 | Economically optimized deployment of reserves
7 | Alignment of performance evaluation with resource expectations
8 | Improved reflection of reserve deployment in pricing during events
9 | Document PJM and resource actions during event
10 | Retain current dispatch and pricing process using SCED and LPC.
11 | Maintain accurate locational dispatch signals and prices reflecting accurate inputs, such as loss of unit.
12 | Maintain pricing consistent with target dispatch to meet load forecast and reserve requirements.
13 | Accurate assignment of obligation for synchronized reserves under long term SCED updates and new ORDCs.
14 | Accurate calculation of performance for synchronized reserves under long term SCED updates and new ORDCs.
15 | Limit use of load bias to affect outcomes

## 2. Options Matrix- Design Comp.
SRDTF
Synchronized Reserve Event Actions and Expectations
OPTIONS MATRIX
Strive for simplicity
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21 | Column22 | Column23 | Column24 | Column25 | Column26 | Column27 | Column28 | Column29 | Column30 | Column31 | Column32 | Column33 | Column34 | Column35 | Column36 | Column37 | Column38 | Column39 | Column40 | Column41 | Column42 | Column43 | Column44 | Column45 | Column46 | Column47 | Column48 | Column49 | Column50 | Column51 | Column52 | Column53 | Column54 | Column55 | Column56 | Column57 | Column58 | Column59 | Column60 | Column61 | Column62 | Column63 | Column64 | Column65 | Column66 | Column67 | Column68 | Column69 | Column70 | Column71 | Column72 | Column73 | Column74 | Column75 | Column76 | Column77 | Column78 | Column79 | Column80 | Column81 | Column82 | Column83 | Column84 | Column85 | Column86 | Column87 | Column88 | Column89 | Column90 | Column91 | Column92 | Column93 | Column94 | Column95 | Column96 | Column97 | Column98 | Column99 | Column100 | Column101 | Column102 | Column103 | Column104 | Column105 | Column106 | Column107 | Column108 | Column109 | Column110 | Column111 | Column112 | Column113 | Column114 | Column115 | Column116 | Column117 | Column118 | Column119 | Column120 | Column121 | Column122 | Column123 | Column124 | Column125 | Column126 | Column127 | Column128 | Column129 | Column130 | Column131 | Column132 | Column133 | Column134 | Column135 | Column136 | Column137 | Column138 | Column139 | Column140 | Column141 | Column142 | Column143 | Column144 | Column145 | Column146 | Column147 | Column148 | Column149 | Column150 | Column151 | Column152 | Column153 | Column154 | Column155 | Column156 | Column157 | Column158 | Column159 | Column160 | Column161 | Column162 | Column163 | Column164 | Column165 | Column166 | Column167 | Column168 | Column169 | Column170 | Column171 | Column172 | Column173 | Column174 | Column175 | Column176 | Column177 | Column178 | Column179 | Column180 | Column181 | Column182 | Column183 | Column184 | Column185 | Column186 | Column187 | Column188 | Column189 | Column190 | Column191 | Column192 | Column193 | Column194 | Column195 | Column196 | Column197 | Column198 | Column199 | Column200 | Column201 | Column202 | Column203 | Column204 | Column205 | Column206 | Column207 | Column208 | Column209 | Column210 | Column211 | Column212 | Column213 | Column214 | Column215 | Column216 | Column217 | Column218 | Column219 | Column220 | Column221 | Column222 | Column223 | Column224 | Column225 | Column226 | Column227 | Column228 | Column229 | Column230 | Column231 | Column232 | Column233 | Column234 | Column235 | Column236 | Column237 | Column238 | Column239 | Column240 | Column241 | Column242 | Column243 | Column244 | Column245 | Column246 | Column247
1 | Deployment mechanism | High | All-call and initiation in EMS. DR initiation is through DR Hub, and not EMS. | Use approval of existing SCED case to initiate event and communication | Automated deployment tool (ADT), to send dispatch signals to resources including synchronized reserves. | [6 empty] | Low - Medium
1a | Sub-zone deployment | High | Operator discretion to deploy RTO or Sub-zone reserves with corresponding communications | ADT will determine set of reserves to convert to energy.
1b | Communication of an event | Medium | All call and telemetry. Emergency procedures. DR Hub is the primary means for DR. | Units respond back by telemetry or other means, acknowledging the event initiation | Synchronized reserve event declaration without requesting all units. Automated deployment tool (ADT) instructions communicated through basepoints.
2 | Constraint control | High | Manual operator intervention. Even if SCED cases are approved, basepoints that reflect constraint control are superseded by all-call instructions. Constraints may go into violation as a result of loading units that were being kept down to control constraints. | Automatically honor active constraints during deployment | ADT to use same constraint limits as the last approved SCED solution. Subsequent SCED case will use short term emergency constraint limits until end of spin event.
3 | Pricing during events | High | LMP based on approved SCED case, if there is one approved. | LMP more reflective of system conditions for all events
3a | Timing | Low | Pricing is approved in current 5-min interval and would be reflected in a later interval. The updates to five minute dispatch and pricing (Docket No. ER21-1919) planned for November 1, 2021, will align the LMPs with the RT SCED dispatch instructions effective for each five minute interval, and eliminate the existing lag introduced with the short term changes implemented in October, 2020. | Price is reflected in the next interval
3b | Pricing at the start of the spin event | High | LMP based on last approved SCED case, which does not reflect lost unit. | SCED case available to be deployed that reflects the loss of the largest unit to get units moving in the right direction
4 | Response performance evaluation | High | The magnitude of each resource’s response to a Synchronized Reserve Event (both Tier 1 and Tier 2) is the difference between the resource’s output at the start of the event and its output ten (10) minutes after the start of the event. In order to allow for small fluctuations and possible telemetry delays, resource output at the start of the event is defined as the lowest telemetered output between one (1) minute prior to and one (1) minute following the start of the event. Similarly, a resource’s output ten (10) minutes after the event is defined as the greatest output achieved between nine (9) and eleven (11) minutes after the start of the event. All resources (both Tier 1 and Tier 2) must maintain an output level greater than or equal to that which was achieved as of ten (10) minutes after the event for the duration of the event or thirty (30) minutes from the start of the event, whichever is shorter. The response actually credited to a given resource will be reduced by the amount the MW output of that resource falls below the level achieved after ten (10) minutes by either the end of the event or after thirty (30) minutes from the start of the event, whichever is shorter For Demand Resources that are considered “batch load” resources, a second method of verification will be used for instances where a Synchronized Reserve Event is initiated and the resource is operating at the minimum consumption level of its duty cycle. In this case, the magnitude of the response will be measured as the difference between (a) the resource’s consumption at the end of the event and (b) the maximum consumption within a ten (10) minute period following the event provided that all subsequent minutes following that minute are no less than 50% of the consumption in that minute. | More accurate evaluation of response (both assignments and performance). Adapt to long term SCED changes. | Response performance based on basepoints, which may change throughout an event.
5 | Targeted deployment | High | All call goes to all units in the region. All units are eligible to respond. DR Hub determines which DR registrations are deployed and notifies the relevant Curtailment Service Providers. | Units follow specific basepoints provided by SCED case. SCED case would adjust reserve deployment to be closer to system needs rather than 100% SR. | ADT will deploy the exact amount of reserves needed based on the contingency. | [6 empty] | Low
5a | Basepoint calculation | High | Basepoints are superseded by all-call instructions. SCED cases that do not see lost unit may send conflicting instructions. | Proactively having SCED calculate the basepoints for the largest possible unit loss. | Basepoints calculated in the ADT based on the actual contingency.
7 | Operator interactions and control | High | Reactive based on which units actually respond. Poor performance from assigned resources limits predictability. | Proactive usage of SCED cases throughout event with predicable response. | Select the unit lost to input into the ADT. | [6 empty] | Low - High
7a | Operator Visibility |  | Limited tool visibility into expected response since basepoints are superseded. Resources would appear to be deviating from basepoints. | Updated tools to show when large unit losses are reflected in SCED cases. Usage of SCED allows operators to see expected dispatching and pricing information. | Improve visualization of deployed reserves from ADT to operators.(Control room upgrade, no manual or tariff changes needed.)
7b | SCED usage |  | SCED usage during events is inconsistent due to short duration of events and delay in case seeing the actual unit lost. | Initial SCED case to trigger event designed for SR deployment. Normal SCED case usage continues as normal afterwards.
7c | ACE overshoot actions |  | End deployment event early, manually reduce or turn off units. | Approve new RTSCED case more suitable for system conditions with expectations units are following basepoints. Status quo options are still available. | Address cause of overshoot - remove instruction for all resources to ramp up, remove use of high load bias without an underlying forecast error, continue using SCED with accurate inputs. Update settlements rules to not compensate over performance.
7d | Emergency Operation (i.e. in the event of SCED is not operating properly) |  | Follow the existing emergency procedures
8 | Resource transition |  | Resources that typically follow basepoints through AGC would need to stop and purposely deviate to load 100% reserves. Upon event termination, resources would be expected to resume basepoint following. Transitions may require time and manual intervention depending on the resource. | Should be no transition as most online units would just continue to follow basepoints without manual intervention. Inflexible T2 units would need to come on. | For units using AGC, no transition. For units under manual dispatch, continue to respond to PJM dispatch instructions manually. | [6 empty] | Medium
9 | Documentation of PJM and resource actions |  | Existing language in M12 and M13 | Expand on existing manual language with regards to PJM and unit actions. Governing document changes if needed. | PJM Manual Updates; Notice and training to generation operators/dispatchers with updated process. | [6 empty] | Medium - High
10 | Inputs and modeling assumptions in reserve deployment tool. |  | No tool to deploy reserves. All-call instructions to load 100% SR. | Unit loss modeled accurately. Continue to use accurate load forecast and reserve requirements. All cleared synchronized reserves made eligible for energy dispatch. | Unit loss modelled when available to SCED after State Estimator validation to get updated flows. Initial spin deployment case to move units in right direction and being recovery. All units are eligible for energy dispatch. | Unit loss modelled in SCED by bypassing State Estimator validation. | [5 empty] | High
Instructions:
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Component Details" tab.
3. Using informal/non-binding voting, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Solution Details" tab.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.
7. If consensus is achieved on a single package (Tier 1 decision-making method), this will be documented in a Consensus Proposal Report to the parent committee.
8. If not, the group will identify up to 3 possible solution packages in a comparative Proposal Alternatives Report to the parent committee (Tier 2 decision-making method).

## 2a. Component Details
SRDTF
Synchronized Reserve Event Actions and Expectations
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component |  | Detailed Description
1 |  | <enter detailed description of this component>
2 |  | <enter detailed description of this component>
3 |  | <enter detailed description of this component>
4 |  | <enter detailed description of this component>
5 |  | <enter detailed description of this component>

## 2b. Solution Details
SRDTF
Synchronized Reserve Event Actions and Expectations
SOLUTION DETAILS
Instructions: Complete this form as needed. Potential solutions should be populated from the Proposal Matrix
Package Solutions2
| A | B | C | D | E
1
2
3
4
5

## 3. Package Matrix
SRDTF
Synchronized Reserve Event Actions and Expectations
PACKAGE/ PROPOSAL MATRIX
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1 | Deployment mechanism | High | All-call and initiation in EMS. DR initiation is through DR Hub, and not EMS. | Status quo
1a | Sub-zone deployment | High | Operator discretion to deploy RTO or Sub-zone reserves with corresponding communications | Same operator discretion as far as communication. Basepoints will reflect any regional limitations through active constraints.
1b | Communication of an event | Medium | All call and telemetry. Emergency procedures. DR Hub is the primary means for DR. | Status quo with updated messaging
2 | Constraint control | High | Manual operator intervention. Even if SCED cases are approved, basepoints that reflect constraint control are superseded by all-call instructions. Constraints may go into violation as a result of loading units that were being kept down to control constraints. | Automatic through IRD case. Constraints active at the time of event will be controlled by the case. Option to use same controllling percentage as RTSCED or 100%.
3 | Pricing during events | High | LMP based on approved SCED case, if there is one approved. | IRD case used at start of event and RTSCED cases will be approved for longer events.
3a | Timing | Low | Pricing is approved in current 5-min interval and would be reflected in a later interval. The updates to five minute dispatch and pricing (Docket No. ER21-1919) planned for November 1, 2021, will align the LMPs with the RT SCED dispatch instructions effective for each five minute interval, and eliminate the existing lag introduced with the short term changes implemented in October, 2020. | IRD case would override RTSCED case if one was already approved for the same interval.
3b | Pricing at the start of the spin event | High | LMP based on last approved SCED case, which does not reflect lost unit. | IRD case will always be approved and used in LMP unless there's a technical issue.
4 | Response performance evaluation | High | The magnitude of each resource’s response to a Synchronized Reserve Event (both Tier 1 and Tier 2) is the difference between the resource’s output at the start of the event and its output ten (10) minutes after the start of the event. In order to allow for small fluctuations and possible telemetry delays, resource output at the start of the event is defined as the lowest telemetered output between one (1) minute prior to and one (1) minute following the start of the event. Similarly, a resource’s output ten (10) minutes after the event is defined as the greatest output achieved between nine (9) and eleven (11) minutes after the start of the event. All resources (both Tier 1 and Tier 2) must maintain an output level greater than or equal to that which was achieved as of ten (10) minutes after the event for the duration of the event or thirty (30) minutes from the start of the event, whichever is shorter. The response actually credited to a given resource will be reduced by the amount the MW output of that resource falls below the level achieved after ten (10) minutes by either the end of the event or after thirty (30) minutes from the start of the event, whichever is shorter For Demand Resources that are considered “batch load” resources, a second method of verification will be used for instances where a Synchronized Reserve Event is initiated and the resource is operating at the minimum consumption level of its duty cycle. In this case, the magnitude of the response will be measured as the difference between (a) the resource’s consumption at the end of the event and (b) the maximum consumption within a ten (10) minute period following the event provided that all subsequent minutes following that minute are no less than 50% of the consumption in that minute. | Expected resonse based on approved IRD and SCED basepoints. Measured response will be status quo. More details are in the presentation.
5 | Targeted deployment | High | All call goes to all units in the region. All units are eligible to respond. DR Hub determines which DR registrations are deployed and notifies the relevant Curtailment Service Providers. | Modified all call to have units follow basepoints. Basepoints will be updated for expected response from units. Units should not deviate from their basepoints. |  |  |  |  | Low
5a | Basepoint calculation | High | Basepoints are superseded by all-call instructions. SCED cases that do not see lost unit may send conflicting instructions. | IRD case will flip inflexible T2 to energy and dispatch other units based on system conditions. Bias applied to RTO based on the MW amount of the largest unit. |  |  |  |  | Low - Medium
7 | Operator interactions and control | High | Reactive based on which units actually respond. Poor performance from assigned resources limits predictability. | Proactive with basepoints from IRD optimization to initiate events. RTSCED can be used throughout event to adjust based on updated conditions. |  |  |  |  | Low - High
7a | Operator Visibility |  | Limited tool visibility into expected response since basepoints are superseded. Resources would appear to be deviating from basepoints. | Tool enhancements to display when unit lost is reflected in RTSCED cases. Displays to dispatch expected regional response and pricing. |  |  |  |  | Medium
7b | SCED usage |  | SCED usage during events is inconsistent due to short duration of events and delay in case seeing the actual unit lost. | Consistent SCED usage throughout the event. IRD to initiate and RTSCED to carry through. |  |  |  |  | Medium - High
7c | ACE overshoot actions |  | End deployment event early, manually reduce or turn off units. | Controlled deployment through updated basepoints throughout spin event. |  |  |  |  | High
7d | Emergency Operation (i.e. in the event of SCED is not operating properly) |  | Follow the existing emergency procedures | Status quo
8 | Resource transition |  | Resources that typically follow basepoints through AGC would need to stop and purposely deviate to load 100% reserves. Upon event termination, resources would be expected to resume basepoint following. Transitions may require time and manual intervention depending on the resource. | Smooth transition as units should be following basepoints before, during, and after events. No all call disruption to load 100% SR.
9 | Documentation of PJM and resource actions |  | Existing language in M12 and M13 | Additional language in appropriate manuals and goverining documents to describe PJM actions and unit expectations based on IRD.
10 | Inputs and modeling assumptions in reserve deployment tool. |  | No tool to deploy reserves. All-call instructions to load 100% SR. | All units are eligible to respond to SR

## Parking Lot
SRDTF
Synchronized Reserve Event Actions and Expectations
Interest Identification
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
SRDTF
Synchronized Reserve Event Actions and Expectations
Revision History
Current Spreadsheet Version:
Version | Posting Date | Description of changes