## Key System Upgrades 2024_2025
System Upgrades With Potential Impact to Congestion June 2024 Through May 2025
Description | Transmission Owner | Projected In-Service Date
Partial Rebuild of 230 kV lines between Clifton and Johnson DP (#265, #200 and #2051) with double circuit steel structures using double circuit conductor at current 230 kV northern Virginia standards with a minimum rating of 1200 MVA. | Dominion | 12/31/2023
Reconductor the 14.2 miles of the existing Juniata-Cumberland 230 kV line with 1272 ACSS/TW HS285 "Pheasant" conductor. | PPL | 12/31/2023
Rebuild 230kV Line #224 between Lanexa and Northern Neck utilizing double circuit structures to current 230kV standards. Only one circuit is to be installed on the structures with this project with a minimum summer emergency rating of 1047 MVA. | Dominion | 3/31/2024
Add forced cooling to increase the normal rating of the Brunot Island-Carson (302) 345 kV High Pressure Fluid Filled (HPFF) underground cable circuit | DL | 4/30/2024
Reconductor Kammer - George Washington 138 kV line (~0.08 miles). Replace the wave trap at Kammer 138 kV. | AEP | 6/1/2024
Rebuild the George Washington – Kammer 138 kV circuit, except for 0.1-mile of previously-upgraded T-line outside each terminal station (6.7 miles of total upgrade scope). Remove the existing 6-wired steel lattice towers and supplement the right-of-way as needed. | AEP | 6/1/2024
Rebuild Hathaway-Rocky Mount (Duke Energy Progress) 230 kV Line #2181 and Line #2058 with double circuit steel structures using double circuit conductor at current 230 kV standards with a minimum rating of 1047 MVA. | Dominion | 6/14/2024
Rebuild 500kV Line #581 Ladysmith to Chancellor - 15.2 miles long | Dominion | 6/30/2024
Install 2nd Chickahominy 500/230 kV transformerRelocate the Chickahominy – Elmont 500kV line #557 to terminate in a new bay at Chickahominy substation and relocate the Chesterfield – Lanexa 115kV line #92 to allow for the expansion of the Chickahominy substation • Add three new 500 kV breakers with 50kA interrupting rating and associated equipment | Dominion | 6/30/2024
Rerate the 23076 Steel-Milford 230 kV line | DPL | 6/30/2024
Reconductor approximately 1.07 miles of 230 kV line #2008 segment from Cub Run-Walney to achieve a summer rating of 1574 MVA. Replace line switch 200826 with a 4000A switch. | Dominion | 11/15/2024
Rebuild approximately 12.3 miles of remaining Lark conductor on the double circuit line between Haviland and East Lima with 1033 54/7 ACSR conductor. | AEP | 12/1/2024
Rebuild 230 kV line No.2063 (Clifton – Ox) and part of 230 kV line No.2164 (Clifton – Keene Mill) with double circuit steel structures using double circuit conductor at current 230 kV northern Virginia standards with a minimum rating of 1200 MVA. | Dominion | 12/31/2024
Rebuild 20 miles of the East Towanda - North Meshoppen 115 kV line | PENELEC | 12/31/2024
Convert 115 kV Line #172 Liberty-Lomar and 115 kV Line #197 Cannon Branch-Lomar to 230 kV to provide a new 230 kV source between Cannon Branch and Liberty. The majority of 115 kV Line #172 Liberty-Lomar and Line #197 Cannon Branch-Lomar is adequate for 230 kV operation. Lines to have a summer rating of 1047 MVA/1047 MVA (SN/SE) | Dominion | 12/31/2024
Extend 230kV Line #2011 Cannon Branch – Clifton to Winters Branch by removing the existing Line #2011 termination at Cannon Branch and extending the line to Brickyard creating 230kV Line #2011 Brickyard-Clifton. Extend a new 230kV line between Brickyard and Winters Branch with a summer rating of 1572MVA/1572MVA (SN/SE) | Dominion | 12/31/2024
Rebuild a 13 mile section of 138 kV line 0108 between LaSalle and Mazon with 1113 ACSR or higher rated conductor. The 13 mile portion of line 7713 from Oglesby (future Corbin) to Mazon that shares double circuit towers with line 0108 will also be reconductored due to the rebuild. | ComEd | 12/31/2024
Wreck and rebuild 5.4 miles of 115 kV line #100 Locks-Harrowgate to achieve a minimum summer emergency rating of 393 MVA. Upgrade terminal equipment at Locks and Harrowgate to not limit the new conductor rating and perform line #100 Chesterfield terminal relay work. | Dominion | 12/31/2024
Install 1.7 miles of 795 ASCR 138kV conductor along the other side of Dragoon Tap 138 kV line, which is currently double circuit tower with one position open. Additionally, install a 2nd 138/34.5 kV transformer at Dragoon, install a high side circuit switcher on the current transformer at Dragoon Station, and install 2-138 kV line breakers on the Dragoon-Jackson 138 kV and Dragoon-Twin Branch 138 kV lines. | AEP | 1/1/2025
Rebuild approximately 2.3 miles along existing ROW from Sweetgum to the Hayport Rd switch 69 kV location as 138 kV single circuit and rebuild approximately 2.0 miles from the Hayport Road switch to Althea 69 kV with double circuit 138 kV construction, one side operated at 69 kV to continue service to K.O. Wheelersburg, using 795 ACSR 26/7 Drake (SE 359 MVA). | AEP | 4/15/2025
Reconductor approximately 24.42 miles of 230 kV line #2114 Remington CT-Elk Run-Gainesville to achieve a summer rating of 1574 MVA by fully reconductoring the line and upgrading the wave trap and substation conductor at Remington CT and Gainesville. | Dominion | 5/30/2025
Highlighted upgrades will be modeled as in-service in annual ARR allocation and annual FTR auction
Note: See the Project Status & Cost Allocation page in the Planning section of the PJM web site for a complete list of all planned upgrades including up-to-date projections of in-service dates