## Planning Parameters
2025-2026 RPM Base Residual Auction Planning Parameters |  |  | 2024-06-05
| RTO | Notes:
Installed Reserve Margin (IRM) | 17.8% | endorsed at the March 20, 2024 MRC meeting https://www.pjm.com/-/media/committees-groups/committees/mrc/2024/20240320/20240320-item-05---irm-fpr-and-elcc-for-25-26-bra---presentation.ashx
Pool-Wide Accredited UCAP Factor | 79.69% | endorsed at the March 20, 2024 MRC meeting.
Forecast Pool Requirement (FPR) | 0.9387 | endorsed at the March 20, 2024 MRC meeting.
Preliminary Forecast Peak Load | 153883.0351 | 2024 Load Report with adjustments for load served outside PJM.
Locational Deliverability Area
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland | COMED | BGE | PL | DAYTON | DEOK | DOM
CETO | NA | -1207 | 5335 | 6772 | 6389 | 2957 | 1435 | 4336 | 4406 | 3428 | -3270 | 4620 | -145 | 2603 | 2797 | 5156
CETL | NA | 3222 | 8717 | 8467 | 8501 | 4282 | 2030 | 6572 | 10846 | 4713 | 5254 | 6031 | 4681 | 3931 | 5387 | 5164
Reliability Requirement | 144450 | 53342.3 | 30953.4 | 13508.8 | 10664 | 5415.8 | 2750.4 | 6557.3 | 12186 | 5064 | 20819.6 | 6940.7 | 8765.4 | 3521.8 | 5596.1 | 25746.2
Total Peak Load of FRR Entities | 11597.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 831.9392 | 0
Preliminary FRR Obligation | 10886.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780.9 | 0
Reliability Requirement adjusted for FRR | 133563.6 | 53342.3 | 30953.4 | 13508.8 | 10664 | 5415.8 | 2750.4 | 6557.3 | 12186 | 5064 | 20819.6 | 6940.7 | 8765.4 | 3521.8 | 5561.7404 | 25746.2
Gross CONE, $/MW-Day (UCAP Price) | 451.61 | 456.19 | 461.66 | 466.35 | 461.66 | 461.66 | 461.66 | 466.35 | 444.26 | 444.26 | 447.33 | 466.35 | 438.47 | 444.26 | 444.26 | 444.26
Net CONE, $/MW-Day (UCAP Price) | 228.81 | 250.98 | 310.88 | 134.57 | 330.97 | 330.97 | 245.68 | 223.8 | 236.78 | 236.78 | 300.32 | 45.34 | 260.21 | 191.38 | 205.25 | 152.69
EE Addback (UCAP) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 451.61 | 456.19 | 466.32 | 466.35 | 496.46 | 496.46 | 461.66 | 466.35 | 444.26 | 444.26 | 450.48 | 466.35 | 438.47 | 444.26 | 444.26 | 444.26
Point (b) UCAP Price, $/MW-Day | 171.61 | 188.24 | 233.16 | 100.93 | 248.23 | 248.23 | 184.26 | 167.85 | 177.59 | 177.59 | 225.24 | 34.01 | 195.16 | 143.54 | 153.94 | 114.52
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Point (a) UCAP Level, MW | 132094.4 | 52755.5 | 30612.9 | 13360.2 | 10546.7 | 5356.2 | 2720.1 | 6485.2 | 12052 | 5008.3 | 20590.6 | 6864.4 | 8669 | 3483.1 | 5500.6 | 25463
Point (b) UCAP Level, MW | 135700.6 | 54195.8 | 31448.7 | 13724.9 | 10834.6 | 5502.5 | 2794.4 | 6662.2 | 12381 | 5145 | 21152.7 | 7051.8 | 8905.6 | 3578.1 | 5650.7 | 26158.1
Point (c) UCAP Level, MW | 142645.9 | 56969.6 | 33058.2 | 14427.4 | 11389.2 | 5784.1 | 2937.4 | 7003.2 | 13014.6 | 5408.4 | 22235.3 | 7412.7 | 9361.4 | 3761.3 | 5939.9 | 27496.9
Nominated PRD Value, MW | 224 | 224 | 14 | 210 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0
VRR Curve adjusted for PRD:
Point (a1) UCAP Price, $/MW-Day | 451.61 | 456.19 | 466.32 | 466.35 |  |  |  | 466.35 |  |  |  | 466.35
Point (b1) UCAP Price, $/MW-Day | 171.61 | 188.24 | 233.16 | 100.93 |  |  |  | 167.85 |  |  |  | 34.01
Point (prd1) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  | 0.01 |  |  |  | 0.01
Point (prd2) UCAP Price, $/MW-Day | 0.01 | 0.01 | 0.01 | 0.01 |  |  |  | 0.01 |  |  |  | 0.01
Point (c) UCAP Price, $/MW-Day | 0 | 0 | 0 | 0 |  |  |  | 0 |  |  |  | 0
Point (a1) UCAP Level, MW | 131884.1 | 52545.2 | 30599.8 | 13163.1 |  |  |  | 6414.8 |  |  |  | 6737.7
Point (b1) UCAP Level, MW | 135490.3 | 53985.5 | 31435.6 | 13527.8 |  |  |  | 6591.8 |  |  |  | 6925.1
Point (prd1) UCAP Level, MW | 142435.2 | 56759.2 | 33045 | 14230.2 |  |  |  | 6932.8 |  |  |  | 7285.9
Point (prd2) UCAP Level, MW | 142645.5 | 56969.5 | 33058.1 | 14427.3 |  |  |  | 7003.2 |  |  |  | 7412.6
Point (c) UCAP Level, MW | 142645.9 | 56969.6 | 33058.2 | 14427.4 |  |  |  | 7003.2 |  |  |  | 7412.7
Pre-Auction Credit Rate, $/MW | 41757.83 | 45803.85 | 56735.6 | 24559.03 | 60402.03 | 60402.03 | 44836.6 | 40843.5 | 43212.35 | 43212.35 | 54808.4 | 8274.55 | 47488.33 | 34926.85 | 37458.13 | 27865.93
Participant-Funded ICTRs Awarded | NA | 1557 | 40 | NA | 1070 | 639 | 72 | NA | NA | NA | 1376 | 65.7 | NA | NA | 155 | NA
FRR Load Requirement (% Obligation):
Minimum Internal Resource Requirement | NA | 97.7% | 79.4% | 44.5% | NA | NA | 34.3% | NA | NA | NA | 88% | 15.5% | NA | NA | 4.4% | 95.2%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and FRR load.
LDA/Zone | CETO (Capacity Emergency Transfer Objective) | CETL (Capacity Emergency Transfer Limit) | CETL to CETO Ratio % | 2023 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load | LDA/Zone
RTO | NA | NA | NA | 148659.4 | 153883.0351 | NA | 11597.2834 | 142285.7517 | RTO
AE | 2025 | >2,328.8 | >115% | 2310 | 2355 | 1.0195 | 0 | 2355 | AE
AEP | -2203 | * | * | 21723 | 23296 | 1 | 10744.4 | 12551.6 | AEP
APS | 1606 | >1,846.9 | >115% | 8452.2 | 8836 | 1.0454 | 0 | 8836 | APS
ATSI | 4406 | 10846 | 246.2% | 11550 | 11978 | 1.0371 | 0 | 11978 | ATSI
ATSI-CLEVELAND | 3428 | 4713 | 137.5% | NA | 4012.63 | NA | 0 | NA | ATSI-CLEVELAND
BGE | 4620 | 6031 | 130.5% | 6200 | 6259 | 1.0095 | 0 | 6259 | BGE
COMED | -3270 | 5254 | * | 18720 | 18839 | 1.0064 | 0 | 18839 | COMED
DAYTON | 2603 | 3931 | 151% | 3140 | 3135 | 0.99841 | 0 | 3135 | DAYTON
DEOK | 2797 | 5387 | 192.6% | 5030 | 5076 | 1.0091 | 831.9392 | 4244.0608 | DEOK
DLCO | 1873 | >2,154.0 | >115% | 2620 | 2622 | 1.0008 | 0 | 2622 | DLCO
DOM | 5156 | 5164 | 100.2% | 21200 | 23021 | 1.0859 | 0 | 23021 | DOM
DPL | 1161 | >1,335.2 | >115% | 3660 | 3673 | 1.0036 | 0 | 3673 | DPL
DPL SOUTH | 1435 | 2030 | 141.5% | NA | 2236.857 | NA | 0 | 2236.857 | DPL SOUTH
EKPC | 883 | >1,015.5 | >115% | 1950 | 2362.0351 | 1.2113 | 20.9442 | 2341.091 | EKPC
JCPL | 3779 | >4,345.9 | >115% | 5730 | 5719 | 0.99808 | 0 | 5719 | JCPL
METED | 1503 | >1,728.5 | >115% | 2900 | 2958 | 1.02 | 0 | 2958 | METED
OVEC | NA | NA | NA | 60 | 60 | 1 | 0 | 60 | OVEC
PECO | 2900 | >3,335.0 | >115% | 8030 | 8119 | 1.0111 | 0 | 8119 | PECO
PENLC | 314 | >361.1 | * | 2730 | 2745 | 1.0055 | 0 | 2745 | PENLC
PEPCO | 4336 | 6572 | 151.6% | 5810 | 5818 | 1.0014 | 0 | 5818 | PEPCO
PL (incl. UGI) | -145 | 4681 | * | 7034.2 | 7040 | 1.0008 | 0 | 7040 | PL (incl. UGI)
PS | 6389 | 8501 | 133.1% | 9420 | 9584 | 1.0174 | 0 | 9584 | PS
PS NORTH | 2957 | 4282 | 144.8% | NA | 4878.256 | NA | 0 | 4878.256 | PS NORTH
RECO | NA | NA | NA | 390 | 388 | 0.99487 | 0 | 388 | RECO
EMAAC | 5335 | 8717 | 163.4% | NA | 29838 | NA | 0 |  | EMAAC
SWMAAC | 6772 | 8467 | 125% | NA | 12077 | NA | 0 |  | SWMAAC
Western MAAC | -6889 | * | * | NA | 12743 | NA | 0 |  | Western MAAC
MAAC | -1207 | * | * | NA | 54658 | NA | 0 |  | MAAC
Western PJM | -2334 | * | * | NA | 76204.0351 | NA | 11597.2834 |  | Western PJM
* LDA has adequate internal resources to meet the reliability criterion.
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation |  | Limiting Facility
MAAC | Thermal |  | Sporn - Kyger Creek 345 kV line in pre-contingency
EMAAC | Voltage |  | Voltage collapse for the loss of Keeney - Rock Springs 500 kV line
SWMAAC | Voltage |  | Voltage collapse for the loss of Brandon Shore unit 1
PS | Thermal |  | Brunswick - Meadow Road 230 kV ckt Z2331 for the loss of Metuchen -Pierson Ave - Meadow Rd- Deans 230 kV ckt s2219 Aldene - Stanley Terrance 230kV for the loss of WEST ORANGE - ORANGE HEIGHTS 230 kV Roseland - Williams PIPE 230 kV for the loss of Roseland - Cedar Grove 230 kV Kitattiny - Bush 230 kVline for the loss of Portland - Martins Creek 230 kV
PSNORTH | Thermal |  | Aldene - Stanley Terrance 230kV for the loss of WEST ORANGE - ORANGE HEIGHTS 230 kV Roseland - Williams PIPE 230 kV for the loss of Roseland - Cedar Grove 230 kV
DPLSOUTH | Thermal |  | Cool Spring - Milford 230 kV for the loss of the Indian River - Mildord 230 kV
PEPCO | Thermal |  | North West 326 - Conastone 230 kV line for the loss of Brighton - Conastone 500 kV line North West 326 - Conastone 230 kV line for the loss of North West 311 - Conastone 230 kV line
ATSI | Thermal |  | 345 kV line Wylie Ridge - Toronto for the loss of two 345/138 kV transformers at Wylie Ridge
ATSI-CLEVELAND | Thermal |  | Austinburg - Sanborn 138 kV for the loss of Stacy - Leroy Center 138 kV Barberton - Alcoa 138 kV for the loss of Juniper - Star 345 kV
COMED | Thermal |  | Conastone - Peach Bottom 500 kV line pre contingency overload
BGE | Voltage |  | Voltage drop at various buses including PUMPHREY 115 kV bus for the loss of Brighton - Conastone 500 kV line
PL | Thermal |  | Wescosville 500/138 kV transformer pre-contingency
DAYTON | Thermal |  | Wylie Ridge - Toronto 345 kV for the loss of Wylie Ridge 345/138 kV transformer #1 and #2
DEOK | Thermal |  | Pierce 345/138 kV transformer for the loss of Pierce - Foster 345 kV line and Conastone - Peachbottom pre-contingency
DOM | Thermal |  | Goose Creek - Asburn 230 kV for the loss of Pleasant View - Ashburn - Beaumeade 230 kV Dickerson - Dickerson H 230 kV ckt 2 for the loss of Dickerson - Dickerson H 230 kV ckt 1
4/11/2024 - Added PRD to Planning Parameters
4/11/2024 - Note: EE and FRR data is not currently final and will be added to the Planning Parameters after the appropriate submission deadlines
6/5/2024 - Updated to include FRR values

## Net CONE
RPM CONE and E&AS Values for 2025/2026 Base Residual Auction
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price / Pool-Wide Average Accredited UCAP Factor
Reference Resource Accredited UCAP Factor | [6 empty] | 79% | Based on reference resource AUCAPF
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, Dayton, DEOK, Dominion, Duquesne (DLCo), EKPC, OVEC
CONE Area 4: MetEd, Penelec, PPL
CONE Area 5: ComEd
Zone/LDA | 2024/2025 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Escalation | 2025/2026 BRA CONE: Levelized Revenue Requirement, $/MW-Year | Gross CONE, $/MW-Day, UCAP Price | Historic Net Energy Revenue Offset, $/MW-Year | Ancillary Services Offset, $/MW-Year per Tariff | Net E&AS Revenue Offset, $/MW-Year | Net CONE, $/MW-Day, ICAP Price | Net CONE, $/MW-Day, UCAP Price | LDA Modeled with VRR Curve
CONE Area 1 | 123117.5818 | 1.0812 | 133119.5069 | 461.66
AE |  |  |  | 461.66 | 36135.916 | 2199 | 38334.916 | 259.6838 | 328.71
DPL |  |  |  | 461.66 | 60078.1699 | 2199 | 62277.1699 | 194.0886 | 245.68 | DPL SOUTH
JCPL |  |  |  | 461.66 | 37086.1608 | 2199 | 39285.1608 | 257.0804 | 325.42
PE |  |  |  | 461.66 | 34809.8431 | 2199 | 37008.8431 | 263.3169 | 333.31
PSEG |  |  |  | 461.66 | 35485.0857 | 2199 | 37684.0857 | 261.4669 | 330.97 | PS, PSEG NORTH
RECO |  |  |  | 461.66 | 44080.8687 | 2199 | 46279.8687 | 237.9168 | 301.16
EMAAC |  |  |  | 461.66 |  |  |  | 245.6 | 310.88 | EMAAC
CONE Area 2 | 123919.5337 | 1.0852 | 134473.3557 | 466.35
BGE |  |  |  | 466.35 | 119201.5571 | 2199 | 121400.5571 | 35.8159 | 45.34 | BGE
PEPCO |  |  |  | 466.35 | 67741.8712 | 2199 | 69940.8712 | 176.8013 | 223.8 | PEPCO
SWMAAC |  |  |  | 466.35 |  |  |  | 106.31 | 134.57 | SWMAAC
CONE Area 4 | 118504.999 | 1.0669 | 126433.334 | 438.47
METED |  |  |  | 438.47 | 68747.2741 | 2199 | 70946.2741 | 152.0193 | 192.43
PENELEC |  |  |  | 438.47 | 74117.8441 | 2199 | 76316.8441 | 137.3055 | 173.8
PPL |  |  |  | 438.47 | 49202.861 | 2199 | 51401.861 | 205.5657 | 260.21 | PPL
MAAC |  |  |  | 456.19 |  |  |  | 198.27 | 250.98 | MAAC
CONE Area 3 | 118329.5519 | 1.0826 | 128102.4011 | 444.26
AEP |  |  |  | 444.26 | 74245.6619 | 2199 | 76444.6619 | 141.5281 | 179.15
APS |  |  |  | 444.26 | 86470.1406 | 2199 | 88669.1406 | 108.0363 | 136.75
ATSI |  |  |  | 444.26 | 57626.9012 | 2199 | 59825.9012 | 187.0589 | 236.78 | ATSI, ATSI CLEVELAND
DAYTON |  |  |  | 444.26 | 70718.036 | 2199 | 72917.036 | 151.1928 | 191.38 | DAYTON
DEOK |  |  |  | 444.26 | 66720.9415 | 2199 | 68919.9415 | 162.1437 | 205.25 | DEOK
DLCO |  |  |  | 444.26 | 68385.8314 | 2199 | 70584.8314 | 157.5824 | 199.47
DOM |  |  |  | 444.26 | 81876.5097 | 2199 | 84075.5097 | 120.6216 | 152.69
EKPC |  |  |  | 444.26 | 53735.6204 | 2199 | 55934.6204 | 197.7199 | 250.28
OVEC |  |  |  | 444.26 | 68725.0827 | 2199 | 70924.0827 | 156.6529 | 198.29
CONE Area 5 | 118330 | NA | 128986.3077 | 447.33
COMED |  |  |  | 447.33 | 39305.9493 | 2199 | 41504.9493 | 237.2533 | 300.32 | COMED
RTO | 120440.3333 |  | 130222.9811 | 451.61 | 62046.4616 | 2199 | 64245.4616 | 180.7603 | 228.81 | RTO
CONE Area 5 based on asset life factor of CONE Area 3. 25/26: 1.0069; 27/28: 1.0376; 28/29: 1.0581; 29/30: 1.0818

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2025/2026 model
Upgrade ID | Description | Transmission Owner
s2609.2 | Install (1) 1440 MVA 500-230 kV transformer at Goose Creek Substation. Extend the existing 500kV ring bus at Goose Creek Substation to be set up for a future six-breaker ring arrangement. One breaker to be installed initially creating a five-breaker ring bus. Install a new 230kV ring bus at Goose Creek Substation to be set up for a future four-breaker ring arrangement. Three 230kV breakers to be installed initially. Cut and extend line #227 Belmont-Beaumeade into Goose Creek Substation. | Dominion
b3718.14 | Construct a new 230 kV transmission line for ~3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the 500 kV line. New conductor to have a minimum summer normal rating of 1573 MVA. | Dominion
b3718.13 | Cut and loop 230 kV Line #2079 (Sterling Park-Dranesville) into Davis Drive substation and install two GIS 230 kV breakers. | Dominion
b3718.12 | Upgrade 4-500 kV breakers (total) to 63 kA on either end of 500 kV Line #584 (Loudoun-Mosby) | Dominion
b3718.11 | Upgrade 4-500 kV breakers (total) to 63kA on either end of 500 kV Line #502 (Loudoun-Mosby) | Dominion
b3718.10 | Reconductor ~1.61 miles of 230 kV line #9349 (Sojourner-Mars) to achieve a summer rating of 1574 MVA. | Dominion
b3718.9 | Reconductor ~3.98 miles of 230 kV line #2218 (Sojourner-Runway-Shellhorn) to achieve a summer rating of 1574 MVA. | Dominion
b3718.8 | Reconductor ~0.84 miles of 230 kV line #2223 (Lockridge-Roundtable) to achieve a summer rating of 1574 MVA. | Dominion
b3718.7 | Reconductor ~2.17 miles of 230 kV line #2188 (Lockridge-Greenway-Shellhorn) to achieve a summer rating of 1574 MVA. | Dominion
b3718.6 | Reconductor ~0.64 miles of 230 kV line #2186 (Enterprise-Shellhorn) to achieve a summer rating of 1574 MVA. | Dominion
b3718.5 | Reconductor ~1.52 miles of 230 kV line #2031 (Enterprise-Greenway-Roundtable) to achieve a summer rating of 1574 MVA. | Dominion
b3718.4 | Reconductor ~0.62 miles of 230 kV line #2214 (Buttermilk-Roundtable) to achieve a summer rating of 1574 MVA. | Dominion
b3726 | Install two new 500 kV breakers on the existing open SVC string to create a new bay position. Relocate & Reterminate facilities as necessary to move the 500 kV SVC into the new bay position and Install a 500 kV breaker on the 500/138 kV #3 transformer. Upgrade relaying at Black Oak substation. | APS
Key Transmission Upgrades included for 2024/2025 model but not included for 2025/2026 model
Upgrade ID | Description | Transmission Owner
None