## Notes
Thermal analysis column headings
Column Heading | Title | Description
Reserved(FG# assinged by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Fr Bus | From Bus Number | PSSE model bus number corresponding to the FROM bus of a facility identified as a potential violation
Fr Name | From Bus Name | PSSE model bus name corresponding to the FROM bus of a facility identified as a potential violation
To Bus | To Bus Number | PSSE model bus number corresponding to the TO bus of a facility identified as a potential violation
To Name | To Bus Name | PSSE model bus name corresponding to the TO bus of a facility identified as a potential violation
Tert Bus | Tertiary Bus Number | PSSE model bus number corresponding to the tertiary bus of a facility identified as a potential violation
Tert Name | Tertiary Bus Name | PSSE model bus name corresponding to the tertiary bus of a facility identified as a potential violation
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Facility Rating | Applicable thermal rating (MVA) of facility
DC Ld(%) | Direct Current Loading percentage | Percentage above Line Rating determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above Line Rating determined from AC testing
Cont Type | Contingency Type | N-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Conductor Rating (MVA) | Conductor Rating | Normal/Long Term Emergency/Short Term Emergency/Load Dump ratings of conductor
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Magnitude analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Upper/Lower Limit | High/Low Voltage Limit (P.U.) | Threshold of Per Unit High/Low voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Type | Contingency 2 Type | N-1-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower)
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Drop analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Vdrop (%) | Voltage Drop | The percentage that the voltage has dropped as a result of the contingency
Delta Voltage Limit | Voltage Drop Limit | Threshold of percentage drop, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Short Circuit analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | Short Circuit model bus number where breaker is located
Bus Name | Bus Name | Aspen bus name and voltage where breaker is located
Bus KV | BUS Voltage | Nominal BUS voltage
Area | Area Number | Area number of bus identified as potential violation
Breaker | Breaker Name | Breaker name as given by Transmission Owner
Rating Type | Type of Breaker | Symmetrical (S) or Total (T) rated type of breaker
DUTY_P | Duty Percentage | The percentage of the asymmetrical fault current divided by breaker capacity
DUTY_A | Asymmetrical Fault Current | The combination of the symmetrical component and the direct current component of the current.
BKR_CAPA (A) | Breaker Capacity | Breaker’s derated interrupting capability, (A)
Pre-fault Voltage (KV) | Pre-fault KV | Voltage on the bus prior to fault event
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Stability analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis dynamics case info. | Analysis dynamics case info. | Dynamics case year, loading condition, MMWG Series. For example, MMWG 2018 Series 2023 SLL case.
Stability issue category | Stability issue category | Stability issue category: transient stability or damping or dynamic voltage recovery or voltage ride through
Bus # | Bus number | Bus number of the identified plant or station in the analysis power flow model.
Bus Name | Bus name | Bus name of the identified plant or station in the analysis power flow model.
Area | Area | Area number of the identified plant or station.
Stability Contingency description | Contingency description | Detailed contingency description that causes the identified potential stability issue including sequence and fault clearing times.
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Other analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Facility Name | Facility Name | Facilities such as line, substation, generator, etc.
Violations details | Violations details | TO to describe the details of the violation
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Purpose of FERC FORM 715 VIOLATION SUBMISSIONS:
PJM seeks Transmission Owner (TO) criteria violation submissions on facilities in accordance with Local TO criteria. This would also include violations which are not power flow violations of criteria.
Criteria applied by Transmission Owner:
FERC Form 715 Analysis (Thermal/Voltage Magnitude/Voltage Drop/Short Circuit/Stability/Other)
TERMINOLOGY USED IN TEMPLATE:
Descriptions of the column headings used in each Excel tab are provided below.
ANALYSIS PROCEDURE:
Transmission Owners are expected to identify FERC Form 715 violations. All violations are to be captured and recorded in the applicable Excel tab. Please use the corresponding tabs based on the type of violation below:
  * FERC Form 715 Thermal tab should be used to enter thermal violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Magnitude tab should be used to enter voltage magnitude violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Drop tab should be used to enter voltage drop/rise violations associated with FERC Form 715 criteria
  * FERC Form 715 Short Circuit tab should be used to enter short circuit violations associated with FERC Form 715 criteria
  * FERC Form 715 Stability tab should be used to enter stability violations associated with FERC Form 715 criteria
  * FERC Form 715 Other tab should be used to enter violations associated with FERC Form 715 criteria which can not be included in the other tabs
TRANSMISSION OWNER CRITERIA:
In addition to the NERC and PJM criteria included in RTEP studies, PJM also considers Transmission Owner specific criteria. Individual TO criteria can be found at the following link:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx

## FERC Form 715 Thermal
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Contingency 1 description | Cont 2 Name | Contingency 2 description | Transformer Capability/ Line Conductor Rating (SN/SE/WN/WE MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment | M3 Process Status
AEP-T1 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243169 | 05HAVILND2 | 245898 | 05PAULDING |  |  | 1 | 69 | 205 | 50 |  | 116.56 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-T2 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243169 | 05HAVILND2 | 245898 | 05PAULDING |  |  | 1 | 69 | 205 | 50 |  | 117.11 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-T3 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243179 | 05S HICKSV | 245886 | 05MARK CEN |  |  | 1 | 69 | 205 | 53 |  | 104.57 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | 257/257/325/325 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T4 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243179 | 05S HICKSV | 245886 | 05MARK CEN |  |  | 1 | 69 | 205 | 53 |  | 104.68 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | 257/257/325/325 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T5 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243179 | 05S HICKSV | 245886 | 05MARK CEN |  |  | 1 | 69 | 205 | 53 |  | 103.7 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | 257/257/325/325 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T6 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243179 | 05S HICKSV | 245886 | 05MARK CEN |  |  | 1 | 69 | 205 | 53 |  | 103.66 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | 257/257/325/325 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T7 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 62 |  | 117.25 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T8 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 62 |  | 116.7 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T9 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 62 |  | 117.26 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T10 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 62 |  | 114.29 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T11 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 125.49 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T12 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 63 |  | 120.1 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T13 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 63 |  | 120.08 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T14 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244949 | 05GAVIN1 | 246740 | 05MEIGS |  |  | 1 | 69 | 205 | 82 |  | 101.74 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T15 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244949 | 05GAVIN1 | 246740 | 05MEIGS |  |  | 1 | 69 | 205 | 82 |  | 101.75 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T16 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245637 | 05TIFFIN C | 247481 | 05HOLME STSS |  |  | 1 | 69 | 205 | 39 |  | 114.81 | N-1-1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | AEP_P1-2_#5151_710 | OPEN BRANCH FROM BUS 243015 TO BUS 243130 CKT 1 / 243015 05GREENL 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243015 TO BUS 245621 CKT 3 / 243015 05GREENL 138 245621 05GREENLAW 69.0 3 | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T17 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245637 | 05TIFFIN C | 247481 | 05HOLME STSS |  |  | 1 | 69 | 205 | 39 |  | 114.13 | N-1-1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | AEP_P1-3_#11863_05GREENL 138_3 | OPEN BRANCH FROM BUS 243015 TO BUS 245621 CKT 3 / 243015 05GREENL 138 245621 05GREENLAW 69.0 3 | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T18 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245637 | 05TIFFIN C | 247481 | 05HOLME STSS |  |  | 1 | 69 | 205 | 39 |  | 114.13 | N-1-1 | AEP_P1-3_#11863_05GREENL 138_3 | OPEN BRANCH FROM BUS 243015 TO BUS 245621 CKT 3 / 243015 05GREENL 138 245621 05GREENLAW 69.0 3 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T19 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245637 | 05TIFFIN C | 247481 | 05HOLME STSS |  |  | 1 | 69 | 205 | 39 |  | 114.81 | N-1-1 | AEP_P1-2_#5151_710 | OPEN BRANCH FROM BUS 243015 TO BUS 243130 CKT 1 / 243015 05GREENL 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243015 TO BUS 245621 CKT 3 / 243015 05GREENL 138 245621 05GREENLAW 69.0 3 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T20 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245637 | 05TIFFIN C | 247481 | 05HOLME STSS |  |  | 1 | 69 | 205 | 39 |  | 101.44 | N-1-1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | AEP_P1-2_#5151_710 | OPEN BRANCH FROM BUS 243015 TO BUS 243130 CKT 1 / 243015 05GREENL 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243015 TO BUS 245621 CKT 3 / 243015 05GREENL 138 245621 05GREENLAW 69.0 3 | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T21 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.83 | N-1-1 | AEP_P1-2_#11825_11937 | OPEN BRANCH FROM BUS 245663 TO BUS 245679 CKT 1 / 245663 05HOWARD 69.0 245679 05WILLARD 69.0 1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T22 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.83 | N-1-1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | AEP_P1-2_#11825_11937 | OPEN BRANCH FROM BUS 245663 TO BUS 245679 CKT 1 / 245663 05HOWARD 69.0 245679 05WILLARD 69.0 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T23 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.05 | N-1-1 | AEP_P1-3_#11866_05HOWARD 138_1 | OPEN BRANCH FROM BUS 243024 TO BUS 245666 CKT 1 / 243024 05HOWARD 138 245666 05HOWRD1EQ 999 1 OPEN BRANCH FROM BUS 245663 TO BUS 245666 CKT 1 / 245663 05HOWARD 69.0 245666 05HOWRD1EQ 999 1 OPEN BRANCH FROM BUS 243024 TO BUS 243039 CKT 1 / 243024 05HOWARD 138 243039 05MELMOR 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243061 CKT 1 / 243024 05HOWARD 138 243061 05NLEXTN 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243100 CKT 1 / 243024 05HOWARD 138 243100 05SHELGH 138 1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T24 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.05 | N-1-1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | AEP_P1-3_#11866_05HOWARD 138_1 | OPEN BRANCH FROM BUS 243024 TO BUS 245666 CKT 1 / 243024 05HOWARD 138 245666 05HOWRD1EQ 999 1 OPEN BRANCH FROM BUS 245663 TO BUS 245666 CKT 1 / 245663 05HOWARD 69.0 245666 05HOWRD1EQ 999 1 OPEN BRANCH FROM BUS 243024 TO BUS 243039 CKT 1 / 243024 05HOWARD 138 243039 05MELMOR 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243061 CKT 1 / 243024 05HOWARD 138 243061 05NLEXTN 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243100 CKT 1 / 243024 05HOWARD 138 243100 05SHELGH 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T25 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 102.5 | N-1-1 | AEP_P1-2_#711_6224 | OPEN BRANCH FROM BUS 242926 TO BUS 242928 CKT 1 / 242926 05MALIS 765 242928 05MARYSV 765 1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T26 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.99 | N-1-1 | AEP_P1-2_#6392_9217 | OPEN BRANCH FROM BUS 243070 TO BUS 246770 CKT 1 / 243070 05OHIOCT 138 246770 05DRESDN 138 1 REMOVE UNIT 1A FROM BUS 247234 / 247234 05DREG1A 18.0 1A REMOVE UNIT 1B FROM BUS 247235 / 247235 05DREG1B 18.0 1B REMOVE UNIT 1S FROM BUS 247236 / 247236 05DREG1S 18.0 1S | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T27 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.02 | N-1-1 | AEP_P1-2_#7105_8900707 | OPEN BRANCH FROM BUS 243024 TO BUS 243039 CKT 1 / 243024 05HOWARD 138 243039 05MELMOR 138 1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T28 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 102.6 | N-1-1 | AEP_P1-3_#7222_05MALIS 765_1 | OPEN BRANCH FROM BUS 242926 TO BUS 242928 CKT 1 / 242926 05MALIS 765 242928 05MARYSV 765 1 OPEN BRANCH FROM BUS 242926 TO BUS 246751 CKT 1 / 242926 05MALIS 765 246751 05VASSEL 765 1 OPEN BRANCH FROM BUS 242926 TO BUS 243538 CKT 1 / 242926 05MALIS 765 243538 05MALISX 138 1 OPEN BRANCH FROM BUS 243537 TO BUS 243538 CKT SR / 243537 05MALIS 138 243538 05MALISX 138 SR OPEN BRANCH FROM BUS 243537 TO BUS 243538 CKT ZB / 243537 05MALIS 138 243538 05MALISX 138 ZB | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T29 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 100.98 | N-1-1 | PJM_PLANT DRESDEN | REMOVE MACHINE 1A FROM BUS 247234 REMOVE MACHINE 1B FROM BUS 247235 REMOVE MACHINE 1S FROM BUS 247236 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T30 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 42 |  | 107.71 | N-1-1 | AEP_P1-2_#7441_100545 | OPEN BRANCH FROM BUS 242928 TO BUS 246999 CKT 1 / 242928 05MARYSV 765 246999 05SORENS 765 1 | AEP_P1-2_#15232 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 | 39/39/49/49 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T31 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 106.74 | N-1-1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | AEP_P1-2_#11829_5541 | OPEN BRANCH FROM BUS 245650 TO BUS 247429 CKT 1 / 245650 05BLOOMVL 69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 245650 TO BUS 245674 CKT 1 / 245650 05BLOOMVL 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245674 CKT 1 / 245655 05CARROTHR 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245621 TO BUS 245646 CKT 1 / 245621 05GREENLAW 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245646 CKT 1 / 245635 05WROCKWSS 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 247429 CKT 1 / 244726 05HONEYCRKSS69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245671 CKT 1 / 244726 05HONEYCRKSS69.0 245671 05REPUBLC8 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245635 CKT 1 / 244726 05HONEYCRKSS69.0 245635 05WROCKWSS 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245636 CKT 1 / 245635 05WROCKWSS 69.0 245636 05SYCAMOR8 69.0 1 | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T32 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 106.74 | N-1-1 | AEP_P1-2_#11829_5541 | OPEN BRANCH FROM BUS 245650 TO BUS 247429 CKT 1 / 245650 05BLOOMVL 69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 245650 TO BUS 245674 CKT 1 / 245650 05BLOOMVL 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245674 CKT 1 / 245655 05CARROTHR 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245621 TO BUS 245646 CKT 1 / 245621 05GREENLAW 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245646 CKT 1 / 245635 05WROCKWSS 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 247429 CKT 1 / 244726 05HONEYCRKSS69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245671 CKT 1 / 244726 05HONEYCRKSS69.0 245671 05REPUBLC8 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245635 CKT 1 / 244726 05HONEYCRKSS69.0 245635 05WROCKWSS 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245636 CKT 1 / 245635 05WROCKWSS 69.0 245636 05SYCAMOR8 69.0 1 | AEP_P1-2_#11827_836 | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T33 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 105.18 | Line w/o Fault | AEP_P2-1_245655 05CARROTHR 69.0 247193 05BULLHDSS 69.0 1 | OPEN BRANCH FROM BUS 245655 TO BUS 247193 CKT 1 |  |  | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T34 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 105.02 | FB | AEP_P4_#15235_05CARROTHR 69.0_X | OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245674 CKT 1 / 245655 05CARROTHR 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 247193 CKT 1 / 245655 05CARROTHR 69.0 247193 05BULLHDSS 69.0 1 REMOVE SWSHUNT FROM BUS 245655 / 245655 05CARROTHR 69.0 REMOVE LOAD D1 FROM BUS 245655 / 245655 05CARROTHR 69.0 D1 |  |  | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T35 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 104.96 | FB | AEP_P4_#12279_05CARROTHR 69.0_A | OPEN BRANCH FROM BUS 245650 TO BUS 247429 CKT 1 / 245650 05BLOOMVL 69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 245650 TO BUS 245674 CKT 1 / 245650 05BLOOMVL 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 247193 CKT 1 / 245655 05CARROTHR 69.0 247193 05BULLHDSS 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245674 CKT 1 / 245655 05CARROTHR 69.0 245674 05ST.STEPHSS69.0 1 OPEN BRANCH FROM BUS 245621 TO BUS 245646 CKT 1 / 245621 05GREENLAW 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245646 CKT 1 / 245635 05WROCKWSS 69.0 245646 05E.TIFF2 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 247429 CKT 1 / 244726 05HONEYCRKSS69.0 247429 05N.BLOOMVSS69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245671 CKT 1 / 244726 05HONEYCRKSS69.0 245671 05REPUBLC8 69.0 1 OPEN BRANCH FROM BUS 244726 TO BUS 245635 CKT 1 / 244726 05HONEYCRKSS69.0 245635 05WROCKWSS 69.0 1 OPEN BRANCH FROM BUS 245635 TO BUS 245636 CKT 1 / 245635 05WROCKWSS 69.0 245636 05SYCAMOR8 69.0 1 REMOVE SWSHUNT FROM BUS 245655 / 245655 05CARROTHR 69.0 REMOVE LOAD D1 FROM BUS 245655 / 245655 05CARROTHR 69.0 D1 |  |  | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T36 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 105.02 | Bus | AEP_P2-2_#14114_05CARROTHR 69.0_1 | OPEN BRANCH FROM BUS 245655 TO BUS 247193 CKT 1 / 245655 05CARROTHR 69.0 247193 05BULLHDSS 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245674 CKT 1 / 245655 05CARROTHR 69.0 245674 05ST.STEPHSS69.0 1 REMOVE SWSHUNT FROM BUS 245655 / 245655 05CARROTHR 69.0 REMOVE LOAD D1 FROM BUS 245655 / 245655 05CARROTHR 69.0 D1 |  |  | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T37 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 44 |  | 104.63 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T38 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 44 |  | 121.89 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T39 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 44 |  | 121.9 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T40 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 44 |  | 104.55 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T41 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 44 |  | 104.55 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T42 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 56 |  | 103.19 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T43 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 244760 | 05PTPLEASN |  |  | 1 | 69 | 205 | 56 |  | 103.19 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP017 | Need
AEP-T44 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.35 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T45 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.35 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T46 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.36 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T47 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.36 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T48 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.35 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T49 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244040 | 05CLOV 1 | 244057 | 05ING RAND |  |  | 1 | 69 | 205 | 90 |  | 112.43 | N-1-1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T50 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244057 | 05ING RAND | 244067 | 05MONTERAV |  |  | 1 | 69 | 205 | 90 |  | 111.67 | N-1-1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T51 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244040 | 05CLOV 1 | 244057 | 05ING RAND |  |  | 1 | 69 | 205 | 90 |  | 111.96 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T52 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244057 | 05ING RAND | 244067 | 05MONTERAV |  |  | 1 | 69 | 205 | 90 |  | 111.22 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T53 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 107.59 | N-1-1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T54 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244040 | 05CLOV 1 | 244057 | 05ING RAND |  |  | 1 | 69 | 205 | 90 |  | 112.43 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T55 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244040 | 05CLOV 1 | 244057 | 05ING RAND |  |  | 1 | 69 | 205 | 90 |  | 112.41 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T56 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 107.23 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T57 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244057 | 05ING RAND | 244067 | 05MONTERAV |  |  | 1 | 69 | 205 | 90 |  | 111.67 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T58 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244057 | 05ING RAND | 244067 | 05MONTERAV |  |  | 1 | 69 | 205 | 90 |  | 111.64 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T59 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244040 | 05CLOV 1 | 244057 | 05ING RAND |  |  | 1 | 69 | 205 | 90 |  | 100.21 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | AEP_P1-3_#11378_05CATAWB 138_1 | OPEN BRANCH FROM BUS 242583 TO BUS 244034 CKT 1 / 242583 05CATAWB 138 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244034 CKT 1 / 244033 05CATAWBA 69.0 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244032 TO BUS 244034 CKT 1 / 244032 05CATAWBA 34.5 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244037 CKT 1 / 244033 05CATAWBA 69.0 244037 05CLEVEL 69.0 1 OPEN BRANCH FROM BUS 244033 TO BUS 244062 CKT 1 / 244033 05CATAWBA 69.0 244062 05MASON CR 69.0 1 REMOVE SWSHUNT FROM BUS 244033 / 244033 05CATAWBA 69.0 OPEN BRANCH FROM BUS 244032 TO BUS 244079 CKT 1 / 244032 05CATAWBA 34.5 244079 05VETHOSPZ 34.5 1 | 102/102/129/129 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T60 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 107.55 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-3_#12037_05HUNTCT 138_1 | OPEN BRANCH FROM BUS 242676 TO BUS 244101 CKT 1 / 242676 05HUNTCT 138 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 244101 TO BUS 244102 CKT 1 / 244101 05HUNTCTEQ 999 244102 05HUNTCRT1 69.0 1 OPEN BRANCH FROM BUS 244054 TO BUS 244101 CKT 1 / 244054 05HUNTNGTN 34.5 244101 05HUNTCTEQ 999 1 OPEN BRANCH FROM BUS 242676 TO BUS 247631 CKT 1 / 242676 05HUNTCT 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 REMOVE SWSHUNT FROM BUS 242676 / 242676 05HUNTCT 138 | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T61 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244067 | 05MONTERAV | 244097 | 05HUNTCRT2 |  |  | 1 | 69 | 205 | 90 |  | 107.59 | N-1-1 | AEP_P1-3_#11370_05ROANO2 138_5 | OPEN BRANCH FROM BUS 242774 TO BUS 247631 CKT 1 / 242774 05ROANO2 138 247631 05BENNINGTON 138 1 OPEN BRANCH FROM BUS 242601 TO BUS 242774 CKT 1 / 242601 05CLEARB 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242656 TO BUS 242774 CKT 1 / 242656 05GRASSH 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242724 TO BUS 242774 CKT 1 / 242724 05MOSELEY 138 242774 05ROANO2 138 1 OPEN BRANCH FROM BUS 242773 TO BUS 242774 CKT Z1 / 242773 05ROANO1 138 242774 05ROANO2 138 Z1 OPEN BRANCH FROM BUS 242774 TO BUS 246981 CKT 1 / 242774 05ROANO2 138 246981 05SUNSCA 138 1 OPEN BRANCH FROM BUS 242774 TO BUS 244073 CKT 1 / 242774 05ROANO2 138 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 242774 TO BUS 244072 CKT 1 / 242774 05ROANO2 138 244072 05ROANOKE 34.5 1 OPEN BRANCH FROM BUS 244030 TO BUS 244073 CKT 1 / 244030 05CAMPBEL1 69.0 244073 05ROANOKE 69.0 1 OPEN BRANCH FROM BUS 244073 TO BUS 244098 CKT 1 / 244073 05ROANOKE 69.0 244098 05WALNUTA2 69.0 1 OPEN BRANCH FROM BUS 244072 TO BUS 244084 CKT 1 / 244072 05ROANOKE 34.5 244084 05VTNMILLZ 34.5 1 | AEP_P1-2_#6218_101 | OPEN BRANCH FROM BUS 242607 TO BUS 242676 CKT 1 / 242607 05CLOVRD 138 242676 05HUNTCT 138 1 | 125/125/158/158 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T62 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242714 | 05MEADWV | 242875 | 05MEADWVW |  |  | 1 | 138/69 | 205 | 78 |  | 103.36 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | 60/70/69/78 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP024 | Need
AEP-T63 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 245805 | 05LEIPSIC |  |  | 1 | 69 | 205 | 73 |  | 175.61 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T64 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 245806 | 05DSCHLERT |  |  | 1 | 69 | 205 | 73 |  | 164.94 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T65 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 245810 | 05NLEIP SW |  |  | 1 | 69 | 205 | 73 |  | 164.03 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T66 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 245810 | 05NLEIP SW |  |  | 1 | 69 | 205 | 73 |  | 153.77 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T67 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 245792 | 05E.LEIPSC |  |  | 1 | 138/69 | 205 | 69 |  | 136.66 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 59/69/69/75 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T68 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245757 | 05MCCOMB OP | 245770 | 05NEW LIBR |  |  | 1 | 35 | 205 | 20 |  | 112.05 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 20/20/28/28 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T69 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245730 | 05CAIRO | 245740 | 05E LIMA |  |  | 1 | 69 | 205 | 50 |  | 100.77 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T70 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 245805 | 05LEIPSIC |  |  | 1 | 69 | 205 | 73 |  | 100.86 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T71 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 245805 | 05LEIPSIC |  |  | 1 | 69 | 205 | 73 |  | 100.69 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T72 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 245805 | 05LEIPSIC |  |  | 1 | 69 | 205 | 73 |  | 100.53 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T73 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 245805 | 05LEIPSIC |  |  | 1 | 69 | 205 | 73 |  | 100.01 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | 73/73/91/91 | Yes | Part 4: Thermal Limits |  | Associated with AEP-2020-OH020 | Need
AEP-T74 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 247313 | 05WOLFGL 3EQ | 247314 | 05WOLF GL T3 | 3 | 69/999 | 205 | 130 |  | 103.55 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T75 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244207 | 05REEDYCEQ |  |  | 1 | 35/999 | 205 | 39 |  | 124.12 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 35/39/39/44 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T76 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244207 | 05REEDYCEQ |  |  | 1 | 35/999 | 205 | 39 |  | 124.16 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 35/39/39/44 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T77 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 41 |  | 183.03 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T78 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 41 |  | 183.05 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T79 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244207 | 05REEDYCEQ |  |  | 1 | 35/999 | 205 | 44 |  | 171.68 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 35/39/39/44 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T80 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244207 | 05REEDYCEQ |  |  | 1 | 35/999 | 205 | 44 |  | 171.6 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 35/39/39/44 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T81 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246239 | 05DECATUR | 246261 | 05S DECATU |  |  | 1 | 69 | 205 | 50 |  | 110.51 | N-1-1 | AEP_P1-2_#11910_2683 | OPEN BRANCH FROM BUS 246231 TO BUS 246233 CKT 1 / 246231 05ADAMS- 69.0 246233 05BERNE 69.0 1 | AEP_P1-2_#13952 | OPEN BRANCH FROM BUS 246020 TO BUS 246638 CKT 1 / 246020 05N PORTLN 69.0 246638 05BOCKOVENSS69.0 1 OPEN BRANCH FROM BUS 246020 TO BUS 246022 CKT 1 / 246020 05N PORTLN 69.0 246022 05PORTLAND 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3149
AEP-T82 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246239 | 05DECATUR | 246261 | 05S DECATU |  |  | 1 | 69 | 205 | 50 |  | 110.5 | N-1-1 | AEP_P1-2_#13952 | OPEN BRANCH FROM BUS 246020 TO BUS 246638 CKT 1 / 246020 05N PORTLN 69.0 246638 05BOCKOVENSS69.0 1 OPEN BRANCH FROM BUS 246020 TO BUS 246022 CKT 1 / 246020 05N PORTLN 69.0 246022 05PORTLAND 69.0 1 | AEP_P1-2_#11910_2683 | OPEN BRANCH FROM BUS 246231 TO BUS 246233 CKT 1 / 246231 05ADAMS- 69.0 246233 05BERNE 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3149
AEP-T83 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246386 | 05CONCORD | 246413 | 05WHITAKER |  |  | 1 | 35 | 205 | 37 |  | 102.49 | Line w/o Fault | AEP_P2-1_246381 05BERCADO 34.5 246415 05KLINE 34.5 1 | OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3151
AEP-T84 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 17 |  | 125.91 | FB | AEP_P4_#10542_05COLUMBIA 138_D | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 |  |  | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T85 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246386 | 05CONCORD | 246413 | 05WHITAKER |  |  | 1 | 35 | 205 | 37 |  | 102.84 | FB | AEP_P4_#14782_05KLINE 34.5_CB1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3151
AEP-T86 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246386 | 05CONCORD | 246413 | 05WHITAKER |  |  | 1 | 35 | 205 | 37 |  | 102.81 | FB | AEP_P4_#14141_05KLINE 34.5_B | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246368 CKT 1 / 246300 05BEIGER 34.5 246368 05VIRGIL S 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246302 CKT 1 / 246300 05BEIGER 34.5 246302 05MILES MISH34.5 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3151
AEP-T87 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246386 | 05CONCORD | 246413 | 05WHITAKER |  |  | 1 | 35 | 205 | 37 |  | 102.84 | Bus | AEP_P2-2_#14784_05KLINE 34.5_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3151
AEP-T88 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 25 |  | 208.25 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T89 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 25 |  | 208.02 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T90 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 25 |  | 198.34 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T91 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 25 |  | 198.69 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T92 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 164.66 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T93 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 164.66 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T94 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 164.69 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T95 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 164.69 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T96 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246208 | 05ROBISONP | 246903 | 05DIEBOLD |  |  | 1 | 69 | 205 | 50 |  | 144.36 | N-1-1 | AEP_P1-2_#5609_16777 | OPEN BRANCH FROM BUS 243366 TO BUS 243389 CKT 1 / 243366 05ROB PK12 138 243389 05WALLEN 138 1 | AEP_P1-3_#11928_05INDUST PK1 138_1 | OPEN BRANCH FROM BUS 243316 TO BUS 246127 CKT 1 / 243316 05INDUST PK1 138 246127 05IND PKEQ 999 1 OPEN BRANCH FROM BUS 246127 TO BUS 246129 CKT 1 / 246127 05IND PKEQ 999 246129 05INDUST P 69.0 1 OPEN BRANCH FROM BUS 246127 TO BUS 246128 CKT 1 / 246127 05IND PKEQ 999 246128 05INDUST P 34.5 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243316 TO BUS 243338 CKT 1 / 243316 05INDUST PK1 138 243338 05MCKINLEY3 138 1 OPEN BRANCH FROM BUS 245511 TO BUS 246373 CKT 1 / 245511 05INDUST PK2 138 246373 05SPY RUN1 138 1 OPEN BRANCH FROM BUS 243381 TO BUS 245511 CKT 1 / 243381 05SUMMIT 138 245511 05INDUST PK2 138 1 REMOVE SWSHUNT FROM BUS 243316 / 243316 05INDUST PK1 138 OPEN BRANCH FROM BUS 246129 TO BUS 246133 CKT 1 / 246129 05INDUST P 69.0 246133 05KROEMER SS69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T97 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246208 | 05ROBISONP | 246903 | 05DIEBOLD |  |  | 1 | 69 | 205 | 50 |  | 144.36 | N-1-1 | AEP_P1-3_#11928_05INDUST PK1 138_1 | OPEN BRANCH FROM BUS 243316 TO BUS 246127 CKT 1 / 243316 05INDUST PK1 138 246127 05IND PKEQ 999 1 OPEN BRANCH FROM BUS 246127 TO BUS 246129 CKT 1 / 246127 05IND PKEQ 999 246129 05INDUST P 69.0 1 OPEN BRANCH FROM BUS 246127 TO BUS 246128 CKT 1 / 246127 05IND PKEQ 999 246128 05INDUST P 34.5 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243316 TO BUS 243338 CKT 1 / 243316 05INDUST PK1 138 243338 05MCKINLEY3 138 1 OPEN BRANCH FROM BUS 245511 TO BUS 246373 CKT 1 / 245511 05INDUST PK2 138 246373 05SPY RUN1 138 1 OPEN BRANCH FROM BUS 243381 TO BUS 245511 CKT 1 / 243381 05SUMMIT 138 245511 05INDUST PK2 138 1 REMOVE SWSHUNT FROM BUS 243316 / 243316 05INDUST PK1 138 OPEN BRANCH FROM BUS 246129 TO BUS 246133 CKT 1 / 246129 05INDUST P 69.0 246133 05KROEMER SS69.0 1 | AEP_P1-2_#5609_16777 | OPEN BRANCH FROM BUS 243366 TO BUS 243389 CKT 1 / 243366 05ROB PK12 138 243389 05WALLEN 138 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T98 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 37 |  | 140.61 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T99 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 37 |  | 140.56 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T100 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 136.55 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T101 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 136.53 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T102 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 37 |  | 135.97 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T103 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 37 |  | 135.12 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T104 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 133.68 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T105 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 133.03 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T106 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 17 |  | 121.45 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T107 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 17 |  | 121.44 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T108 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 17 |  | 121.51 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T109 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 17 |  | 121.51 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T110 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 117.77 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T111 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 246270 | 05CHURBUSC |  |  | 1 | 35 | 205 | 17 |  | 117.78 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T112 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245909 | 05W HICKSV | 246212 | 05VULCRFTT |  |  | 1 | 69 | 205 | 50 |  | 116.69 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T113 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245909 | 05W HICKSV | 246212 | 05VULCRFTT |  |  | 1 | 69 | 205 | 50 |  | 116.7 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T114 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243086 | 05S HICK | 243179 | 05S HICKSV |  |  | 1 | 138/69 | 205 | 90 |  | 101.05 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | 94/107/84/107 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by B3151
AEP-T115 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243086 | 05S HICK | 243179 | 05S HICKSV |  |  | 1 | 138/69 | 205 | 90 |  | 101.05 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | 94/107/84/107 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by B3151
AEP-T116 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 32 |  | 140.95 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T117 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 32 |  | 140.94 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T118 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 32 |  | 131.6 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T119 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246277 | 05COLUMBIA1 | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 32 |  | 131.78 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 25/25/32/32 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T120 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 119.77 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T121 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 119.81 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T122 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 119.81 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T123 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 119.77 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T124 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 106.05 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T125 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 106.05 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T126 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 101.62 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T127 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 24 |  | 101.67 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T128 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 43 |  | 104.78 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T129 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243263 | 05COLUMBIA | 246277 | 05COLUMBIA1 |  |  | 1 | 138/35 | 205 | 43 |  | 104.78 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 35/37/41/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T130 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 17 |  | 100.46 | Single | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 |  |  | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T131 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246165 | 05WALLEN | 246269 | 05CARROLL |  |  | 1 | 35 | 205 | 17 |  | 100.46 | Single | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 |  |  | 17/17/24/24 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T132 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 247313 | 05WOLFGL 3EQ | 247314 | 05WOLF GL T3 | 3 | 69/999 | 205 | 130 |  | 103.32 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T133 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242884 | 05S.LYNCHB | 242886 | 05SKIMMR |  |  | 1 | 69 | 205 | 49 |  | 114.22 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1607.1 | Submitted for inclusion in Local Plan
AEP-T134 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242884 | 05S.LYNCHB | 242886 | 05SKIMMR |  |  | 1 | 69 | 205 | 49 |  | 114.01 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1607.1 | Submitted for inclusion in Local Plan
AEP-T135 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242884 | 05S.LYNCHB | 242886 | 05SKIMMR |  |  | 1 | 69 | 205 | 61 |  | 103.18 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1607.1 | Submitted for inclusion in Local Plan
AEP-T136 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246113 | 05BASS | 246160 | 05SPY RUN1 |  |  | 1 | 35 | 205 | 26 |  | 109.48 | N-1-1 | AEP_P1-2_#7890 | OPEN BRANCH FROM BUS 243366 TO BUS 246993 CKT 1 / 243366 05ROB PK12 138 246993 05PURDUE 138 1 | AEP_P1-3_#11928_05INDUST PK1 138_1 | OPEN BRANCH FROM BUS 243316 TO BUS 246127 CKT 1 / 243316 05INDUST PK1 138 246127 05IND PKEQ 999 1 OPEN BRANCH FROM BUS 246127 TO BUS 246129 CKT 1 / 246127 05IND PKEQ 999 246129 05INDUST P 69.0 1 OPEN BRANCH FROM BUS 246127 TO BUS 246128 CKT 1 / 246127 05IND PKEQ 999 246128 05INDUST P 34.5 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243316 TO BUS 243338 CKT 1 / 243316 05INDUST PK1 138 243338 05MCKINLEY3 138 1 OPEN BRANCH FROM BUS 245511 TO BUS 246373 CKT 1 / 245511 05INDUST PK2 138 246373 05SPY RUN1 138 1 OPEN BRANCH FROM BUS 243381 TO BUS 245511 CKT 1 / 243381 05SUMMIT 138 245511 05INDUST PK2 138 1 REMOVE SWSHUNT FROM BUS 243316 / 243316 05INDUST PK1 138 OPEN BRANCH FROM BUS 246129 TO BUS 246133 CKT 1 / 246129 05INDUST P 69.0 246133 05KROEMER SS69.0 1 | 46/46/58/58 | No | Part 4: Thermal Limits | Substation equipment exclusion | Associated with S2152 | Submitted for inclusion in Local Plan
AEP-T137 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246113 | 05BASS | 246160 | 05SPY RUN1 |  |  | 1 | 35 | 205 | 26 |  | 109.48 | N-1-1 | AEP_P1-3_#11928_05INDUST PK1 138_1 | OPEN BRANCH FROM BUS 243316 TO BUS 246127 CKT 1 / 243316 05INDUST PK1 138 246127 05IND PKEQ 999 1 OPEN BRANCH FROM BUS 246127 TO BUS 246129 CKT 1 / 246127 05IND PKEQ 999 246129 05INDUST P 69.0 1 OPEN BRANCH FROM BUS 246127 TO BUS 246128 CKT 1 / 246127 05IND PKEQ 999 246128 05INDUST P 34.5 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243316 TO BUS 243338 CKT 1 / 243316 05INDUST PK1 138 243338 05MCKINLEY3 138 1 OPEN BRANCH FROM BUS 245511 TO BUS 246373 CKT 1 / 245511 05INDUST PK2 138 246373 05SPY RUN1 138 1 OPEN BRANCH FROM BUS 243381 TO BUS 245511 CKT 1 / 243381 05SUMMIT 138 245511 05INDUST PK2 138 1 REMOVE SWSHUNT FROM BUS 243316 / 243316 05INDUST PK1 138 OPEN BRANCH FROM BUS 246129 TO BUS 246133 CKT 1 / 246129 05INDUST P 69.0 246133 05KROEMER SS69.0 1 | AEP_P1-2_#7890 | OPEN BRANCH FROM BUS 243366 TO BUS 246993 CKT 1 / 243366 05ROB PK12 138 246993 05PURDUE 138 1 | 46/46/58/58 | No | Part 4: Thermal Limits | Substation equipment exclusion | Associated with S2152 | Submitted for inclusion in Local Plan
AEP-T138 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242884 | 05S.LYNCHB | 242886 | 05SKIMMR |  |  | 1 | 69 | 205 | 61 |  | 103.18 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | 49/49/61/61 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1607.1 | Submitted for inclusion in Local Plan
AEP-T139 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245678 | 05NGALIOSS |  |  | 1 | 69 | 205 | 31 |  | 102.34 | N-1-1 | AEP_P1-2_#13310_11237 | OPEN BRANCH FROM BUS 244167 TO BUS 247494 CKT 1 / 244167 05ADRIAN SS 69.0 247494 05HURD Z 69.0 1 OPEN BRANCH FROM BUS 243180 TO BUS 244167 CKT 1 / 243180 05SBERWICK 69.0 244167 05ADRIAN SS 69.0 1 OPEN BRANCH FROM BUS 245721 TO BUS 247494 CKT 1 / 245721 05TYMOCHSS 69.0 247494 05HURD Z 69.0 1 OPEN BRANCH FROM BUS 245706 TO BUS 245721 CKT 1 / 245706 05N UP SAN 69.0 245721 05TYMOCHSS 69.0 1 OPEN BRANCH FROM BUS 245706 TO BUS 245715 CKT 1 / 245706 05N UP SAN 69.0 245715 05U SANDSK 69.0 1 | AEP_P1-2_#5132_688 | OPEN BRANCH FROM BUS 242976 TO BUS 243117 CKT 1 / 242976 05BUCYRC 138 243117 05SULFRS 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243117 CKT 1 / 243024 05HOWARD 138 243117 05SULFRS 138 1 OPEN BRANCH FROM BUS 242976 TO BUS 245653 CKT 1 / 242976 05BUCYRC 138 245653 05BUCYRS C 69.0 1 | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Removed due to model correction | Submitted for inclusion in Local Plan
AEP-T140 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244171 | 05J.EARLY | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 103 |  | 137.81 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | 102/102/129/129 | Yes | Part 4: Thermal Limits |  | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-T141 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244171 | 05J.EARLY | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 103 |  | 139.26 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | 102/102/129/129 | Yes | Part 4: Thermal Limits |  | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-T142 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244171 | 05J.EARLY | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 86 |  | 119.11 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | 102/102/129/129 | Yes | Part 4: Thermal Limits |  | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-T143 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 63 |  | 120.11 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2187 No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. | Submitted for inclusion in Local Plan
AEP-T144 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 63 |  | 120.09 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2187 No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. | Submitted for inclusion in Local Plan
AEP-T145 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244949 | 05GAVIN1 | 246740 | 05MEIGS |  |  | 1 | 69 | 205 | 82 |  | 101.74 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | Associated with S2187 No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. | Submitted for inclusion in Local Plan
AEP-T146 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244949 | 05GAVIN1 | 246740 | 05MEIGS |  |  | 1 | 69 | 205 | 82 |  | 101.75 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | Associated with S2187 No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. | Submitted for inclusion in Local Plan
AEP-T147 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244171 | 05J.EARLY | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 86 |  | 128.75 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | 102/102/129/129 | Yes | Part 4: Thermal Limits |  | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-T148 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 73 |  | 102.88 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T149 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 73 |  | 102.88 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T150 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 121.08 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T151 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 121.08 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T152 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 119.35 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T153 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 119.35 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion exclusion | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T154 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 73 |  | 100.5 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T155 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 73 |  | 100.5 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T156 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 109.94 | N-1-1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T157 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 110.52 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T158 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243694 | 05INEZ | 243806 | 05INEZ |  |  | 1 | 138/69 | 205 | 78 |  | 115.55 | N-1-1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 70/78/70/78 | NO | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-AP047, solution presented at June SRRTEP S# TBD | Solution
AEP-T159 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 108.1 | N-1-1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T160 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243694 | 05INEZ | 243806 | 05INEZ |  |  | 1 | 138/69 | 205 | 78 |  | 116.41 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | 70/78/70/78 | NO | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-AP047, solution presented at June SRRTEP S# TBD | Solution
AEP-T161 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243694 | 05INEZ | 243806 | 05INEZ |  |  | 1 | 138/69 | 205 | 78 |  | 113.64 | N-1-1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | 70/78/70/78 | NO | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-AP047, solution presented at June SRRTEP S# TBD | Solution
AEP-T162 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243694 | 05INEZ | 243806 | 05INEZ |  |  | 1 | 138/69 | 205 | 78 |  | 112.59 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | 70/78/70/78 | NO | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-AP047, solution presented at June SRRTEP S# TBD | Solution
AEP-T163 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244594 | 05CEDARCRK | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 91 |  | 108.12 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 and Potential M-3 need identified, awaiting field and engineering analysis | Submitted for inclusion in Local Plan
AEP-T164 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243831 | 05STRDREQ1 | 243832 | 05STROUDS | 246748 | 05STROUD L | 1 | 999/69 | 205 | 42 |  | 146.9 | N-1-1 | AEP_P1-3_#13356_05ELLIOT 138_1 | OPEN BRANCH FROM BUS 243506 TO BUS 243829 CKT 1 / 243506 05ELLIOT 138 243829 05ELLIOT 69.0 1 | AEP_P1-3_#11605_05STROUD 138_2 | OPEN BRANCH FROM BUS 243579 TO BUS 243835 CKT 1 / 243579 05STROUD 138 243835 05STRDREQ2 999 1 OPEN BRANCH FROM BUS 243832 TO BUS 243835 CKT 1 / 243832 05STROUDS 69.0 243835 05STRDREQ2 999 1 | 37/42/41/45 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2224 | Submitted for inclusion in Local Plan
AEP-T165 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243831 | 05STRDREQ1 | 243832 | 05STROUDS | 246748 | 05STROUD L | 1 | 999/69 | 205 | 42 |  | 146.9 | N-1-1 | AEP_P1-3_#11605_05STROUD 138_2 | OPEN BRANCH FROM BUS 243579 TO BUS 243835 CKT 1 / 243579 05STROUD 138 243835 05STRDREQ2 999 1 OPEN BRANCH FROM BUS 243832 TO BUS 243835 CKT 1 / 243832 05STROUDS 69.0 243835 05STRDREQ2 999 1 | AEP_P1-3_#13356_05ELLIOT 138_1 | OPEN BRANCH FROM BUS 243506 TO BUS 243829 CKT 1 / 243506 05ELLIOT 138 243829 05ELLIOT 69.0 1 | 37/42/41/45 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2224 | Submitted for inclusion in Local Plan
AEP-T166 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243831 | 05STRDREQ1 | 243832 | 05STROUDS | 246748 | 05STROUD L | 1 | 999/69 | 205 | 45 |  | 144.45 | N-1-1 | AEP_P1-3_#13356_05ELLIOT 138_1 | OPEN BRANCH FROM BUS 243506 TO BUS 243829 CKT 1 / 243506 05ELLIOT 138 243829 05ELLIOT 69.0 1 | AEP_P1-3_#11605_05STROUD 138_2 | OPEN BRANCH FROM BUS 243579 TO BUS 243835 CKT 1 / 243579 05STROUD 138 243835 05STRDREQ2 999 1 OPEN BRANCH FROM BUS 243832 TO BUS 243835 CKT 1 / 243832 05STROUDS 69.0 243835 05STRDREQ2 999 1 | 37/42/41/45 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2224 | Submitted for inclusion in Local Plan
AEP-T167 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243831 | 05STRDREQ1 | 243832 | 05STROUDS | 246748 | 05STROUD L | 1 | 999/69 | 205 | 45 |  | 144.45 | N-1-1 | AEP_P1-3_#11605_05STROUD 138_2 | OPEN BRANCH FROM BUS 243579 TO BUS 243835 CKT 1 / 243579 05STROUD 138 243835 05STRDREQ2 999 1 OPEN BRANCH FROM BUS 243832 TO BUS 243835 CKT 1 / 243832 05STROUDS 69.0 243835 05STRDREQ2 999 1 | AEP_P1-3_#13356_05ELLIOT 138_1 | OPEN BRANCH FROM BUS 243506 TO BUS 243829 CKT 1 / 243506 05ELLIOT 138 243829 05ELLIOT 69.0 1 | 37/42/41/45 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2224 | Submitted for inclusion in Local Plan
AEP-T168 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245625 | 05MAPLE GR | 245628 | 05RIVERVIE |  |  | 1 | 69 | 205 | 43 |  | 198.63 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T169 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245623 | 05HOLRAN | 245625 | 05MAPLE GR |  |  | 1 | 69 | 205 | 43 |  | 180.36 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T170 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 245623 | 05HOLRAN |  |  | 1 | 69 | 205 | 43 |  | 166.52 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T171 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 35 |  | 136.3 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 37/37/47/47 | Yes No | Part 4: Thermal Limits | Solved by existing baseline project | Potential M-3 need identified, awaiting field and engineering analysis Solved by b3099
AEP-T172 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 35 |  | 136.36 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 37/37/47/47 | Yes No | Part 4: Thermal Limits | Solved by existing baseline project | Potential M-3 need identified, awaiting field and engineering analysis Solved by b3099
AEP-T173 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 105.82 | N-1-1 | AEP_P1-2_#14698 | OPEN BRANCH FROM BUS 245983 TO BUS 245994 CKT 1 / 245983 05GRISTMILL 138 245994 05GEMINI 138 1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T174 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 105.94 | N-1-1 | AEP_P1-3_#14700_05GRISTMILL 138_1 | OPEN BRANCH FROM BUS 245977 TO BUS 245983 CKT 1 / 245977 05GRISTMILL 345 245983 05GRISTMILL 138 1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T175 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 104.15 | N-1-1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | AEP_P1-3_#14700_05GRISTMILL 138_1 | OPEN BRANCH FROM BUS 245977 TO BUS 245983 CKT 1 / 245977 05GRISTMILL 345 245983 05GRISTMILL 138 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T176 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245874 | 05E DELPHO |  |  | 1 | 69 | 205 | 40 |  | 104.19 | N-1-1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | AEP_P1-2_#14698 | OPEN BRANCH FROM BUS 245983 TO BUS 245994 CKT 1 / 245983 05GRISTMILL 138 245994 05GEMINI 138 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T177 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 115.81 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T178 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 115.8 | N-1-1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T179 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 105.16 | N-1-1 | AEP_P1-2_#11794_903 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T180 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 105.16 | N-1-1 | AEP_P1-3_#12221_05W VAN WR 69 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 247878 CKT 1 / 245911 05W VAN WR 34.5 247878 05SW.VANW SS34.5 1 OPEN BRANCH FROM BUS 245895 TO BUS 247878 CKT 1 / 245895 05WOHCTYSS 34.5 247878 05SW.VANW SS34.5 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T181 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 103.21 | N-1-1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | AEP_P1-3_#12221_05W VAN WR 69 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 247878 CKT 1 / 245911 05W VAN WR 34.5 247878 05SW.VANW SS34.5 1 OPEN BRANCH FROM BUS 245895 TO BUS 247878 CKT 1 / 245895 05WOHCTYSS 34.5 247878 05SW.VANW SS34.5 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T182 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 50 |  | 121.73 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T183 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 50 |  | 121.74 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T184 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 50 |  | 121.73 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T185 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246740 | 05MEIGS | 246984 | 05HEMLOCK |  |  | 1 | 69 | 205 | 50 |  | 121.73 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T186 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243175 | 05N DELPHO | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 54 |  | 103.21 | N-1-1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | AEP_P1-2_#11794_903 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T187 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 245256 | 05W N PHIL |  |  | 1 | 35 | 205 | 23 |  | 133.79 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T188 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245891 | 05N MID PT | 245907 | 05VAN WERT |  |  | 1 | 69 | 205 | 40 |  | 111.7 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T189 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 245256 | 05W N PHIL |  |  | 1 | 35 | 205 | 23 |  | 135.99 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T190 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 110.79 | N-1-1 | AEP_P1-2_#11672_865 | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 / 244986 05E AMSTDA 69.0 245079 05CIRCLGSS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 / 245079 05CIRCLGSS 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 / 245079 05CIRCLGSS 69.0 245080 05SPRINGF8 69.0 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 / 245044 05HAMMSVLL 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 / 245048 05ROSS 8 69.0 247482 05HOLT SS 69.0 Z1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T191 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 110.79 | N-1-1 | AEP_P1-2_#11672_865 | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 / 244986 05E AMSTDA 69.0 245079 05CIRCLGSS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 / 245079 05CIRCLGSS 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 / 245079 05CIRCLGSS 69.0 245080 05SPRINGF8 69.0 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 / 245044 05HAMMSVLL 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 / 245048 05ROSS 8 69.0 247482 05HOLT SS 69.0 Z1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T192 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245891 | 05N MID PT | 245907 | 05VAN WERT |  |  | 1 | 69 | 205 | 40 |  | 111.7 | N-1-1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T193 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244073 | 05ROANOKE | 244098 | 05WALNUTA2 |  |  | 1 | 69 | 205 | 90 |  | 108.14 | N-1-1 | AEP_P1-3_#11378_05CATAWB 138_1 | OPEN BRANCH FROM BUS 242583 TO BUS 244034 CKT 1 / 242583 05CATAWB 138 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244034 CKT 1 / 244033 05CATAWBA 69.0 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244032 TO BUS 244034 CKT 1 / 244032 05CATAWBA 34.5 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244037 CKT 1 / 244033 05CATAWBA 69.0 244037 05CLEVEL 69.0 1 OPEN BRANCH FROM BUS 244033 TO BUS 244062 CKT 1 / 244033 05CATAWBA 69.0 244062 05MASON CR 69.0 1 REMOVE SWSHUNT FROM BUS 244033 / 244033 05CATAWBA 69.0 OPEN BRANCH FROM BUS 244032 TO BUS 244079 CKT 1 / 244032 05CATAWBA 34.5 244079 05VETHOSPZ 34.5 1 | AEP_P1-3_#13885_05HANCK1 138_1 | OPEN BRANCH FROM BUS 242663 TO BUS 244049 CKT 1 / 242663 05HANCK1 138 244049 05HANCK1EQ 999 1 OPEN BRANCH FROM BUS 244049 TO BUS 244052 CKT 1 / 244049 05HANCK1EQ 999 244052 05HANCOCK1 34.5 1 OPEN BRANCH FROM BUS 244049 TO BUS 244053 CKT 1 / 244049 05HANCK1EQ 999 244053 05HANCOCK 69.0 1 | 99/99/125/125 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T194 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244073 | 05ROANOKE | 244098 | 05WALNUTA2 |  |  | 1 | 69 | 205 | 90 |  | 108.14 | N-1-1 | AEP_P1-3_#13885_05HANCK1 138_1 | OPEN BRANCH FROM BUS 242663 TO BUS 244049 CKT 1 / 242663 05HANCK1 138 244049 05HANCK1EQ 999 1 OPEN BRANCH FROM BUS 244049 TO BUS 244052 CKT 1 / 244049 05HANCK1EQ 999 244052 05HANCOCK1 34.5 1 OPEN BRANCH FROM BUS 244049 TO BUS 244053 CKT 1 / 244049 05HANCK1EQ 999 244053 05HANCOCK 69.0 1 | AEP_P1-3_#11378_05CATAWB 138_1 | OPEN BRANCH FROM BUS 242583 TO BUS 244034 CKT 1 / 242583 05CATAWB 138 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244034 CKT 1 / 244033 05CATAWBA 69.0 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244032 TO BUS 244034 CKT 1 / 244032 05CATAWBA 34.5 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244037 CKT 1 / 244033 05CATAWBA 69.0 244037 05CLEVEL 69.0 1 OPEN BRANCH FROM BUS 244033 TO BUS 244062 CKT 1 / 244033 05CATAWBA 69.0 244062 05MASON CR 69.0 1 REMOVE SWSHUNT FROM BUS 244033 / 244033 05CATAWBA 69.0 OPEN BRANCH FROM BUS 244032 TO BUS 244079 CKT 1 / 244032 05CATAWBA 34.5 244079 05VETHOSPZ 34.5 1 | 99/99/125/125 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T195 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 110.79 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | AEP_P1-2_#11672_865 | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 / 244986 05E AMSTDA 69.0 245079 05CIRCLGSS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 / 245079 05CIRCLGSS 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 / 245079 05CIRCLGSS 69.0 245080 05SPRINGF8 69.0 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 / 245044 05HAMMSVLL 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 / 245048 05ROSS 8 69.0 247482 05HOLT SS 69.0 Z1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T196 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 110.79 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | AEP_P1-2_#11672_865 | OPEN BRANCH FROM BUS 244986 TO BUS 245079 CKT 1 / 244986 05E AMSTDA 69.0 245079 05CIRCLGSS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 247482 CKT 1 / 245079 05CIRCLGSS 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245079 TO BUS 245080 CKT 1 / 245079 05CIRCLGSS 69.0 245080 05SPRINGF8 69.0 1 OPEN BRANCH FROM BUS 245044 TO BUS 247482 CKT 1 / 245044 05HAMMSVLL 69.0 247482 05HOLT SS 69.0 1 OPEN BRANCH FROM BUS 245048 TO BUS 247482 CKT Z1 / 245048 05ROSS 8 69.0 247482 05HOLT SS 69.0 Z1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T197 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 114.35 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T198 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 114.34 | N-1-1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T199 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 102.01 | N-1-1 | AEP_P1-2_#11794_903 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T200 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245871 | 05DELPHOS | 245902 | 05S DELPHO |  |  | 1 | 69 | 205 | 50 |  | 102.01 | N-1-1 | AEP_P1-3_#12221_05W VAN WR 69 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 247878 CKT 1 / 245911 05W VAN WR 34.5 247878 05SW.VANW SS34.5 1 OPEN BRANCH FROM BUS 245895 TO BUS 247878 CKT 1 / 245895 05WOHCTYSS 34.5 247878 05SW.VANW SS34.5 1 | AEP_P1-2_#11795_904 | OPEN BRANCH FROM BUS 243168 TO BUS 247383 CKT 1 / 243168 05HAVILND1 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245907 TO BUS 247383 CKT 1 / 245907 05VAN WERT 69.0 247383 05N.VANWRTSS69.0 1 OPEN BRANCH FROM BUS 245908 TO BUS 247383 CKT Z1 / 245908 05VANWERT8 69.0 247383 05N.VANWRTSS69.0 Z1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T201 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 107.54 | N-1-1 | AEP_P1-3_#12221_05W VAN WR 69 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 247878 CKT 1 / 245911 05W VAN WR 34.5 247878 05SW.VANW SS34.5 1 OPEN BRANCH FROM BUS 245895 TO BUS 247878 CKT 1 / 245895 05WOHCTYSS 34.5 247878 05SW.VANW SS34.5 1 | AEP_P1-3_#11852_05NDELPH 138_1 | OPEN BRANCH FROM BUS 243051 TO BUS 243175 CKT 1 / 243051 05NDELPH 138 243175 05N DELPHO 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T202 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 102.07 | N-1-1 | AEP_P1-3_#11848_05HAVILAND2 138_4 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243169 TO BUS 246352 CKT 4 / 243169 05HAVILND2 69.0 246352 05HAVILAND2 138 4 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-3_#11852_05NDELPH 138_1 | OPEN BRANCH FROM BUS 243051 TO BUS 243175 CKT 1 / 243051 05NDELPH 138 243175 05N DELPHO 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T203 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 105.35 | N-1-1 | AEP_P1-3_#13604 | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 / 242994 05EAMSTD 138 244986 05E AMSTDA 69.0 1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T204 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 105.35 | N-1-1 | AEP_P1-3_#13604 | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 / 242994 05EAMSTD 138 244986 05E AMSTDA 69.0 1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T205 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 101.41 | N-1-1 | AEP_P1-2_#11533_804 | OPEN BRANCH FROM BUS 246622 TO BUS 246635 CKT 1 / 246622 05WESTERVL 69.0 246635 05HUNTLEY 69.0 1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T206 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 101.41 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-2_#11533_804 | OPEN BRANCH FROM BUS 246622 TO BUS 246635 CKT 1 / 246622 05WESTERVL 69.0 246635 05HUNTLEY 69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T207 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 128.19 | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2 | OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 OPEN BRANCH FROM BUS 243513 TO BUS 246613 CKT 2 / 243513 05GENOA 138 246613 05GENOA 69.0 2 OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 OPEN BRANCH FROM BUS 246613 TO BUS 246643 CKT 1 / 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1 REMOVE SWSHUNT FROM BUS 246613 / 246613 05GENOA 69.0 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 75/75/94/94 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T208 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 128.19 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-3_#11531_05GENOA 138_2 | OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 OPEN BRANCH FROM BUS 243513 TO BUS 246613 CKT 2 / 243513 05GENOA 138 246613 05GENOA 69.0 2 OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 OPEN BRANCH FROM BUS 246613 TO BUS 246643 CKT 1 / 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1 REMOVE SWSHUNT FROM BUS 246613 / 246613 05GENOA 69.0 | 75/75/94/94 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T209 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 105.35 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | AEP_P1-3_#13604 | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 / 242994 05EAMSTD 138 244986 05E AMSTDA 69.0 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T210 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 105.35 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | AEP_P1-3_#13604 | OPEN BRANCH FROM BUS 242994 TO BUS 244986 CKT 1 / 242994 05EAMSTD 138 244986 05E AMSTDA 69.0 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T211 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 245256 | 05W N PHIL |  |  | 1 | 35 | 205 | 23 |  | 136.9 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T212 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 245256 | 05W N PHIL |  |  | 1 | 35 | 205 | 23 |  | 137.14 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T213 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 127.99 | N-1-1 | AEP_P1-2_#11532_805 | OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 75/75/94/94 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T214 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 100.16 | N-1-1 | AEP_P1-2_#9276_26958 | OPEN BRANCH FROM BUS 242966 TO BUS 242994 CKT 1 / 242966 05BROADA 138 242994 05EAMSTD 138 1 OPEN BRANCH FROM BUS 242966 TO BUS 243127 CKT 1 / 242966 05BROADA 138 243127 05TIDD 1-2 138 1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T215 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 100.16 | N-1-1 | AEP_P1-2_#9276_26958 | OPEN BRANCH FROM BUS 242966 TO BUS 242994 CKT 1 / 242966 05BROADA 138 242994 05EAMSTD 138 1 OPEN BRANCH FROM BUS 242966 TO BUS 243127 CKT 1 / 242966 05BROADA 138 243127 05TIDD 1-2 138 1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T216 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 100.15 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | AEP_P1-2_#9276_26958 | OPEN BRANCH FROM BUS 242966 TO BUS 242994 CKT 1 / 242966 05BROADA 138 242994 05EAMSTD 138 1 OPEN BRANCH FROM BUS 242966 TO BUS 243127 CKT 1 / 242966 05BROADA 138 243127 05TIDD 1-2 138 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T217 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243113 | 05STORON | 245049 | 05S TORONT |  |  | 1 | 138/69 | 205 | 62 |  | 100.15 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | AEP_P1-2_#9276_26958 | OPEN BRANCH FROM BUS 242966 TO BUS 242994 CKT 1 / 242966 05BROADA 138 242994 05EAMSTD 138 1 OPEN BRANCH FROM BUS 242966 TO BUS 243127 CKT 1 / 242966 05BROADA 138 243127 05TIDD 1-2 138 1 | 66/74/74/81 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T218 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246601 | 05SAWMILL | 246830 | 05LAZELLE N |  |  | 1 | 69 | 205 | 69 |  | 127.99 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-2_#11532_805 | OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T219 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 162.45 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T220 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 125.49 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T221 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245943 | 05NATRIUM |  |  | 1 | 69 | 205 | 50 |  | 145.58 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T222 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 63 |  | 137.62 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T223 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245943 | 05NATRIUM |  |  | 1 | 69 | 205 | 63 |  | 127.4 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T224 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 124.94 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T225 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245943 | 05NATRIUM |  |  | 1 | 69 | 205 | 63 |  | 127.4 | N-1-1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T226 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245943 | 05NATRIUM |  |  | 1 | 69 | 205 | 63 |  | 127.4 | N-1-1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T227 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 103.16 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T228 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245943 | 05NATRIUM |  |  | 1 | 69 | 205 | 50 |  | 100.15 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T229 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 163.44 | N-1-1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T230 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 103.59 | N-1-1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T231 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 107.45 | N-1-1 | FE-P1-2-MP-138-003 | DISCONNECT BRANCH FROM BUS 235299 TO BUS 235329 CKT 1 /* 01BELMNT 138 01EUREKA 138 DISCONNECT BRANCH FROM BUS 235329 TO BUS 235408 CKT 1 /* 01EUREKA 138 01STMARY 138 DISCONNECT BRANCH FROM BUS 235301 TO BUS 235408 CKT 1 /* 01BENSRN 138 01STMARY 138 DISCONNECT BRANCH FROM BUS 235301 TO BUS 235361 CKT 1 /* 01BENSRN 138 01LONGR 138 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T232 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 101.9 | N-1-1 | FE-P1-2-MP-138-559T | DISCONNECT BRANCH FROM BUS 235378 TO BUS 246067 CKT 1 /* 01NMARTN 138 05NATRIU 138 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T233 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 63 |  | 137.62 | N-1-1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T234 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 63 |  | 137.62 | N-1-1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T235 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 124.93 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T236 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246379 | 05AM GENRL_2 | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 122.48 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T237 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 101.19 | N-1-1 | AEP_P1-2_#11730_893 | OPEN BRANCH FROM BUS 245922 TO BUS 245935 CKT 1 / 245922 05IRELAND SS69.0 245935 05G WASHON 69.0 1 OPEN BRANCH FROM BUS 245922 TO BUS 245938 CKT 1 / 245922 05IRELAND SS69.0 245938 05KAMMER 69.0 1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T238 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245928 | 05COLOMBI | 245951 | 05CONNERRN |  |  | 1 | 69 | 205 | 50 |  | 102.32 | N-1-1 | FE-P1-2-MP-138-086 | DISCONNECT BRANCH FROM BUS 235378 TO BUS 235382 CKT 1 /* 01NMARTN 138 01PADENC 138 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T239 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245930 | 05CRESAPS | 245950 | 05MCELROY |  |  | 1 | 69 | 205 | 75 |  | 138.83 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 75/75/94/94 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T240 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245930 | 05CRESAPS | 245938 | 05KAMMER |  |  | 1 | 69 | 205 | 90 |  | 117.19 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 100/100/126/126 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T241 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246368 | 05VIRGIL S |  |  | 1 | 35 | 205 | 76 |  | 150.04 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T242 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246368 | 05VIRGIL S |  |  | 1 | 35 | 205 | 76 |  | 150.04 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T243 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245930 | 05CRESAPS | 245950 | 05MCELROY |  |  | 1 | 69 | 205 | 94 |  | 109.17 | Tower | AEP_P7-1_#10854 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 |  |  | 75/75/94/94 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T244 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245930 | 05CRESAPS | 245950 | 05MCELROY |  |  | 1 | 69 | 205 | 75 |  | 100.1 | N-1-1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | 75/75/94/94 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T245 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246368 | 05VIRGIL S |  |  | 1 | 35 | 205 | 98 |  | 113.96 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T246 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246368 | 05VIRGIL S |  |  | 1 | 35 | 205 | 98 |  | 113.96 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T247 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246415 | 05KLINE |  |  | 1 | 35 | 205 | 76 |  | 158.82 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T248 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246415 | 05KLINE |  |  | 1 | 35 | 205 | 76 |  | 158.82 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T249 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246415 | 05KLINE |  |  | 1 | 35 | 205 | 98 |  | 120.7 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T250 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245930 | 05CRESAPS | 245950 | 05MCELROY |  |  | 1 | 69 | 205 | 75 |  | 100.1 | N-1-1 | AEP_P1-2_#5152_716 | OPEN BRANCH FROM BUS 243012 TO BUS 243049 CKT 1 / 243012 05G WASHGTON 138 243049 05NATRIUM12 138 1 | AEP_P1-2_#13652_775 | OPEN BRANCH FROM BUS 243026 TO BUS 246067 CKT 1 / 243026 05KAMMER13 138 246067 05NATRIUM34 138 1 | 75/75/94/94 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T251 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244684 | 0510TH ST | 247466 | 05MANSBACHSS |  |  | 1 | 69 | 205 | 54 |  | 114.8 | N-1-1 | AEP_P1-2_#14753 | OPEN BRANCH FROM BUS 243659 TO BUS 243676 CKT 1 / 243659 05BELFN5EQ 999 243676 05BELLF2 138 1 OPEN BRANCH FROM BUS 243659 TO BUS 243762 CKT 1 / 243659 05BELFN5EQ 999 243762 05BELLEFNT 34.5 1 OPEN BRANCH FROM BUS 243675 TO BUS 243676 CKT Z1 / 243675 05BELLF1 138 243676 05BELLF2 138 Z1 OPEN BRANCH FROM BUS 243676 TO BUS 246887 CKT 1 / 243676 05BELLF2 138 246887 05RAMEY 138 1 OPEN BRANCH FROM BUS 243674 TO BUS 243676 CKT 1 / 243674 05BELHAV 138 243676 05BELLF2 138 1 OPEN BRANCH FROM BUS 243676 TO BUS 243699 CKT 1 / 243676 05BELLF2 138 243699 05OXYGEN 138 1 OPEN BRANCH FROM BUS 243676 TO BUS 244660 CKT 3 / 243676 05BELLF2 138 244660 05BELLEFNT 69.0 3 OPEN BRANCH FROM BUS 243762 TO BUS 244655 CKT 1 / 243762 05BELLEFNT 34.5 244655 05ARMCO 34.5 1 | AEP_P1-2_#5972_194 | OPEN BRANCH FROM BUS 243064 TO BUS 243675 CKT 1 / 243064 05NPROCT 138 243675 05BELLF1 138 1 OPEN BRANCH FROM BUS 243675 TO BUS 243762 CKT 1 / 243675 05BELLF1 138 243762 05BELLEFNT 34.5 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T252 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244684 | 0510TH ST | 247466 | 05MANSBACHSS |  |  | 1 | 69 | 205 | 54 |  | 114.8 | N-1-1 | AEP_P1-2_#5972_194 | OPEN BRANCH FROM BUS 243064 TO BUS 243675 CKT 1 / 243064 05NPROCT 138 243675 05BELLF1 138 1 OPEN BRANCH FROM BUS 243675 TO BUS 243762 CKT 1 / 243675 05BELLF1 138 243762 05BELLEFNT 34.5 1 | AEP_P1-2_#14753 | OPEN BRANCH FROM BUS 243659 TO BUS 243676 CKT 1 / 243659 05BELFN5EQ 999 243676 05BELLF2 138 1 OPEN BRANCH FROM BUS 243659 TO BUS 243762 CKT 1 / 243659 05BELFN5EQ 999 243762 05BELLEFNT 34.5 1 OPEN BRANCH FROM BUS 243675 TO BUS 243676 CKT Z1 / 243675 05BELLF1 138 243676 05BELLF2 138 Z1 OPEN BRANCH FROM BUS 243676 TO BUS 246887 CKT 1 / 243676 05BELLF2 138 246887 05RAMEY 138 1 OPEN BRANCH FROM BUS 243674 TO BUS 243676 CKT 1 / 243674 05BELHAV 138 243676 05BELLF2 138 1 OPEN BRANCH FROM BUS 243676 TO BUS 243699 CKT 1 / 243676 05BELLF2 138 243699 05OXYGEN 138 1 OPEN BRANCH FROM BUS 243676 TO BUS 244660 CKT 3 / 243676 05BELLF2 138 244660 05BELLEFNT 69.0 3 OPEN BRANCH FROM BUS 243762 TO BUS 244655 CKT 1 / 243762 05BELLEFNT 34.5 244655 05ARMCO 34.5 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T253 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 247773 | 05BASF Z |  |  | 1 | 35 | 205 | 27 45 |  | 129.72 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 27/27/38/38 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T254 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 246415 | 05KLINE |  |  | 1 | 35 | 205 | 98 |  | 120.7 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T255 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246389 | 05CAP AV | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 125.49 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T256 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 247773 | 05BASF Z |  |  | 1 | 35 | 205 | 27 45 |  | 129.69 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 27/27/38/38 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T257 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244741 | 0524TH ST |  |  | 1 | 35 | 205 | 17 26 |  | 237.18 180.63 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T258 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244741 | 0524TH ST |  |  | 1 | 35 | 205 | 17 26 |  | 237.16 180.15 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T259 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244741 | 0524TH ST |  |  | 1 | 35 | 205 | 21 31 |  | 187.15 147.27 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T260 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246613 | 05GENOA | 246622 | 05WESTERVL |  |  | 1 | 69 | 205 | 73 |  | 120.89 | N-1-1 | AEP_P1-2_#11536_812 | OPEN BRANCH FROM BUS 246601 TO BUS 246830 CKT 1 / 246601 05SAWMILL 69.0 246830 05LAZELLE N 69.0 1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T261 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246613 | 05GENOA | 246622 | 05WESTERVL |  |  | 1 | 69 | 205 | 73 |  | 120.89 | N-1-1 | AEP_P1-3_#11537_05SAWMIL 138_1 | OPEN BRANCH FROM BUS 243566 TO BUS 246601 CKT 1 / 243566 05SAWMIL 138 246601 05SAWMILL 69.0 1 OPEN BRANCH FROM BUS 246601 TO BUS 246830 CKT 1 / 246601 05SAWMILL 69.0 246830 05LAZELLE N 69.0 1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T262 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246613 | 05GENOA | 246622 | 05WESTERVL |  |  | 1 | 69 | 205 | 73 |  | 120.89 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-3_#11537_05SAWMIL 138_1 | OPEN BRANCH FROM BUS 243566 TO BUS 246601 CKT 1 / 243566 05SAWMIL 138 246601 05SAWMILL 69.0 1 OPEN BRANCH FROM BUS 246601 TO BUS 246830 CKT 1 / 246601 05SAWMILL 69.0 246830 05LAZELLE N 69.0 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T263 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246389 | 05CAP AV | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 125.49 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T264 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246389 | 05CAP AV | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 124.94 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T265 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246613 | 05GENOA | 246622 | 05WESTERVL |  |  | 1 | 69 | 205 | 73 |  | 120.89 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-2_#11536_812 | OPEN BRANCH FROM BUS 246601 TO BUS 246830 CKT 1 / 246601 05SAWMILL 69.0 246830 05LAZELLE N 69.0 1 | 73/73/91/91 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T266 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244741 | 0524TH ST |  |  | 1 | 35 | 205 | 21 31 |  | 187.09 147.27 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T267 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 43 |  | 103.05 | N-1-1 | AEP_P1-2_#5236_2841 | OPEN BRANCH FROM BUS 243765 TO BUS 246155 CKT Z1 / 243765 05FORD LIMA1 138 246155 05FORD LIMA2 138 Z1 OPEN BRANCH FROM BUS 243082 TO BUS 243765 CKT 1 / 243082 05ROCKHILL1 138 243765 05FORD LIMA1 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T268 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 43 |  | 103.05 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5236_2841 | OPEN BRANCH FROM BUS 243765 TO BUS 246155 CKT Z1 / 243765 05FORD LIMA1 138 246155 05FORD LIMA2 138 Z1 OPEN BRANCH FROM BUS 243082 TO BUS 243765 CKT 1 / 243082 05ROCKHILL1 138 243765 05FORD LIMA1 138 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T269 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244700 | 05DARRAH |  |  | 1 | 35 | 205 | 17 43 |  | 250.18 114.54 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T270 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 244700 | 05DARRAH |  |  | 1 | 35 | 205 | 17 43 |  | 250.12 114.02 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 17/17/21/21 56/56/70/70 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T271 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245939 | 05LOCKWOODSS | 245942 | 05MOUNDVIL |  |  | 1 | 69 | 205 | 86 |  | 100.47 | N-1-1 | AEP_P1-3_#1282_05WBELLA 345_1 | OPEN BRANCH FROM BUS 242948 TO BUS 243143 CKT 3 / 242948 05WBELLA 345 243143 05WBELLA 138 3 | AEP_P1-2_#13645_25338 | OPEN BRANCH FROM BUS 243143 TO BUS 246108 CKT 1 / 243143 05WBELLA 138 246108 05KAMMER24 138 1 | 148/148/187/187 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T272 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245939 | 05LOCKWOODSS | 245942 | 05MOUNDVIL |  |  | 1 | 69 | 205 | 86 |  | 100.46 | N-1-1 | AEP_P1-2_#13645_25338 | OPEN BRANCH FROM BUS 243143 TO BUS 246108 CKT 1 / 243143 05WBELLA 138 246108 05KAMMER24 138 1 | AEP_P1-3_#1282_05WBELLA 345_1 | OPEN BRANCH FROM BUS 242948 TO BUS 243143 CKT 3 / 242948 05WBELLA 345 243143 05WBELLA 138 3 | 148/148/187/187 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T273 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 244718 | 05JOHNSON LN |  |  | 1 | 35 | 205 | 43 |  | 128.96 115.12 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 54/54/76/76 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T274 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 244718 | 05JOHNSON LN |  |  | 1 | 35 | 205 | 43 |  | 128.91 114.25 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 54/54/76/76 | Yes No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T275 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246389 | 05CAP AV | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 124.93 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T276 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246389 | 05CAP AV | 246908 | 05AM GENRL_1 |  |  | 1 | 35 | 205 | 62 |  | 122.47 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T277 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 244737 | 05W.HUNTGT |  |  | 2 | 35 | 205 | 35 |  | 154.28 148.57 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 31/35/31/35 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T278 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 244737 | 05W.HUNTGT |  |  | 2 | 35 | 205 | 35 |  | 154.26 148.14 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 31/35/31/35 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T279 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 244737 | 05W.HUNTGT |  |  | 2 | 35 | 205 | 35 |  | 145.14 139.15 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 31/35/31/35 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T280 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 244737 | 05W.HUNTGT |  |  | 2 | 35 | 205 | 35 |  | 145.08 139.15 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 31/35/31/35 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T281 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 245836 | 05ROCKHILL |  |  | 1 | 35 | 205 | 27 |  | 106.83 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T282 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246313 | 05DODGE SS | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 45 |  | 199.18 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 54/54/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T283 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246313 | 05DODGE SS | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 45 |  | 199.17 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 54/54/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T284 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 245836 | 05ROCKHILL |  |  | 1 | 35 | 205 | 27 |  | 106.83 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T285 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 27 |  | 107.43 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T286 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 27 |  | 107.43 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T287 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 43 |  | 161.43 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T288 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 43 |  | 161.43 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T289 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 51 |  | 125.81 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T290 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245840 | 05S SIDE |  |  | 1 | 35 | 205 | 51 |  | 125.81 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T291 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 45 |  | 161.19 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T292 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 45 |  | 161.19 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T293 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 57 |  | 118.06 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T294 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 247492 | 05LIBERTYTSS |  |  | 1 | 35 | 205 | 41 |  | 109.53 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | Base Case |  | 62/62/78/78 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T295 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246927 | 05SAND H | 247468 | 05CRICKET SS |  |  | 1 | 138 | 205 | 219 |  | 101.99 | N-1-1 | AEP_P1-2_#7279_17397 | OPEN BRANCH FROM BUS 246927 TO BUS 246928 CKT 1 / 246927 05SAND H 138 246928 05WARTON H1 138 1 | Base Case |  | 257/360/325/404 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T296 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243347 | 05TIDD 3-4 | 243779 | 05WHELGS |  |  | 2 | 138 | 205 | 187 |  | 103.19 | N-1-1 | AEP_P1-2_#5194_759 | OPEN BRANCH FROM BUS 243347 TO BUS 243779 CKT 1 / 243347 05TIDD 3-4 138 243779 05WHELGS 138 1 | Base Case |  | 205/205/258/258 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T297 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243347 | 05TIDD 3-4 | 243779 | 05WHELGS |  |  | 1 | 138 | 205 | 187 |  | 103.14 | N-1-1 | AEP_P1-2_#5195_760 | OPEN BRANCH FROM BUS 243347 TO BUS 243779 CKT 2 / 243347 05TIDD 3-4 138 243779 05WHELGS 138 2 | Base Case |  | 205/205/258/258 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T298 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 57 |  | 118.06 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | 50/50/63/63 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T299 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 56 |  | 191.14 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T300 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 56 |  | 188.45 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T301 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 44 |  | 177.46 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T302 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243022 | 05WOLF GLADE | 244182 | 05GALAX2 |  |  | 1 | 69 | 205 | 44 |  | 177.96 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | 44/44/56/56 | Yes | Part 4: Thermal Limits |  | Associated with S2179
AEP-T303 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 244222 | 05HOLSTON2 |  |  | 1 | 35 | 205 | 27 |  | 110.49 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 27/27/38/38 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T304 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 244222 | 05HOLSTON2 |  |  | 1 | 35 | 205 | 27 |  | 110.09 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 27/27/38/38 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T305 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 47 |  | 188.65 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T306 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 47 |  | 188.69 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T307 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 244222 | 05HOLSTON2 |  |  | 1 | 35 | 205 | 38 |  | 122.77 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 27/27/38/38 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T308 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 244222 | 05HOLSTON2 |  |  | 1 | 35 | 205 | 38 |  | 122.8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 27/27/38/38 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T309 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 247721 | 05KYLE HILLZ |  |  | 1 | 35 | 205 | 41 |  | 108.74 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 51/51/65/65 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by b3099
AEP-T310 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 247721 | 05KYLE HILLZ |  |  | 1 | 35 | 205 | 41 |  | 108.73 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 51/51/65/65 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by b3099
AEP-T311 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244213 | 05SEWAGEPL | 244219 | 05WKINGSP |  |  | 1 | 35 | 205 | 42 |  | 113.61 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 30/30/42/42 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T312 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 244218 | 05WKINGSEQ |  |  | 1 | 35/999 | 205 | 71 |  | 107.96 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 60/75/60/75 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T313 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 244218 | 05WKINGSEQ |  |  | 1 | 35/999 | 205 | 71 |  | 107.96 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 60/75/60/75 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T314 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244213 | 05SEWAGEPL |  |  | 1 | 35 | 205 | 43 |  | 110.32 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 30/30/43/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T315 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 244213 | 05SEWAGEPL |  |  | 1 | 35 | 205 | 43 |  | 110.35 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 30/30/43/43 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by b3099
AEP-T316 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246234 | 05NBLUFFTN | 246235 | 05BLUFFTON |  |  | 1 | 69 | 205 | 50 |  | 102.8 | N-1-1 | AEP_P1-2_#11907_9398 | OPEN BRANCH FROM BUS 246245 TO BUS 246250 CKT 1 / 246245 05KINGSLAN 69.0 246250 05MAGLEY 69.0 1 | AEP_P1-3_#11948_05HILLCR 138_3 | OPEN BRANCH FROM BUS 243309 TO BUS 246124 CKT 3 / 243309 05HILLCR 138 246124 05HILLCREQ 999 3 OPEN BRANCH FROM BUS 246124 TO BUS 246242 CKT 3 / 246124 05HILLCREQ 999 246242 05HILLCRES 69.0 3 OPEN BRANCH FROM BUS 246240 TO BUS 246242 CKT 1 / 246240 05FERGUSON 69.0 246242 05HILLCRES 69.0 1 OPEN BRANCH FROM BUS 246242 TO BUS 246246 CKT 1 / 246242 05HILLCRES 69.0 246246 05KINNERK8 69.0 1 OPEN BRANCH FROM BUS 246148 TO BUS 246242 CKT 1 / 246148 05PETTIT AVE69.0 246242 05HILLCRES 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T317 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246234 | 05NBLUFFTN | 246235 | 05BLUFFTON |  |  | 1 | 69 | 205 | 50 |  | 102.83 | N-1-1 | AEP_P1-3_#11948_05HILLCR 138_3 | OPEN BRANCH FROM BUS 243309 TO BUS 246124 CKT 3 / 243309 05HILLCR 138 246124 05HILLCREQ 999 3 OPEN BRANCH FROM BUS 246124 TO BUS 246242 CKT 3 / 246124 05HILLCREQ 999 246242 05HILLCRES 69.0 3 OPEN BRANCH FROM BUS 246240 TO BUS 246242 CKT 1 / 246240 05FERGUSON 69.0 246242 05HILLCRES 69.0 1 OPEN BRANCH FROM BUS 246242 TO BUS 246246 CKT 1 / 246242 05HILLCRES 69.0 246246 05KINNERK8 69.0 1 OPEN BRANCH FROM BUS 246148 TO BUS 246242 CKT 1 / 246148 05PETTIT AVE69.0 246242 05HILLCRES 69.0 1 | AEP_P1-2_#11907_9398 | OPEN BRANCH FROM BUS 246245 TO BUS 246250 CKT 1 / 246245 05KINGSLAN 69.0 246250 05MAGLEY 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T318 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 104.1 | N-1-1 | AEP_P1-2_#5505_1728 | OPEN BRANCH FROM BUS 243237 TO BUS 246232 CKT 1 / 243237 05ADAM 138 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 246231 TO BUS 246232 CKT 1 / 246231 05ADAMS- 69.0 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243237 TO BUS 243358 CKT 1 / 243237 05ADAM 138 243358 05PENNVI 138 1 OPEN BRANCH FROM BUS 243319 TO BUS 243358 CKT 1 / 243319 05JAY 138 243358 05PENNVI 138 1 | AEP_P1-2_#8002_2001727 | OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T319 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 104.1 | N-1-1 | AEP_P1-2_#5505_1728 | OPEN BRANCH FROM BUS 243237 TO BUS 246232 CKT 1 / 243237 05ADAM 138 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 246231 TO BUS 246232 CKT 1 / 246231 05ADAMS- 69.0 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243237 TO BUS 243358 CKT 1 / 243237 05ADAM 138 243358 05PENNVI 138 1 OPEN BRANCH FROM BUS 243319 TO BUS 243358 CKT 1 / 243319 05JAY 138 243358 05PENNVI 138 1 | AEP_P1-3_#12010_05MAGLEY 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243334 TO BUS 246250 CKT 1 / 243334 05MAGLEY 138 246250 05MAGLEY 69.0 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T320 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 104.31 | N-1-1 | AEP_P1-3_#11947_05ADAM 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 246232 CKT 1 / 243237 05ADAM 138 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 246231 TO BUS 246232 CKT 1 / 246231 05ADAMS- 69.0 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243237 TO BUS 243358 CKT 1 / 243237 05ADAM 138 243358 05PENNVI 138 1 | AEP_P1-2_#8002_2001727 | OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T321 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 104.31 | N-1-1 | AEP_P1-3_#11947_05ADAM 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 246232 CKT 1 / 243237 05ADAM 138 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 246231 TO BUS 246232 CKT 1 / 246231 05ADAMS- 69.0 246232 05ADAMS1EQ 999 1 OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243237 TO BUS 243358 CKT 1 / 243237 05ADAM 138 243358 05PENNVI 138 1 | AEP_P1-3_#12010_05MAGLEY 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243334 TO BUS 246250 CKT 1 / 243334 05MAGLEY 138 246250 05MAGLEY 69.0 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T322 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 100.89 | N-1-1 | AEP_P1-2_#8002_2001727 | OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 | AEP_P1-2_#15020 | OPEN BRANCH FROM BUS 243278 TO BUS 247837 CKT 1 / 243278 05DESOTO 138 247837 05PERCH 138 1 OPEN BRANCH FROM BUS 243319 TO BUS 247837 CKT 1 / 243319 05JAY 138 247837 05PERCH 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T323 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 100.09 | N-1-1 | AEP_P1-3_#12010_05MAGLEY 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243334 TO BUS 246250 CKT 1 / 243334 05MAGLEY 138 246250 05MAGLEY 69.0 1 | AEP_P1-3_#13471_05LINCOLN1 138_1 | OPEN BRANCH FROM BUS 243330 TO BUS 246138 CKT 1 / 243330 05LINCOLN1 138 246138 05LINCO1EQ 999 1 OPEN BRANCH FROM BUS 246138 TO BUS 247119 CKT 1 / 246138 05LINCO1EQ 999 247119 05LINCOLN 69.0 1 OPEN BRANCH FROM BUS 246136 TO BUS 246138 CKT 1 / 246136 05LINCOLN 34.5 246138 05LINCO1EQ 999 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T324 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 100.06 | N-1-1 | AEP_P1-3_#13471_05LINCOLN1 138_1 | OPEN BRANCH FROM BUS 243330 TO BUS 246138 CKT 1 / 243330 05LINCOLN1 138 246138 05LINCO1EQ 999 1 OPEN BRANCH FROM BUS 246138 TO BUS 247119 CKT 1 / 246138 05LINCO1EQ 999 247119 05LINCOLN 69.0 1 OPEN BRANCH FROM BUS 246136 TO BUS 246138 CKT 1 / 246136 05LINCOLN 34.5 246138 05LINCO1EQ 999 1 | AEP_P1-3_#12010_05MAGLEY 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243334 TO BUS 246250 CKT 1 / 243334 05MAGLEY 138 246250 05MAGLEY 69.0 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T325 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 246242 | 05HILLCRES |  |  | 1 | 69 | 205 | 54 |  | 100.02 | N-1-1 | AEP_P1-2_#15020 | OPEN BRANCH FROM BUS 243278 TO BUS 247837 CKT 1 / 243278 05DESOTO 138 247837 05PERCH 138 1 OPEN BRANCH FROM BUS 243319 TO BUS 247837 CKT 1 / 243319 05JAY 138 247837 05PERCH 138 1 | AEP_P1-3_#12010_05MAGLEY 138_1 | OPEN BRANCH FROM BUS 243237 TO BUS 243334 CKT 1 / 243237 05ADAM 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243242 TO BUS 243334 CKT 1 / 243242 05ALLEN 138 243334 05MAGLEY 138 1 OPEN BRANCH FROM BUS 243334 TO BUS 246250 CKT 1 / 243334 05MAGLEY 138 246250 05MAGLEY 69.0 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3150
AEP-T326 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 35 |  | 136.66 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T327 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 35 |  | 136.61 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T328 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 35 |  | 124.43 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T329 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 35 |  | 123.22 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T330 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 102.33 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T331 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 102.29 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T332 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 41 |  | 107.36 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by B3151
AEP-T333 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246280 | 05GATEWY P | 246295 | 05WHITLEY |  |  | 1 | 35 | 205 | 41 |  | 107.36 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Solved by existing baseline project; Substation equipment exclusion | Solved by B3151
AEP-T334 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 106.33 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T335 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 106.32 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T336 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 102.28 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T337 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 246280 | 05GATEWY P |  |  | 1 | 69/35 | 205 | 31 |  | 101.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | 28/31/28/31 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3151
AEP-T338 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 246997 | 05PLETCHER |  |  | 1 | 69 | 205 | 75 |  | 105.89 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3160
AEP-T339 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 246997 | 05PLETCHER |  |  | 1 | 69 | 205 | 75 |  | 105.88 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3160
AEP-T340 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 246997 | 05PLETCHER |  |  | 1 | 69 | 205 | 75 |  | 105.87 | N-1-1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3160
AEP-T341 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 246997 | 05PLETCHER |  |  | 1 | 69 | 205 | 75 |  | 105.85 | N-1-1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by existing baseline project | Solved by B3160
AEP-T342 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244620 | 05PIKEVL | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 94 |  | 100.44 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 | Submitted for inclusion in Local Plan
AEP-T343 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244620 | 05PIKEVL | 244640 | 05S.PIKEV2 |  |  | 1 | 69 | 205 | 94 |  | 100.44 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | 75/75/94/94 | No | Part 4: Thermal Limits | Solved by S2220 which is in service in March 2020 | Associated with S2220 | Submitted for inclusion in Local Plan
AEP-T344 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 109.06 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T345 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 109.06 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T346 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 104.94 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T347 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 104.94 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T348 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 101.89 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T349 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 101.89 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T350 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 101.88 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T351 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 243735 | 05JEFF |  |  | 1 | 69 | 205 | 56 |  | 101.88 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-T352 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 245256 | 05W N PHIL |  |  | 1 | 138/35 | 205 | 20 |  | 186.22 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 156/167/177/186 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T353 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 245256 | 05W N PHIL |  |  | 1 | 138/35 | 205 | 20 |  | 191.91 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 156/167/177/186 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T354 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 37 |  | 141.94 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | 37/37/47/47 | Yes No | Part 4: Thermal Limits | Solved by existing baseline project | Potential M-3 need identified, awaiting field and engineering analysis Solved by b3099
AEP-T355 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244209 | 05REEDYCRK | 244211 | 05ARBUTUS SS |  |  | 1 | 35 | 205 | 37 |  | 141.68 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | 37/37/47/47 | Yes No | Part 4: Thermal Limits | Solved by existing baseline project | Potential M-3 need identified, awaiting field and engineering analysis Solved by b3099
AEP-T356 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245227 | 05GEN TIRE | 245240 | 05NEWCOMTW |  |  | 1 | 35 | 205 | 17 |  | 123.38 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 17/17/24/24 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T357 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245227 | 05GEN TIRE | 245240 | 05NEWCOMTW |  |  | 1 | 35 | 205 | 17 |  | 124.7 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 17/17/24/24 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T358 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245228 | 05GREER | 245245 | 05MILL ST SS |  |  | 1 | 35 | 205 | 15 |  | 223.34 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 15/15/22/22 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T359 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245228 | 05GREER | 245245 | 05MILL ST SS |  |  | 1 | 35 | 205 | 15 |  | 230.36 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 15/15/22/22 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T360 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245228 | 05GREER | 245245 | 05MILL ST SS |  |  | 1 | 35 | 205 | 22 |  | 157.77 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 15/15/22/22 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T361 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245228 | 05GREER | 245245 | 05MILL ST SS |  |  | 1 | 35 | 205 | 22 |  | 158.45 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 15/15/22/22 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T362 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245212 | 05GREERZ | 245229 | 05GREER |  |  | 1 | 69 | 205 | 31 |  | 115.09 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T363 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245212 | 05GREERZ | 245229 | 05GREER |  |  | 1 | 69 | 205 | 31 |  | 119.51 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 31/31/43/43 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T364 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 247447 | 05NEW PHILA |  |  | 1 | 35 | 205 | 23 |  | 132.6 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T365 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 247447 | 05NEW PHILA |  |  | 1 | 35 | 205 | 23 |  | 136.07 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 27/27/38/38 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T366 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245253 | 05NEWCOMTW | 245450 | 05KIMBLTN |  |  | 1 | 69 | 205 | 46 |  | 107.81 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-2_#12210_16598 | OPEN BRANCH FROM BUS 245445 TO BUS 245452 CKT 1 / 245445 05WBYESVLL 69.0 245452 05DERWENT 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T367 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245253 | 05NEWCOMTW | 245450 | 05KIMBLTN |  |  | 1 | 69 | 205 | 46 |  | 108.11 | N-1-1 | AEP_P1-2_#12210_16598 | OPEN BRANCH FROM BUS 245445 TO BUS 245452 CKT 1 / 245445 05WBYESVLL 69.0 245452 05DERWENT 69.0 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T368 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245450 | 05KIMBLTN | 245493 | 05SALTFRKZ |  |  | 1 | 69 | 205 | 46 |  | 105.92 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-2_#12210_16598 | OPEN BRANCH FROM BUS 245445 TO BUS 245452 CKT 1 / 245445 05WBYESVLL 69.0 245452 05DERWENT 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T369 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246593 | 05LAZELLE S | 246830 | 05LAZELLE N |  |  | Z1 | 69 | 205 | 69 |  | 110.24 | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2 | OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 OPEN BRANCH FROM BUS 243513 TO BUS 246613 CKT 2 / 243513 05GENOA 138 246613 05GENOA 69.0 2 OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 OPEN BRANCH FROM BUS 246613 TO BUS 246643 CKT 1 / 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1 REMOVE SWSHUNT FROM BUS 246613 / 246613 05GENOA 69.0 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 55/69/72/82 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T370 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246593 | 05LAZELLE S | 246830 | 05LAZELLE N |  |  | Z1 | 69 | 205 | 69 |  | 110.23 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-3_#11531_05GENOA 138_2 | OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 OPEN BRANCH FROM BUS 243513 TO BUS 246613 CKT 2 / 243513 05GENOA 138 246613 05GENOA 69.0 2 OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 OPEN BRANCH FROM BUS 246613 TO BUS 246643 CKT 1 / 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1 REMOVE SWSHUNT FROM BUS 246613 / 246613 05GENOA 69.0 | 55/69/72/82 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T371 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246593 | 05LAZELLE S | 246830 | 05LAZELLE N |  |  | Z1 | 69 | 205 | 69 |  | 110.06 | N-1-1 | AEP_P1-2_#11532_805 | OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | 55/69/72/82 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T372 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246593 | 05LAZELLE S | 246830 | 05LAZELLE N |  |  | Z1 | 69 | 205 | 69 |  | 110.06 | N-1-1 | AEP_P1-3_#11595_05HUNTLEY2 138_4 | OPEN BRANCH FROM BUS 243512 TO BUS 246370 CKT 1 / 243512 05DIAMONDISS 138 246370 05HUNTLEY2 138 1 OPEN BRANCH FROM BUS 246370 TO BUS 246635 CKT 4 / 246370 05HUNTLEY2 138 246635 05HUNTLEY 69.0 4 | AEP_P1-2_#11532_805 | OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 | 55/69/72/82 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T373 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245450 | 05KIMBLTN | 245493 | 05SALTFRKZ |  |  | 1 | 69 | 205 | 46 |  | 106.32 | N-1-1 | AEP_P1-2_#12210_16598 | OPEN BRANCH FROM BUS 245445 TO BUS 245452 CKT 1 / 245445 05WBYESVLL 69.0 245452 05DERWENT 69.0 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T374 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 245256 | 05W N PHIL |  |  | 1 | 138/35 | 205 | 22 |  | 173.75 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 156/167/177/186 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T375 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 245256 | 05W N PHIL |  |  | 1 | 138/35 | 205 | 22 |  | 174.16 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 156/167/177/186 | No | Part 4: Thermal Limits | Substation equipment exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T376 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245577 | 05E.LANCASTZ | 245581 | 05LANCASTE |  |  | 1 | 69 | 205 | 40 |  | 136.9 | N-1-1 | AEP_P1-2_#5723_751 | OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 245595 CKT 1 / 243104 05SLANCS 138 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 244707 TO BUS 245595 CKT 1 / 244707 05HEFT SS 69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245586 TO BUS 245595 CKT 1 / 245586 05QUARRY R 69.0 245595 05S.LANCAST269.0 1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T377 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245577 | 05E.LANCASTZ | 245581 | 05LANCASTE |  |  | 1 | 69 | 205 | 40 |  | 136.89 | N-1-1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | AEP_P1-2_#5723_751 | OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 245595 CKT 1 / 243104 05SLANCS 138 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 244707 TO BUS 245595 CKT 1 / 244707 05HEFT SS 69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245586 TO BUS 245595 CKT 1 / 245586 05QUARRY R 69.0 245595 05S.LANCAST269.0 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T378 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246313 | 05DODGE SS | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 57 |  | 153.36 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 54/54/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T379 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246313 | 05DODGE SS | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 57 |  | 153.36 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 54/54/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T380 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245582 | 05LANCAST JT | 245828 | 05LANCAS JTZ |  |  | Z1 | 69 | 205 | 35 |  | 100.7 | N-1-1 | AEP_P1-2_#11546_4387 | OPEN BRANCH FROM BUS 245575 TO BUS 245577 CKT 1 / 245575 05E LANCST 69.0 245577 05E.LANCASTZ69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245581 CKT 1 / 245577 05E.LANCASTZ69.0 245581 05LANCASTE 69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | 35/35/48/48 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T381 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245582 | 05LANCAST JT | 245828 | 05LANCAS JTZ |  |  | Z1 | 69 | 205 | 35 |  | 100.69 | N-1-1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | AEP_P1-2_#11546_4387 | OPEN BRANCH FROM BUS 245575 TO BUS 245577 CKT 1 / 245575 05E LANCST 69.0 245577 05E.LANCASTZ69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245581 CKT 1 / 245577 05E.LANCASTZ69.0 245581 05LANCASTE 69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 | 35/35/48/48 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T382 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246314 | 05DRAGOON | 246341 | 05RAILROAD |  |  | 1 | 35 | 205 | 56 |  | 106.73 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T383 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246314 | 05DRAGOON | 246341 | 05RAILROAD |  |  | 1 | 35 | 205 | 56 |  | 106.73 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T384 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245581 | 05LANCASTE | 245591 | 05S.LANCAST1 |  |  | 1 | 69 | 205 | 40 |  | 111.34 | N-1-1 | AEP_P1-2_#5723_751 | OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 245595 CKT 1 / 243104 05SLANCS 138 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 244707 TO BUS 245595 CKT 1 / 244707 05HEFT SS 69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245586 TO BUS 245595 CKT 1 / 245586 05QUARRY R 69.0 245595 05S.LANCAST269.0 1 | AEP_P1-3_#11608_05W.LANCAST1 138_2 | OPEN BRANCH FROM BUS 243023 TO BUS 243149 CKT 1 / 243023 05HOCKNG 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243089 TO BUS 243149 CKT 1 / 243089 05SBALTM 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243149 TO BUS 246290 CKT 2 / 243149 05W.LANCAST1 138 246290 05W.LANCAST269.0 2 OPEN BRANCH FROM BUS 245569 TO BUS 246290 CKT 1 / 245569 05ANCHR HOC169.0 246290 05W.LANCAST269.0 1 OPEN BRANCH FROM BUS 245573 TO BUS 245589 CKT 1 / 245573 05DELMONT8 69.0 245589 05S C P 1 69.0 1 OPEN BRANCH FROM BUS 245573 TO BUS 246290 CKT 1 / 245573 05DELMONT8 69.0 246290 05W.LANCAST269.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T385 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245581 | 05LANCASTE | 245591 | 05S.LANCAST1 |  |  | 1 | 69 | 205 | 40 |  | 111.34 | N-1-1 | AEP_P1-3_#11608_05W.LANCAST1 138_2 | OPEN BRANCH FROM BUS 243023 TO BUS 243149 CKT 1 / 243023 05HOCKNG 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243089 TO BUS 243149 CKT 1 / 243089 05SBALTM 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243149 TO BUS 246290 CKT 2 / 243149 05W.LANCAST1 138 246290 05W.LANCAST269.0 2 OPEN BRANCH FROM BUS 245569 TO BUS 246290 CKT 1 / 245569 05ANCHR HOC169.0 246290 05W.LANCAST269.0 1 OPEN BRANCH FROM BUS 245573 TO BUS 245589 CKT 1 / 245573 05DELMONT8 69.0 245589 05S C P 1 69.0 1 OPEN BRANCH FROM BUS 245573 TO BUS 246290 CKT 1 / 245573 05DELMONT8 69.0 246290 05W.LANCAST269.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 | AEP_P1-2_#5723_751 | OPEN BRANCH FROM BUS 243104 TO BUS 243149 CKT 1 / 243104 05SLANCS 138 243149 05W.LANCAST1 138 1 OPEN BRANCH FROM BUS 243104 TO BUS 245595 CKT 1 / 243104 05SLANCS 138 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 244707 TO BUS 245595 CKT 1 / 244707 05HEFT SS 69.0 245595 05S.LANCAST269.0 1 OPEN BRANCH FROM BUS 245586 TO BUS 245595 CKT 1 / 245586 05QUARRY R 69.0 245595 05S.LANCAST269.0 1 | 40/40/56/56 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T386 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 246357 | 05SOUTHBEN |  |  | 1 | 35 | 205 | 62 |  | 105.01 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T387 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 246357 | 05SOUTHBEN |  |  | 1 | 35 | 205 | 62 |  | 104.82 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T388 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245587 | 05RALSTON | 245828 | 05LANCAS JTZ |  |  | 1 | 69 | 205 | 35 |  | 126.99 | N-1-1 | AEP_P1-2_#11546_4387 | OPEN BRANCH FROM BUS 245575 TO BUS 245577 CKT 1 / 245575 05E LANCST 69.0 245577 05E.LANCASTZ69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245581 CKT 1 / 245577 05E.LANCASTZ69.0 245581 05LANCASTE 69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | 35/35/48/48 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T389 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245587 | 05RALSTON | 245828 | 05LANCAS JTZ |  |  | 1 | 69 | 205 | 35 |  | 127 | N-1-1 | AEP_P1-3_#11609_05W.LANCAST2 138_1 | OPEN BRANCH FROM BUS 243025 TO BUS 246021 CKT 1 / 243025 05JUNCTN 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 243552 TO BUS 246021 CKT 1 / 243552 05PICKR8 138 246021 05W.LANCAST2 138 1 OPEN BRANCH FROM BUS 245599 TO BUS 246021 CKT 1 / 245599 05W.LANCAST169.0 246021 05W.LANCAST2 138 1 REMOVE SWSHUNT FROM BUS 246021 / 246021 05W.LANCAST2 138 OPEN BRANCH FROM BUS 245570 TO BUS 245590 CKT 1 / 245570 05ANCHRHC8 69.0 245590 05S C P 2 69.0 1 OPEN BRANCH FROM BUS 245570 TO BUS 245599 CKT 1 / 245570 05ANCHRHC8 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245583 TO BUS 245599 CKT 1 / 245583 05MEM DRIV 69.0 245599 05W.LANCAST169.0 1 OPEN BRANCH FROM BUS 245599 TO BUS 246290 CKT Z1 / 245599 05W.LANCAST169.0 246290 05W.LANCAST269.0 Z1 REMOVE SWSHUNT FROM BUS 245599 / 245599 05W.LANCAST169.0 | AEP_P1-2_#11546_4387 | OPEN BRANCH FROM BUS 245575 TO BUS 245577 CKT 1 / 245575 05E LANCST 69.0 245577 05E.LANCASTZ69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245581 CKT 1 / 245577 05E.LANCASTZ69.0 245581 05LANCASTE 69.0 1 OPEN BRANCH FROM BUS 245577 TO BUS 245595 CKT 1 / 245577 05E.LANCASTZ69.0 245595 05S.LANCAST269.0 1 | 35/35/48/48 | Yes | Part 4: Thermal Limits |  | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T390 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245129 | 05EASTON S | 245156 | 05N CANTON |  |  | 1 | 69 | 205 | 54 |  | 109.66 | N-1-1 | AEP_P1-3_#11759_05WAGENHALS2 138_2 | OPEN BRANCH FROM BUS 243139 TO BUS 245195 CKT 2 / 243139 05WAGENHALS2 138 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245192 TO BUS 245195 CKT 2 / 245192 05WAGNHAL2 69.0 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245193 TO BUS 245195 CKT 1 / 245193 05WAGNHAL2 23.0 245195 05WAGNL2EQ 999 1 OPEN BRANCH FROM BUS 243139 TO BUS 246267 CKT Z1 / 243139 05WAGENHALS2 138 246267 05WAGENHALS1 138 Z1 OPEN BRANCH FROM BUS 242980 TO BUS 243139 CKT 2 / 242980 05CANTNC 138 243139 05WAGENHALS2 138 2 OPEN BRANCH FROM BUS 243139 TO BUS 244070 CKT 1 / 243139 05WAGENHALS2 138 244070 05JUNE ROAD 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 243772 CKT 2 / 243139 05WAGENHALS2 138 243772 05LTV2 138 2 OPEN BRANCH FROM BUS 243052 TO BUS 243139 CKT 1 / 243052 05NECANT 138 243139 05WAGENHALS2 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 244943 CKT 1 / 243139 05WAGENHALS2 138 244943 05PACKARD BP 138 1 OPEN BRANCH FROM BUS 245127 TO BUS 245192 CKT 2 / 245127 05E CANTON 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245189 TO BUS 245192 CKT 2 / 245189 05W LOUISV 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245193 TO BUS 247301 CKT 1 / 245193 05WAGNHAL2 23.0 247301 05GEORGTW2 23.0 1 | AEP_P1-2_#6604_3700745 | OPEN BRANCH FROM BUS 243077 TO BUS 243134 CKT 1 / 243077 05PROMWY 138 243134 05W.CANTON1 138 1 OPEN BRANCH FROM BUS 243077 TO BUS 243142 CKT 1 / 243077 05PROMWY 138 243142 05WAYVIE 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T391 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245129 | 05EASTON S | 245156 | 05N CANTON |  |  | 1 | 69 | 205 | 54 |  | 108.82 | N-1-1 | AEP_P1-2_#6604_3700745 | OPEN BRANCH FROM BUS 243077 TO BUS 243134 CKT 1 / 243077 05PROMWY 138 243134 05W.CANTON1 138 1 OPEN BRANCH FROM BUS 243077 TO BUS 243142 CKT 1 / 243077 05PROMWY 138 243142 05WAYVIE 138 1 | AEP_P1-3_#11759_05WAGENHALS2 138_2 | OPEN BRANCH FROM BUS 243139 TO BUS 245195 CKT 2 / 243139 05WAGENHALS2 138 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245192 TO BUS 245195 CKT 2 / 245192 05WAGNHAL2 69.0 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245193 TO BUS 245195 CKT 1 / 245193 05WAGNHAL2 23.0 245195 05WAGNL2EQ 999 1 OPEN BRANCH FROM BUS 243139 TO BUS 246267 CKT Z1 / 243139 05WAGENHALS2 138 246267 05WAGENHALS1 138 Z1 OPEN BRANCH FROM BUS 242980 TO BUS 243139 CKT 2 / 242980 05CANTNC 138 243139 05WAGENHALS2 138 2 OPEN BRANCH FROM BUS 243139 TO BUS 244070 CKT 1 / 243139 05WAGENHALS2 138 244070 05JUNE ROAD 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 243772 CKT 2 / 243139 05WAGENHALS2 138 243772 05LTV2 138 2 OPEN BRANCH FROM BUS 243052 TO BUS 243139 CKT 1 / 243052 05NECANT 138 243139 05WAGENHALS2 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 244943 CKT 1 / 243139 05WAGENHALS2 138 244943 05PACKARD BP 138 1 OPEN BRANCH FROM BUS 245127 TO BUS 245192 CKT 2 / 245127 05E CANTON 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245189 TO BUS 245192 CKT 2 / 245189 05W LOUISV 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245193 TO BUS 247301 CKT 1 / 245193 05WAGNHAL2 23.0 247301 05GEORGTW2 23.0 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T392 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 246357 | 05SOUTHBEN |  |  | 1 | 35 | 205 | 62 |  | 105.01 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 62/62/78/78 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T393 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 131.73 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T394 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 131.73 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T395 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 117.86 | N-1-1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T396 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 107.51 | N-1-1 | AEP_P1-2_#13895 | OPEN BRANCH FROM BUS 244262 TO BUS 246408 CKT 1 / 244262 05MACKEY 34.5 246408 05OSOLO 34.5 1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T397 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 102.74 | N-1-1 | AEP_P1-2_#6934_3800000 | OPEN BRANCH FROM BUS 243385 TO BUS 243517 CKT 1 / 243385 05TWIN B 138 243517 05CAP AV 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T398 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 39 |  | 108.41 | FB | AEP_P4_#10134_05HOWARD 138_B | OPEN BRANCH FROM BUS 243024 TO BUS 243117 CKT 1 / 243024 05HOWARD 138 243117 05SULFRS 138 1 OPEN BRANCH FROM BUS 242984 TO BUS 932050 CKT 1 / 242984 05CHATFL 138 932050 AC2-015 TAP 138 1 OPEN BRANCH FROM BUS 932050 TO BUS 243024 CKT 1 / 932050 AC2-015 TAP 138 243024 05HOWARD 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243100 CKT 1 / 243024 05HOWARD 138 243100 05SHELGH 138 1 OPEN BRANCH FROM BUS 243024 TO BUS 243050 CKT 1 / 243024 05HOWARD 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 241111 TO BUS 243024 CKT 1 / 241111 02ASHLAND 138 243024 05HOWARD 138 1 OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 OPEN BRANCH FROM BUS 242984 TO BUS 245656 CKT 1 / 242984 05CHATFL 138 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245656 TO BUS 247380 CKT 1 / 245656 05CHATFIEL 69.0 247380 05NEW WASHSS69.0 1 REMOVE SWSHUNT FROM BUS 243024 / 243024 05HOWARD 138 |  |  | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T399 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 39 |  | 102.85 | FB | AEP_P4_#14113_05MELMOR 138_C2 | OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 OPEN BRANCH FROM BUS 242984 TO BUS 245656 CKT 1 / 242984 05CHATFL 138 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245656 TO BUS 247380 CKT 1 / 245656 05CHATFIEL 69.0 247380 05NEW WASHSS69.0 1 OPEN BRANCH FROM BUS 242984 TO BUS 932050 CKT 1 / 242984 05CHATFL 138 932050 AC2-015 TAP 138 1 OPEN BRANCH FROM BUS 932050 TO BUS 243024 CKT 1 / 932050 AC2-015 TAP 138 243024 05HOWARD 138 1 |  |  | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T400 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 123.32 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T401 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 123.32 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T402 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 105.85 | N-1-1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T403 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245621 | 05GREENLAW | 245646 | 05E.TIFF2 |  |  | 1 | 69 | 205 | 39 |  | 102.35 | FB | AEP_P4_#7112_05MELMOR 138_C | OPEN BRANCH FROM BUS 243039 TO BUS 243110 CKT 1 / 243039 05MELMOR 138 243110 05STIFFI 138 1 OPEN BRANCH FROM BUS 243110 TO BUS 243137 CKT 1 / 243110 05STIFFI 138 243137 05W.END FOS1 138 1 OPEN BRANCH FROM BUS 243110 TO BUS 245630 CKT 1 / 243110 05STIFFI 138 245630 05S TIFFIN 69.0 1 OPEN BRANCH FROM BUS 242984 TO BUS 243039 CKT 1 / 242984 05CHATFL 138 243039 05MELMOR 138 1 OPEN BRANCH FROM BUS 242984 TO BUS 245656 CKT 1 / 242984 05CHATFL 138 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245655 TO BUS 245656 CKT 1 / 245655 05CARROTHR 69.0 245656 05CHATFIEL 69.0 1 OPEN BRANCH FROM BUS 245656 TO BUS 247380 CKT 1 / 245656 05CHATFIEL 69.0 247380 05NEW WASHSS69.0 1 OPEN BRANCH FROM BUS 242984 TO BUS 932050 CKT 1 / 242984 05CHATFL 138 932050 AC2-015 TAP 138 1 OPEN BRANCH FROM BUS 932050 TO BUS 243024 CKT 1 / 932050 AC2-015 TAP 138 243024 05HOWARD 138 1 |  |  | 39/39/49/49 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T404 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246198 | 05HARLAN | 246208 | 05ROBISONP |  |  | 1 | 69 | 205 | 50 |  | 103.1 | N-1-1 | AEP_P1-2_#14793 | OPEN BRANCH FROM BUS 243086 TO BUS 247108 CKT 1 / 243086 05S HICK 138 247108 05SOWERS 138 1 OPEN BRANCH FROM BUS 243086 TO BUS 243179 CKT 1 / 243086 05S HICK 138 243179 05S HICKSV 69.0 1 OPEN BRANCH FROM BUS 243029 TO BUS 243086 CKT 1 / 243029 05LCKWRD 138 243086 05S HICK 138 1 | AEP_P1-2_#11894_847 | REMOVE LOAD C1 FROM BUS 247109 / 247109 05JOIST SS 69.0 C1 OPEN BRANCH FROM BUS 246182 TO BUS 247109 CKT 1 / 246182 05AUBURN 69.0 247109 05JOIST SS 69.0 1 OPEN BRANCH FROM BUS 246185 TO BUS 247109 CKT 1 / 246185 05BUTLER 69.0 247109 05JOIST SS 69.0 1 OPEN BRANCH FROM BUS 246194 TO BUS 247109 CKT 1 / 246194 05NEW MILENM69.0 247109 05JOIST SS 69.0 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-IM014 | Solution
AEP-T405 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 247492 | 05LIBERTYTSS |  |  | 1 | 35 | 205 | 45 |  | 112.19 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 62/62/78/78 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T406 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 247492 | 05LIBERTYTSS |  |  | 1 | 35 | 205 | 45 |  | 112.19 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 62/62/78/78 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T407 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245663 | 05HOWARD | 245679 | 05WILLARD |  |  | 1 | 69 | 205 | 44 |  | 102.81 | Line w/o Fault | AEP_P2-1_245669 05N WILLAR 69.0 247193 05BULLHDSS 69.0 1 | OPEN BRANCH FROM BUS 245669 TO BUS 247193 CKT 1 |  |  | 44/44/56/56 | Yes No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T408 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 105.85 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T409 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244827 | 05KELLY CK | 244848 | 05CABNCRK1 |  |  | 1 | 46 | 205 | 31 |  | 108.38 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | 31/31/43/43 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T410 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244827 | 05KELLY CK | 244848 | 05CABNCRK1 |  |  | 1 | 46 | 205 | 31 |  | 108.4 | N-1-1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | 31/31/43/43 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-T411 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 117.86 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T412 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 45 |  | 105.16 | N-1-1 | AEP_P1-2_#5236_2841 | OPEN BRANCH FROM BUS 243765 TO BUS 246155 CKT Z1 / 243765 05FORD LIMA1 138 246155 05FORD LIMA2 138 Z1 OPEN BRANCH FROM BUS 243082 TO BUS 243765 CKT 1 / 243082 05ROCKHILL1 138 243765 05FORD LIMA1 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T413 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244110 | 05MERRIMAC | 244111 | 05MIDWAY |  |  | 1 | 69 | 205 | 44 |  | 109.31 | N-1-1 | AEP_P1-2_#6405_14677 | OPEN BRANCH FROM BUS 242708 TO BUS 243874 CKT 1 / 242708 05M FUNK 138 243874 05TECHDR 138 1 | AEP_P1-2_#10192 | OPEN BRANCH FROM BUS 242608 TO BUS 247869 CKT 1 / 242608 05CLYTR1 138 247869 05CLAYTR HY1 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242610 CKT Z1 / 242608 05CLYTR1 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242608 TO BUS 242666 CKT 1 / 242608 05CLYTR1 138 242666 05HAZELH 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242791 CKT 1 / 242608 05CLYTR1 138 242791 05SCHRIS 138 1 OPEN BRANCH FROM BUS 242906 TO BUS 247869 CKT 1 / 242906 05CLAY-1 11.0 247869 05CLAYTR HY1 138 1 REMOVE UNIT 1 FROM BUS 242906 / 242906 05CLAY-1 11.0 1 REMOVE UNIT 2 FROM BUS 242906 / 242906 05CLAY-1 11.0 2 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T414 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244110 | 05MERRIMAC | 244111 | 05MIDWAY |  |  | 1 | 69 | 205 | 44 |  | 109.32 | N-1-1 | AEP_P1-2_#10192 | OPEN BRANCH FROM BUS 242608 TO BUS 247869 CKT 1 / 242608 05CLYTR1 138 247869 05CLAYTR HY1 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242610 CKT Z1 / 242608 05CLYTR1 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242608 TO BUS 242666 CKT 1 / 242608 05CLYTR1 138 242666 05HAZELH 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242791 CKT 1 / 242608 05CLYTR1 138 242791 05SCHRIS 138 1 OPEN BRANCH FROM BUS 242906 TO BUS 247869 CKT 1 / 242906 05CLAY-1 11.0 247869 05CLAYTR HY1 138 1 REMOVE UNIT 1 FROM BUS 242906 / 242906 05CLAY-1 11.0 1 REMOVE UNIT 2 FROM BUS 242906 / 242906 05CLAY-1 11.0 2 | AEP_P1-2_#6405_14677 | OPEN BRANCH FROM BUS 242708 TO BUS 243874 CKT 1 / 242708 05M FUNK 138 243874 05TECHDR 138 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T415 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 107.54 | N-1-1 | AEP_P1-2_#11794_903 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 | AEP_P1-3_#11852_05NDELPH 138_1 | OPEN BRANCH FROM BUS 243051 TO BUS 243175 CKT 1 / 243051 05NDELPH 138 243175 05N DELPHO 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T416 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245825 | 05EXC&L PM | 245849 | 05STERLING1 |  |  | 1 | 35 | 205 | 45 |  | 105.16 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5236_2841 | OPEN BRANCH FROM BUS 243765 TO BUS 246155 CKT Z1 / 243765 05FORD LIMA1 138 246155 05FORD LIMA2 138 Z1 OPEN BRANCH FROM BUS 243082 TO BUS 243765 CKT 1 / 243082 05ROCKHILL1 138 243765 05FORD LIMA1 138 1 | 50/50/63/63 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T417 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246415 | 05KLINE | 247609 | 05KLINE 2EQ |  |  | 2 | 35/999 | 205 | 60 |  | 102.74 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#6934_3800000 | OPEN BRANCH FROM BUS 243385 TO BUS 243517 CKT 1 / 243385 05TWIN B 138 243517 05CAP AV 138 1 | 60/60/60/60 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T418 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244110 | 05MERRIMAC | 244111 | 05MIDWAY |  |  | 1 | 69 | 205 | 56 |  | 109.7 | N-1-1 | AEP_P1-2_#6405_14677 | OPEN BRANCH FROM BUS 242708 TO BUS 243874 CKT 1 / 242708 05M FUNK 138 243874 05TECHDR 138 1 | AEP_P1-2_#10192 | OPEN BRANCH FROM BUS 242608 TO BUS 247869 CKT 1 / 242608 05CLYTR1 138 247869 05CLAYTR HY1 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242610 CKT Z1 / 242608 05CLYTR1 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242608 TO BUS 242666 CKT 1 / 242608 05CLYTR1 138 242666 05HAZELH 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242791 CKT 1 / 242608 05CLYTR1 138 242791 05SCHRIS 138 1 OPEN BRANCH FROM BUS 242906 TO BUS 247869 CKT 1 / 242906 05CLAY-1 11.0 247869 05CLAYTR HY1 138 1 REMOVE UNIT 1 FROM BUS 242906 / 242906 05CLAY-1 11.0 1 REMOVE UNIT 2 FROM BUS 242906 / 242906 05CLAY-1 11.0 2 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T419 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 118.27 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T420 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 118.04 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T421 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 244711 | 05FULKS |  |  | 1 | 35 | 205 | 43 |  | 103.82 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 56/56/56/56 54/70/76/87 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T422 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 244711 | 05FULKS |  |  | 1 | 35 | 205 | 43 |  | 103.78 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 56/56/56/56 54/70/76/87 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T423 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244110 | 05MERRIMAC | 244111 | 05MIDWAY |  |  | 1 | 69 | 205 | 56 |  | 109.7 | N-1-1 | AEP_P1-2_#10192 | OPEN BRANCH FROM BUS 242608 TO BUS 247869 CKT 1 / 242608 05CLYTR1 138 247869 05CLAYTR HY1 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242610 CKT Z1 / 242608 05CLYTR1 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242608 TO BUS 242666 CKT 1 / 242608 05CLYTR1 138 242666 05HAZELH 138 1 OPEN BRANCH FROM BUS 242608 TO BUS 242791 CKT 1 / 242608 05CLYTR1 138 242791 05SCHRIS 138 1 OPEN BRANCH FROM BUS 242906 TO BUS 247869 CKT 1 / 242906 05CLAY-1 11.0 247869 05CLAYTR HY1 138 1 REMOVE UNIT 1 FROM BUS 242906 / 242906 05CLAY-1 11.0 1 REMOVE UNIT 2 FROM BUS 242906 / 242906 05CLAY-1 11.0 2 | AEP_P1-2_#6405_14677 | OPEN BRANCH FROM BUS 242708 TO BUS 243874 CKT 1 / 242708 05M FUNK 138 243874 05TECHDR 138 1 | 44/44/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T424 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 119.01 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T425 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 247492 | 05LIBERTYTSS |  |  | 1 | 35 | 205 | 45 |  | 102.25 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 62/62/78/78 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T426 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 247492 | 05LIBERTYTSS |  |  | 1 | 35 | 205 | 45 |  | 102.15 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 62/62/78/78 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T427 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 118.27 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T428 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 109.02 | N-1-1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T429 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 119 | N-1-1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T430 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 107.6 | N-1-1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T431 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245558 | 05PITTSBUR | 245562 | 05W MT VER |  |  | 1 | 69 | 205 | 46 |  | 107.6 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | 46/46/65/65 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T432 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243179 | 05S HICKSV | 245886 | 05MARK CEN |  |  | 1 | 69 | 205 | 53 |  | 101.86 | Tower | AEP_P7-1_#11067 | OPEN BRANCH FROM BUS 246352 TO BUS 246950 CKT 1 / 246352 05HAVILAND2 138 246950 05TIMBSS 138 1 OPEN BRANCH FROM BUS 243051 TO BUS 247864 CKT 1 / 243051 05NDELPH 138 247864 05LOGTOWN 138 1 |  |  | 257/257/325/325 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T433 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245698 | 05S.UPSDSS | 245715 | 05U SANDSK |  |  | 1 | 69 | 205 | 40 |  | 105.33 | N-1-1 | AEP_P1-3_#12189_05WMTVER 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 243153 CKT 1 / 242950 05ACADEM 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 242963 TO BUS 243153 CKT 1 / 242963 05HEDDSS 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 243098 TO BUS 243153 CKT 1 / 243098 05SHARPR 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 243153 TO BUS 245562 CKT 1 / 243153 05WMTVER 138 245562 05W MT VER 69.0 1 OPEN BRANCH FROM BUS 245558 TO BUS 245562 CKT 1 / 245558 05PITTSBUR 69.0 245562 05W MT VER 69.0 1 REMOVE SWSHUNT FROM BUS 245562 / 245562 05W MT VER 69.0 | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T434 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 107.54 | N-1-1 | AEP_P1-3_#11852_05NDELPH 138_1 | OPEN BRANCH FROM BUS 243051 TO BUS 243175 CKT 1 / 243051 05NDELPH 138 243175 05N DELPHO 69.0 1 | AEP_P1-2_#11794_903 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T435 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 102.04 | N-1-1 | AEP_P1-2_#6934_3800000 | OPEN BRANCH FROM BUS 243385 TO BUS 243517 CKT 1 / 243385 05TWIN B 138 243517 05CAP AV 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T436 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 114.2 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T437 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 54 |  | 107.54 | N-1-1 | AEP_P1-3_#11852_05NDELPH 138_1 | OPEN BRANCH FROM BUS 243051 TO BUS 243175 CKT 1 / 243051 05NDELPH 138 243175 05N DELPHO 69.0 1 | AEP_P1-3_#12221_05W VAN WR 69 | OPEN BRANCH FROM BUS 245866 TO BUS 245870 CKT 1 / 245866 05CAVETT 69.0 245870 05CONVOY8 69.0 1 OPEN BRANCH FROM BUS 243169 TO BUS 245866 CKT 1 / 243169 05HAVILND2 69.0 245866 05CAVETT 69.0 1 OPEN BRANCH FROM BUS 245866 TO BUS 245912 CKT 1 / 245866 05CAVETT 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245903 TO BUS 245912 CKT 1 / 245903 05S VAN WR 69.0 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 245912 CKT 1 / 245911 05W VAN WR 34.5 245912 05W VAN WR 69.0 1 OPEN BRANCH FROM BUS 245911 TO BUS 247878 CKT 1 / 245911 05W VAN WR 34.5 247878 05SW.VANW SS34.5 1 OPEN BRANCH FROM BUS 245895 TO BUS 247878 CKT 1 / 245895 05WOHCTYSS 34.5 247878 05SW.VANW SS34.5 1 | 54/54/76/76 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T438 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245698 | 05S.UPSDSS | 245715 | 05U SANDSK |  |  | 1 | 69 | 205 | 40 |  | 105.35 | N-1-1 | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 | AEP_P1-3_#12189_05WMTVER 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 243153 CKT 1 / 242950 05ACADEM 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 242963 TO BUS 243153 CKT 1 / 242963 05HEDDSS 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 243098 TO BUS 243153 CKT 1 / 243098 05SHARPR 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 243153 TO BUS 245562 CKT 1 / 243153 05WMTVER 138 245562 05W MT VER 69.0 1 OPEN BRANCH FROM BUS 245558 TO BUS 245562 CKT 1 / 245558 05PITTSBUR 69.0 245562 05W MT VER 69.0 1 REMOVE SWSHUNT FROM BUS 245562 / 245562 05W MT VER 69.0 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T439 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 114.01 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T440 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 106.05 | N-1-1 | AEP_P1-3_#13715_05CAP AV 34.5_1 | OPEN BRANCH FROM BUS 243517 TO BUS 246389 CKT 1 / 243517 05CAP AV 138 246389 05CAP AV 34.5 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T441 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246357 | 05SOUTHBEN | 246353 | 05S.BEND 5EQ |  |  | 5 | 35/999 | 205 | 55 |  | 114.2 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 30/30/30/30 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T442 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 37 |  | 120.13 | Single | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T443 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 37 |  | 119.44 | Single | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T444 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 37 |  | 119.44 | Line w/o Fault | AEP_P2-1_246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T445 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 37 |  | 120.13 | FB | AEP_P4_#14139_05TWIN B 138_V1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T446 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 37 |  | 120.13 | Bus | AEP_P2-2_#14780_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 |  |  | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T447 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 132.94 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T448 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 247447 | 05NEW PHILA |  |  | 1 | 35 | 205 | 23 |  | 136.62 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | 27/27/38/38 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T449 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245236 | 05NEWPHIL_1Z | 247447 | 05NEW PHILA |  |  | 1 | 35 | 205 | 23 |  | 137.12 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | 27/27/38/38 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T450 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245640 | 05W END | 247811 | 05LUMBERJ SS |  |  | 1 | 69 | 205 | 40 |  | 108.13 | N-1-1 | AEP_P1-3_#11998_05SBERWI 345_1 | OPEN BRANCH FROM BUS 242917 TO BUS 242942 CKT 1 / 242917 05SBERW EQ 999 242942 05SBERWI 345 1 OPEN BRANCH FROM BUS 242917 TO BUS 243180 CKT 1 / 242917 05SBERW EQ 999 243180 05SBERWICK 69.0 1 OPEN BRANCH FROM BUS 242917 TO BUS 243199 CKT 1 / 242917 05SBERW EQ 999 243199 05SBERW1-L 12.0 1 | AEP_P1-3_#14673_05BUCKLR 138_1 | OPEN BRANCH FROM BUS 242974 TO BUS 245607 CKT 1 / 242974 05BUCKLR 138 245607 05BUCKLY R 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 245626 CKT 1 / 245607 05BUCKLY R 69.0 245626 05N END 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 247145 CKT 1 / 245607 05BUCKLY R 69.0 247145 05W.ALLENDSS69.0 1 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T451 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245640 | 05W END | 247811 | 05LUMBERJ SS |  |  | 1 | 69 | 205 | 40 |  | 107.75 | N-1-1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | AEP_P1-3_#14673_05BUCKLR 138_1 | OPEN BRANCH FROM BUS 242974 TO BUS 245607 CKT 1 / 242974 05BUCKLR 138 245607 05BUCKLY R 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 245626 CKT 1 / 245607 05BUCKLY R 69.0 245626 05N END 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 247145 CKT 1 / 245607 05BUCKLY R 69.0 247145 05W.ALLENDSS69.0 1 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T452 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 132.94 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T453 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 130.26 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T454 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245640 | 05W END | 247811 | 05LUMBERJ SS |  |  | 1 | 69 | 205 | 40 |  | 111.02 | N-1-1 | AEP_P1-3_#5063_05SBERWI 345_1 | OPEN BRANCH FROM BUS 242917 TO BUS 242942 CKT 1 / 242917 05SBERW EQ 999 242942 05SBERWI 345 1 OPEN BRANCH FROM BUS 242917 TO BUS 243180 CKT 1 / 242917 05SBERW EQ 999 243180 05SBERWICK 69.0 1 OPEN BRANCH FROM BUS 242917 TO BUS 243199 CKT 1 / 242917 05SBERW EQ 999 243199 05SBERW1-L 12.0 1 OPEN BRANCH FROM BUS 238745 TO BUS 242942 CKT 1 / 238745 02GALION 345 242942 05SBERWI 345 1 OPEN BRANCH FROM BUS 242936 TO BUS 242942 CKT 1 / 242936 05FOSTOR 345 242942 05SBERWI 345 1 | AEP_P1-3_#14673_05BUCKLR 138_1 | OPEN BRANCH FROM BUS 242974 TO BUS 245607 CKT 1 / 242974 05BUCKLR 138 245607 05BUCKLY R 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 245626 CKT 1 / 245607 05BUCKLY R 69.0 245626 05N END 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 247145 CKT 1 / 245607 05BUCKLY R 69.0 247145 05W.ALLENDSS69.0 1 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T455 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245640 | 05W END | 247811 | 05LUMBERJ SS |  |  | 1 | 69 | 205 | 40 |  | 110.99 | N-1-1 | AEP_P1-3_#14673_05BUCKLR 138_1 | OPEN BRANCH FROM BUS 242974 TO BUS 245607 CKT 1 / 242974 05BUCKLR 138 245607 05BUCKLY R 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 245626 CKT 1 / 245607 05BUCKLY R 69.0 245626 05N END 69.0 1 OPEN BRANCH FROM BUS 245607 TO BUS 247145 CKT 1 / 245607 05BUCKLY R 69.0 247145 05W.ALLENDSS69.0 1 | AEP_P1-3_#5063_05SBERWI 345_1 | OPEN BRANCH FROM BUS 242917 TO BUS 242942 CKT 1 / 242917 05SBERW EQ 999 242942 05SBERWI 345 1 OPEN BRANCH FROM BUS 242917 TO BUS 243180 CKT 1 / 242917 05SBERW EQ 999 243180 05SBERWICK 69.0 1 OPEN BRANCH FROM BUS 242917 TO BUS 243199 CKT 1 / 242917 05SBERW EQ 999 243199 05SBERW1-L 12.0 1 OPEN BRANCH FROM BUS 238745 TO BUS 242942 CKT 1 / 238745 02GALION 345 242942 05SBERWI 345 1 OPEN BRANCH FROM BUS 242936 TO BUS 242942 CKT 1 / 242936 05FOSTOR 345 242942 05SBERWI 345 1 | 40/40/56/56 | No | Part 4: Thermal Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T456 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 244718 | 05JOHNSON LN |  |  | 1 | 35 | 205 | 51 |  | 107.3 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T457 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 244718 | 05JOHNSON LN |  |  | 1 | 35 | 205 | 51 |  | 107.2 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | 54/54/76/76 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T458 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 130.26 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T459 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 129.52 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T460 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246416 | 05TWIN BRCH1 | 246418 | 05TWIN BRCH2 |  |  | 1 | 35 | 205 | 47 |  | 129.52 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | 37/37/47/47 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Associated with AEP-2020-IM020 and AEP-2019-IM044
AEP-T461 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 45 |  | 234.33 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T462 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 45 |  | 234.32 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T463 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 57 |  | 180.91 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T464 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 124.79 | N-1-1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T465 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 246375 | 0512TH ST |  |  | 1 | 35 | 205 | 57 |  | 180.91 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | 56/56/70/70 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T466 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 124.79 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-2_#11506_934 | OPEN BRANCH FROM BUS 245547 TO BUS 247787 CKT 1 / 245547 05BLACKJRD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 247787 TO BUS 247788 CKT 1 / 247787 05COMMERCE 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 247201 TO BUS 247787 CKT 1 / 247201 05SHARP RD 69.0 247787 05COMMERCE 69.0 1 OPEN BRANCH FROM BUS 245564 TO BUS 247788 CKT 1 / 245564 05KELSEYHS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 247788 CKT 1 / 245550 05MARTINSS 69.0 247788 05KOKOSINGSS69.0 1 OPEN BRANCH FROM BUS 245550 TO BUS 245553 CKT 1 / 245550 05MARTINSS 69.0 245553 05MT VERNO 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T467 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 116.92 | N-1-1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T468 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245695 | 05FOREST | 245715 | 05U SANDSK |  |  | 1 | 69 | 205 | 69 |  | 120.5 | N-1-1 | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | 100/100/126/126 | No | Part 4: Thermal Limits | Substation equipment exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-T469 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243153 | 05WMTVER | 245562 | 05W MT VER |  |  | 1 | 138/69 | 205 | 46 |  | 116.92 | N-1-1 | AEP_P1-3_#14372_05ACADEM 138_1 | OPEN BRANCH FROM BUS 242950 TO BUS 245537 CKT 1 / 242950 05ACADEM 138 245537 05ACADEMIA 69.0 1 | AEP_P1-3_#11594_05SHARPR 138_1 | OPEN BRANCH FROM BUS 243098 TO BUS 247201 CKT 1 / 243098 05SHARPR 138 247201 05SHARP RD 69.0 1 | 39/46/45/51 | Yes | Part 4: Thermal Limits |  | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Voltage Magnitude
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Contingency 1 description | Cont 2 Name | Contingency 2 description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment | M3 Process Status
AEP-VM1 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9705 | 0.8881 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM2 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9708 | 0.8885 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM3 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9713 | 0.8885 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM4 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9791 | 0.8881 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM5 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9793 | 0.8885 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM6 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9803 | 0.8885 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM7 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9712 | 0.8904 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM8 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9788 | 0.8904 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM9 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9704 | 0.8863 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM10 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9811 | 0.8863 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM11 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9719 | 0.887 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM12 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9718 | 0.8986 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM13 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.972 | 0.8989 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM14 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9726 | 0.899 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM15 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9839 | 0.887 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM16 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9791 | 0.8986 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM17 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9793 | 0.8989 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM18 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9803 | 0.899 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM19 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9725 | 0.9006 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM20 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9788 | 0.9006 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM21 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9718 | 0.8972 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM22 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9749 | 0.8898 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM23 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9811 | 0.8972 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM24 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9878 | 0.8898 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM25 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243181 | 05SCIOTOVI | 69 | 205 | 0.9744 | 0.9071 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b2604 (delayed by siting) | AEP-2018-OH030 = Need
AEP-VM26 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243181 | 05SCIOTOVI | 69 | 205 | 0.9792 | 0.9071 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b2604 (delayed by siting) | AEP-2018-OH030 = Need
AEP-VM27 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9733 | 0.8982 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM28 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9839 | 0.8982 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM29 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9763 | 0.9011 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM30 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243181 | 05SCIOTOVI | 69 | 205 | 0.9754 | 0.9155 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b2604 (delayed by siting) | AEP-2018-OH030 = Need
AEP-VM31 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243181 | 05SCIOTOVI | 69 | 205 | 0.9792 | 0.9155 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b2604 (delayed by siting) | AEP-2018-OH030 = Need
AEP-VM32 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9878 | 0.9011 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM33 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9808 | 0.9146 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM34 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9812 | 0.9146 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM35 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.981 | 0.9149 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM36 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.978 | 0.9097 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM37 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9814 | 0.9167 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM38 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.993 | 0.9146 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM39 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9938 | 0.9146 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM40 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9931 | 0.9149 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM41 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9928 | 0.9167 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM42 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9921 | 0.9097 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM43 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243826 | 05ORTELCRN | 69 | 205 | 0.9823 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2158 | S2158 = Submitted for inclusion in Local Plan, AEP-2020-OH032 = Need
AEP-VM44 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243826 | 05ORTELCRN | 69 | 205 | 0.9921 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2158 | S2158 = Submitted for inclusion in Local Plan, AEP-2020-OH032 = Need
AEP-VM45 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9794 | 0.9095 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM46 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9778 | 0.9084 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM47 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9953 | 0.9095 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VM48 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9929 | 0.9084 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM49 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 0.9796 | 0.891 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VM50 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 1.004 | 0.891 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VM51 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 0.9856 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VM52 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 1.0091 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VM53 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243173 | 05MILLBRK | 69 | 205 | 0.9728 | 0.8953 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM54 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243173 | 05MILLBRK | 69 | 205 | 0.9782 | 0.8953 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM55 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243173 | 05MILLBRK | 69 | 205 | 0.974 | 0.9049 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM56 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243173 | 05MILLBRK | 69 | 205 | 0.9782 | 0.9049 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM57 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0568 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#1383 | OPEN BRANCH FROM BUS 242521 TO BUS 242532 CKT 5 / 242521 05NAGEL 500 242532 05NAGEL 230 5 OPEN BRANCH FROM BUS 242532 TO BUS 304781 CKT 1 / 242532 05NAGEL 230 304781 6CANERV230 T 230 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM58 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0569 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#1383 | OPEN BRANCH FROM BUS 242521 TO BUS 242532 CKT 5 / 242521 05NAGEL 500 242532 05NAGEL 230 5 OPEN BRANCH FROM BUS 242532 TO BUS 304781 CKT 1 / 242532 05NAGEL 230 304781 6CANERV230 T 230 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM59 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0574 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#350 | OPEN BRANCH FROM BUS 242521 TO BUS 360102 CKT 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM60 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0574 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#350 | OPEN BRANCH FROM BUS 242521 TO BUS 360102 CKT 1 / 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM61 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0583 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-1_#6479_05VACITY 23.0_1 | OPEN BRANCH FROM BUS 246894 TO BUS 246895 CKT 1 / 246894 05VACITY 138 246895 05VACITY 23.0 1 REMOVE UNIT 1 FROM BUS 246895 / 246895 05VACITY 23.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM62 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0584 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-1_#6479_05VACITY 23.0_1 | OPEN BRANCH FROM BUS 246894 TO BUS 246895 CKT 1 / 246894 05VACITY 138 246895 05VACITY 23.0 1 REMOVE UNIT 1 FROM BUS 246895 / 246895 05VACITY 23.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM63 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0586 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-4_05W.KINGSPT1138.00 | REMOVE SWSHUNT FROM BUS 242849 /05W.KINGSPT1138.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM64 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0586 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-4_05REEDCR 138.00 | REMOVE SWSHUNT FROM BUS 242762 /05REEDCR 138.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM65 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0586 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-4_05W.KINGSPT1138.00 | REMOVE SWSHUNT FROM BUS 242849 /05W.KINGSPT1138.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM66 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0586 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-4_05REEDCR 138.00 | REMOVE SWSHUNT FROM BUS 242762 /05REEDCR 138.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM67 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12035_05GARDEC 138_1 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM68 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5294_97 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM69 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#6173_98 | OPEN BRANCH FROM BUS 242605 TO BUS 242700 CKT 1 / 242605 05CLNCHR 138 242700 05LEBANO 138 1 OPEN BRANCH FROM BUS 242635 TO BUS 246766 CKT 1 / 242635 05ELKGAR 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242700 TO BUS 246766 CKT 1 / 242700 05LEBANO 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 246766 CKT 1 / 242788 05SALTV1 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242700 TO BUS 244243 CKT 1 / 242700 05LEBANO 138 244243 05LEBANON 12.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM70 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#8034_5443 | OPEN BRANCH FROM BUS 242677 TO BUS 245220 CKT 1 / 242677 05INDDRV 138 245220 05W.KINGSPT2 138 1 REMOVE UNIT 1 FROM BUS 242677 / 242677 05INDDRV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM71 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12035_05GARDEC 138_1 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM72 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5294_97 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM73 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#6173_98 | OPEN BRANCH FROM BUS 242605 TO BUS 242700 CKT 1 / 242605 05CLNCHR 138 242700 05LEBANO 138 1 OPEN BRANCH FROM BUS 242635 TO BUS 246766 CKT 1 / 242635 05ELKGAR 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242700 TO BUS 246766 CKT 1 / 242700 05LEBANO 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 246766 CKT 1 / 242788 05SALTV1 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242700 TO BUS 244243 CKT 1 / 242700 05LEBANO 138 244243 05LEBANON 12.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM74 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.0588 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#8034_5443 | OPEN BRANCH FROM BUS 242677 TO BUS 245220 CKT 1 / 242677 05INDDRV 138 245220 05W.KINGSPT2 138 1 REMOVE UNIT 1 FROM BUS 242677 / 242677 05INDDRV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM75 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9557 | 1.0589 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#351 | OPEN BRANCH FROM BUS 242521 TO BUS 360106 CKT 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM76 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9558 | 1.059 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#351 | OPEN BRANCH FROM BUS 242521 TO BUS 360106 CKT 1 / 242521 05NAGEL 500 360106 8SULLIVAN TN 500 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM77 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.0704 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#1383 | OPEN BRANCH FROM BUS 242521 TO BUS 242532 CKT 5 / 242521 05NAGEL 500 242532 05NAGEL 230 5 OPEN BRANCH FROM BUS 242532 TO BUS 304781 CKT 1 / 242532 05NAGEL 230 304781 6CANERV230 T 230 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM78 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.0704 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#1383 | OPEN BRANCH FROM BUS 242521 TO BUS 242532 CKT 5 / 242521 05NAGEL 500 242532 05NAGEL 230 5 OPEN BRANCH FROM BUS 242532 TO BUS 304781 CKT 1 / 242532 05NAGEL 230 304781 6CANERV230 T 230 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM79 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.0716 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12035_05GARDEC 138_1 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM80 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.0716 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12035_05GARDEC 138_1 | OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM81 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM82 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM83 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5704 | OPEN BRANCH FROM BUS 242849 TO BUS 244218 CKT 1 / 242849 05W.KINGSPT1 138 244218 05WKINGSEQ 999 1 OPEN BRANCH FROM BUS 244218 TO BUS 244220 CKT 1 / 244218 05WKINGSEQ 999 244220 05WKINGSP 69.0 1 OPEN BRANCH FROM BUS 244218 TO BUS 244219 CKT 1 / 244218 05WKINGSEQ 999 244219 05WKINGSP 34.5 1 OPEN BRANCH FROM BUS 242633 TO BUS 242678 CKT 1 / 242633 05EDENSR 138 242678 05INDIAS 138 1 OPEN BRANCH FROM BUS 242633 TO BUS 242849 CKT 1 / 242633 05EDENSR 138 242849 05W.KINGSPT1 138 1 OPEN BRANCH FROM BUS 242849 TO BUS 244195 CKT Z1 / 242849 05W.KINGSPT1 138 244195 05HOLSTN ARM 138 Z1 OPEN BRANCH FROM BUS 242678 TO BUS 242732 CKT 1 / 242678 05INDIAS 138 242732 05NBRSTL 138 1 REMOVE SWSHUNT FROM BUS 242849 / 242849 05W.KINGSPT1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM84 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM85 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM86 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.073 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5704 | OPEN BRANCH FROM BUS 242849 TO BUS 244218 CKT 1 / 242849 05W.KINGSPT1 138 244218 05WKINGSEQ 999 1 OPEN BRANCH FROM BUS 244218 TO BUS 244220 CKT 1 / 244218 05WKINGSEQ 999 244220 05WKINGSP 69.0 1 OPEN BRANCH FROM BUS 244218 TO BUS 244219 CKT 1 / 244218 05WKINGSEQ 999 244219 05WKINGSP 34.5 1 OPEN BRANCH FROM BUS 242633 TO BUS 242678 CKT 1 / 242633 05EDENSR 138 242678 05INDIAS 138 1 OPEN BRANCH FROM BUS 242633 TO BUS 242849 CKT 1 / 242633 05EDENSR 138 242849 05W.KINGSPT1 138 1 OPEN BRANCH FROM BUS 242849 TO BUS 244195 CKT Z1 / 242849 05W.KINGSPT1 138 244195 05HOLSTN ARM 138 Z1 OPEN BRANCH FROM BUS 242678 TO BUS 242732 CKT 1 / 242678 05INDIAS 138 242732 05NBRSTL 138 1 REMOVE SWSHUNT FROM BUS 242849 / 242849 05W.KINGSPT1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM87 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244508 | 05RIGGS | 138 | 205 | 0.9676 | 1.0731 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5686_171 | OPEN BRANCH FROM BUS 242729 TO BUS 245220 CKT 1 / 242729 05NAGEL 138 245220 05W.KINGSPT2 138 1 REMOVE LOAD D7 FROM BUS 242729 / 242729 05NAGEL 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM88 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242819 | 05SULVN | 138 | 205 | 0.9677 | 1.0731 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12034_05HOLST2 138_1 | OPEN BRANCH FROM BUS 242670 TO BUS 244193 CKT 1 / 242670 05HOLST2 138 244193 05HLSTN1EQ 999 1 OPEN BRANCH FROM BUS 244193 TO BUS 244222 CKT 1 / 244193 05HLSTN1EQ 999 244222 05HOLSTON2 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242670 TO BUS 242722 CKT 1 / 242670 05HOLST2 138 242722 05MORLAN 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 244508 CKT 1 / 242670 05HOLST2 138 244508 05RIGGS 138 1 OPEN BRANCH FROM BUS 242670 TO BUS 242830 CKT 2 / 242670 05HOLST2 138 242830 05TENNE2 138 2 REMOVE SWSHUNT FROM BUS 242670 / 242670 05HOLST2 138 | AEP_P1-2_#5686_171 | OPEN BRANCH FROM BUS 242729 TO BUS 245220 CKT 1 / 242729 05NAGEL 138 245220 05W.KINGSPT2 138 1 REMOVE LOAD D7 FROM BUS 242729 / 242729 05NAGEL 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2249 | Submitted for inclusion in Local Plan
AEP-VM89 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9161 | 0.916 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM90 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9916 | 0.9108 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM91 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9907 | 0.9107 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM92 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9929 | 0.9145 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM93 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9917 | 0.9145 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM94 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9929 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM95 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9906 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM96 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.8713 | 0.8712 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM97 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9945 | 0.8687 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM98 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.993 | 0.8687 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM99 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9945 | 0.8731 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM100 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9916 | 0.8731 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM101 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.8641 | 0.8638 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM102 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.8515 | 0.8513 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM103 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9949 | 0.8423 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM104 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9959 | 0.8425 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM105 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9949 | 0.8423 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM106 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9959 | 0.865 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM107 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9959 | 0.865 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM108 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9949 | 0.8649 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM109 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9949 | 0.8649 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM110 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9982 | 0.8506 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM111 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9982 | 0.8506 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM112 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9964 | 0.8506 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM113 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9964 | 0.8506 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM114 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9982 | 0.8533 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM115 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9982 | 0.8533 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM116 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9943 | 0.8533 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM117 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9943 | 0.8533 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM118 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.8641 | 0.8639 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM119 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.8515 | 0.8513 | 1.05/0.92 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM120 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9959 | 0.8425 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VM121 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.929 | 0.8752 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM122 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.929 | 0.8752 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM123 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8751 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM124 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8751 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM125 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.929 | 0.8752 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM126 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8751 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM127 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9427 | 0.8909 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM128 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9427 | 0.8909 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM129 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8908 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM130 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8908 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM131 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9427 | 0.8909 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM132 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8908 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VM133 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 0.9764 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM134 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 1.0109 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM135 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 1.0109 | 0.9179 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM136 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 0.9775 | 0.9179 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM137 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245732 | 05COLGRVE8 | 69 | 205 | 0.9054 | 0.9051 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM138 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244735 | 05GLANDORF | 69 | 205 | 0.9043 | 0.9044 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM139 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245801 | 05PHILIPS2 | 69 | 205 | 0.8914 | 0.8914 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM140 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 69 | 205 | 0.8898 | 0.8898 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM141 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.7914 | 0.7913 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM142 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.7841 | 0.7841 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM143 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.7817 | 0.7816 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM144 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.7807 | 0.7807 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM145 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9069 | 0.9062 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM146 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.908 | 0.9073 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM147 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9091 | 0.9084 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM148 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9125 | 0.9118 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM149 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.8784 | 0.8786 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM150 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245757 | 05MCCOMB OP | 34.5 | 205 | 0.9161 | 0.9164 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM151 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245889 | 05MILLER8 | 69 | 205 | 0.9136 | 0.9138 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM152 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.9124 | 0.9119 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM153 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245735 | 05CRAWFIS | 69 | 205 | 0.9087 | 0.9088 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM154 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9845 | 0.8022 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM155 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9858 | 0.8032 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM156 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9857 | 0.8053 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM157 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9853 | 0.8116 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM158 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9909 | 0.826 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM159 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9921 | 0.8271 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM160 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9919 | 0.8289 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM161 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9913 | 0.8341 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM162 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9839 | 0.7221 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM163 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9851 | 0.7229 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM164 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9852 | 0.7253 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM165 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9857 | 0.7323 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM166 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245730 | 05CAIRO | 69 | 205 | 0.9863 | 0.8147 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM167 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.989 | 0.818 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM168 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245732 | 05COLGRVE8 | 69 | 205 | 0.9905 | 0.8199 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM169 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245801 | 05PHILIPS2 | 69 | 205 | 0.9941 | 0.8243 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM170 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 69 | 205 | 0.996 | 0.8267 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM171 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.978 | 0.8495 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM172 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9806 | 0.7197 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM173 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9818 | 0.7205 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM174 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9817 | 0.7229 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM175 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9813 | 0.7299 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM176 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245730 | 05CAIRO | 69 | 205 | 0.991 | 0.8125 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM177 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.9834 | 0.8159 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM178 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245732 | 05COLGRVE8 | 69 | 205 | 0.9834 | 0.8177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM179 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245801 | 05PHILIPS2 | 69 | 205 | 0.9834 | 0.8222 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM180 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 69 | 205 | 0.9845 | 0.8246 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM181 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.9781 | 0.8476 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM182 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244735 | 05GLANDORF | 69 | 205 | 0.9876 | 0.8444 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM183 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.719 | 0.719 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM184 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.7175 | 0.7175 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM185 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.7172 | 0.7172 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM186 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.7172 | 0.7172 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM187 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.8569 | 0.8561 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM188 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.8569 | 0.8561 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM189 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.8572 | 0.8564 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM190 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.8587 | 0.858 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM191 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.9181 | 0.9192 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM192 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9181 | 0.9192 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM193 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9183 | 0.9195 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM194 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9649 | 0.7458 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM195 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.965 | 0.746 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM196 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9662 | 0.7473 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM197 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9732 | 0.777 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM198 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9741 | 0.7781 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM199 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242957 | 05BASEL8 | 138 | 205 | 0.9555 | 0.659 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM200 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.9565 | 0.6601 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM201 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9565 | 0.6601 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM202 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9569 | 0.6604 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM203 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9583 | 0.6619 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM204 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9766 | 0.9012 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM205 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9763 | 0.9013 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM206 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9768 | 0.9025 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM207 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9768 | 0.9026 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM208 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.985 | 0.9012 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM209 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9851 | 0.9014 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM210 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9862 | 0.9026 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM211 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9863 | 0.9026 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM212 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9635 | 0.7457 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM213 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.963 | 0.7459 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM214 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9631 | 0.7472 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM215 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9631 | 0.7472 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM216 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.963 | 0.777 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM217 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9631 | 0.7781 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM218 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9631 | 0.7781 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM219 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.7191 | 0.719 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM220 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.8588 | 0.858 | 1.05/0.92 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM221 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9662 | 0.7473 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM222 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9741 | 0.7781 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM223 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243121 | 05ROCKPO | 138 | 205 | 0.9554 | 0.6589 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM224 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9584 | 0.6619 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VM225 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0205 | 0.9047 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM226 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0121 | 0.9049 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM227 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.0159 | 0.7163 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM228 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.029 | 0.7151 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM229 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.0068 | 0.758 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM230 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242798 | 05SHORT | 138 | 205 | 1.0101 | 0.7593 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM231 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.0008 | 0.7581 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM232 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242798 | 05SHORT | 138 | 205 | 1.0019 | 0.7595 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VM233 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9847 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VM234 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9941 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VM235 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.6852 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM236 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.6852 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM237 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9723 | 0.686 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM238 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9723 | 0.686 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM239 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9671 | 0.8085 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM240 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9671 | 0.8084 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM241 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9796 | 0.8089 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM242 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9796 | 0.8089 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM243 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9681 | 0.8494 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM244 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9681 | 0.8493 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM245 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.978 | 0.8497 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM246 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.978 | 0.8497 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM247 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.97 | 0.8516 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM248 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.97 | 0.8516 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM249 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246906 | 05WOODLND8 | 69 | 205 | 1.0189 | 0.8391 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM250 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246906 | 05WOODLND8 | 69 | 205 | 1.0136 | 0.839 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM251 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9799 | 0.8519 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM252 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9799 | 0.8519 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM253 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9727 | 0.8547 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM254 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9727 | 0.8546 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM255 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246904 | 05PERRY8 | 69 | 205 | 1.0214 | 0.8421 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM256 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246904 | 05PERRY8 | 69 | 205 | 1.0085 | 0.842 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM257 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9826 | 0.855 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM258 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9826 | 0.855 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM259 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246903 | 05DIEBOLD | 69 | 205 | 1.0104 | 0.8443 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM260 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246903 | 05DIEBOLD | 69 | 205 | 1.0233 | 0.8444 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM261 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9757 | 0.8608 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM262 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.8608 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM263 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.8845 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM264 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.8845 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM265 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9811 | 0.8849 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM266 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9811 | 0.8849 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM267 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246198 | 05HARLAN | 69 | 205 | 1.0137 | 0.8899 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM268 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246198 | 05HARLAN | 69 | 205 | 1.0034 | 0.8899 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM269 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9875 | 0.9061 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM270 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9875 | 0.9061 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM271 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9813 | 0.9099 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM272 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.983 | 0.9099 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM273 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9765 | 0.9122 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM274 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9764 | 0.9122 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM275 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9776 | 0.9125 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM276 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9776 | 0.9125 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM277 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.979 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM278 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9791 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM279 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.979 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM280 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9791 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM281 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9795 | 0.9137 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM282 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9795 | 0.9137 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM283 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9795 | 0.9137 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM284 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9795 | 0.9138 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM285 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9801 | 0.915 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM286 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9935 | 0.916 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM287 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9935 | 0.916 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM288 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9658 | 0.915 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM289 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9822 | 0.9162 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM290 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9822 | 0.9162 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM291 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9791 | 0.9172 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM292 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9791 | 0.9172 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM293 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9814 | 0.9174 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM294 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9814 | 0.9174 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM295 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 1.0008 | 0.7472 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM296 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9841 | 0.7455 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM297 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9987 | 0.7516 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM298 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.988 | 0.75 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM299 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 1.0009 | 0.7582 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM300 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 1.0009 | 0.7582 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM301 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9938 | 0.7566 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM302 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9939 | 0.7566 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM303 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 1.0063 | 0.7651 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM304 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9998 | 0.7635 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM305 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0016 | 0.7959 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM306 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0017 | 0.7959 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM307 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0123 | 0.7956 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM308 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0123 | 0.7957 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM309 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0135 | 0.8224 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM310 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0048 | 0.8213 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM311 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9982 | 0.8746 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM312 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0036 | 0.8744 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM313 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0036 | 0.8744 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM314 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9983 | 0.8746 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM315 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0041 | 0.8934 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM316 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9997 | 0.8928 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM317 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.99 | 0.8964 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM318 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9941 | 0.8963 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM319 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.99 | 0.8964 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM320 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9941 | 0.8963 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM321 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9925 | 0.8992 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM322 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9966 | 0.899 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM323 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9925 | 0.8992 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM324 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9966 | 0.8991 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM325 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9945 | 0.9014 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM326 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9945 | 0.9014 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM327 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9986 | 0.9012 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM328 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9986 | 0.9013 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM329 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9946 | 0.9114 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM330 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9911 | 0.9109 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM331 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9971 | 0.9141 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM332 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9936 | 0.9137 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM333 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9991 | 0.9163 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM334 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9956 | 0.9158 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM335 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.8999 | 0.8994 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM336 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.902 | 0.9014 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM337 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9048 | 0.9043 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM338 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9187 | 0.9184 | 1.05/0.92 | FB | AEP_P4_#10542_05COLUMBIA 138_D | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM339 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.9058 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM340 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.9058 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM341 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9178 | 0.9173 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM342 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9814 | 0.56 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM343 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9776 | 0.5645 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM344 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9795 | 0.5711 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM345 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9795 | 0.5711 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM346 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9822 | 0.5746 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM347 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9861 | 0.578 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM348 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9811 | 0.7002 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM349 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9842 | 0.8203 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM350 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9814 | 0.859 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM351 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9833 | 0.8611 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM352 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9859 | 0.8641 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM353 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.9186 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM354 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9896 | 0.6271 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM355 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9864 | 0.632 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM356 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9886 | 0.6392 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM357 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9886 | 0.6393 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM358 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9953 | 0.6469 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM359 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9875 | 0.7389 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM360 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9882 | 0.8425 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM361 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9846 | 0.8754 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM362 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9864 | 0.8775 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM363 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9891 | 0.8805 | 1.05/0.92 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM364 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.9186 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM365 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9658 | 0.5601 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM366 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9711 | 0.5646 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM367 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9788 | 0.5712 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM368 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9789 | 0.5712 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM369 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9934 | 0.5747 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM370 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9868 | 0.5781 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM371 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9658 | 0.6224 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM372 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9711 | 0.6273 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM373 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9788 | 0.6345 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM374 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9789 | 0.6345 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM375 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9868 | 0.6421 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM376 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.7005 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM377 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.7345 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM378 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.983 | 0.8204 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM379 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.983 | 0.8391 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM380 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9803 | 0.8591 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM381 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9822 | 0.8612 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM382 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9848 | 0.8642 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM383 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9803 | 0.8726 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM384 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9822 | 0.8747 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM385 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9848 | 0.8777 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM386 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM387 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM388 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9953 | 0.6779 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM389 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9928 | 0.682 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM390 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9947 | 0.6882 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM391 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9948 | 0.6882 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM392 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9972 | 0.6914 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM393 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 1.0001 | 0.6946 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM394 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0095 | 0.7801 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM395 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0014 | 0.8692 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM396 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9925 | 0.8936 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM397 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.995 | 0.8964 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM398 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.997 | 0.8986 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM399 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9841 | 0.6779 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM400 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.988 | 0.682 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM401 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9938 | 0.6881 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM402 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9939 | 0.6881 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM403 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 1.0001 | 0.6913 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM404 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9998 | 0.6945 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM405 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0048 | 0.7801 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM406 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9997 | 0.8692 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM407 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9911 | 0.8936 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM408 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9936 | 0.8964 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM409 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9956 | 0.8986 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM410 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243372 | 05SATURN | 138 | 205 | 0.9807 | 0.8093 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM411 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243372 | 05SATURN | 138 | 205 | 1.0062 | 0.8093 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM412 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243361 | 05RABER | 138 | 205 | 0.981 | 0.8097 | 1.05/0.92 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM413 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243361 | 05RABER | 138 | 205 | 1.0047 | 0.8096 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VM414 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0184 | 0.9012 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM415 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0185 | 0.9017 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM416 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.021 | 0.9061 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM417 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0211 | 0.9067 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM418 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0234 | 0.9105 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM419 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0235 | 0.9111 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM420 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0531 | 1.0531 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246463 05LAKE ST 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246463 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM421 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0509 | 1.0509 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246476 05NILES 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246476 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM422 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0505 | 1.0505 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246476 05NILES 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246476 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM423 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0645 | 1.0643 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246463 05LAKE ST 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246463 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM424 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0626 | 1.0625 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246476 05NILES 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246476 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM425 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0624 | 1.0622 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246476 05NILES 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246476 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM426 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.059 | 1.0587 | 1.05/0.92 | FB | AEP_P4_#12430_05POKAGON 69.0_F | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246516 CKT 1 / 244216 05HOSP TAPSS69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246546 CKT 1 / 244216 05HOSP TAPSS69.0 246546 05STONELAK 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246555 CKT 1 / 244216 05HOSP TAPSS69.0 246555 05WOLVERIN 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM427 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.059 | 1.0587 | 1.05/0.92 | Single | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM428 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.059 | 1.0587 | 1.05/0.92 | Bus | AEP_P2-2_#12429_05POKAGON 69.0_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM429 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.059 | 1.0587 | 1.05/0.92 | FB | AEP_P4_#12429_05POKAGON 69.0_J | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM430 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.059 | 1.0587 | 1.05/0.92 | FB | AEP_P4_#12431_05POKAGON 69.0_H | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246505 TO BUS 246506 CKT 1 / 246505 05BARRETT8 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246506 TO BUS 246511 CKT 1 / 246506 05BARRETTZ 69.0 246511 05COLBY 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 243420 TO BUS 246511 CKT 1 / 243420 05COLBY 34.5 246511 05COLBY 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM431 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0575 | 1.0572 | 1.05/0.92 | FB | AEP_P4_#12430_05POKAGON 69.0_F | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246516 CKT 1 / 244216 05HOSP TAPSS69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246546 CKT 1 / 244216 05HOSP TAPSS69.0 246546 05STONELAK 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246555 CKT 1 / 244216 05HOSP TAPSS69.0 246555 05WOLVERIN 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM432 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0575 | 1.0572 | 1.05/0.92 | Single | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM433 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0575 | 1.0572 | 1.05/0.92 | Bus | AEP_P2-2_#12429_05POKAGON 69.0_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM434 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0575 | 1.0572 | 1.05/0.92 | FB | AEP_P4_#12429_05POKAGON 69.0_J | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM435 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0575 | 1.0572 | 1.05/0.92 | FB | AEP_P4_#12431_05POKAGON 69.0_H | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246505 TO BUS 246506 CKT 1 / 246505 05BARRETT8 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246506 TO BUS 246511 CKT 1 / 246506 05BARRETTZ 69.0 246511 05COLBY 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 243420 TO BUS 246511 CKT 1 / 243420 05COLBY 34.5 246511 05COLBY 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM436 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | FB | AEP_P4_#12430_05POKAGON 69.0_F | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246516 CKT 1 / 244216 05HOSP TAPSS69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246546 CKT 1 / 244216 05HOSP TAPSS69.0 246546 05STONELAK 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246555 CKT 1 / 244216 05HOSP TAPSS69.0 246555 05WOLVERIN 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM437 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | Single | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM438 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | Bus | AEP_P2-2_#12429_05POKAGON 69.0_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM439 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | FB | AEP_P4_#12429_05POKAGON 69.0_J | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM440 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | FB | AEP_P4_#12431_05POKAGON 69.0_H | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246505 TO BUS 246506 CKT 1 / 246505 05BARRETT8 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246506 TO BUS 246511 CKT 1 / 246506 05BARRETTZ 69.0 246511 05COLBY 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 243420 TO BUS 246511 CKT 1 / 243420 05COLBY 34.5 246511 05COLBY 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM441 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0527 | 1.0525 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246428 05NILECTY 34.5 246476 05NILES 34.5 1 | OPEN BRANCH FROM BUS 246428 TO BUS 246476 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM442 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0516 | 1.0514 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246428 05NILECTY 34.5 246476 05NILES 34.5 1 | OPEN BRANCH FROM BUS 246428 TO BUS 246476 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM443 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.052 | 1.0518 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246463 05LAKE ST 34.5 246487 05SIMPLCTZ 34.5 1 | OPEN BRANCH FROM BUS 246463 TO BUS 246487 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM444 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0008 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM445 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0007 | 0.9173 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM446 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0188 | 0.9017 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM447 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0189 | 0.9022 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM448 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0562 | 1.0559 | 1.05/0.92 | Single | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM449 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0561 | 1.0558 | 1.05/0.92 | Bus | AEP_P2-2_#12429_05POKAGON 69.0_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM450 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0561 | 1.0558 | 1.05/0.92 | FB | AEP_P4_#12429_05POKAGON 69.0_J | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM451 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0562 | 1.0559 | 1.05/0.92 | FB | AEP_P4_#12431_05POKAGON 69.0_H | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246505 TO BUS 246506 CKT 1 / 246505 05BARRETT8 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246506 TO BUS 246511 CKT 1 / 246506 05BARRETTZ 69.0 246511 05COLBY 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 243420 TO BUS 246511 CKT 1 / 243420 05COLBY 34.5 246511 05COLBY 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM452 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0562 | 1.0559 | 1.05/0.92 | FB | AEP_P4_#12430_05POKAGON 69.0_F | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246506 CKT 1 / 246480 05POKAGON 69.0 246506 05BARRETTZ 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246516 CKT 1 / 244216 05HOSP TAPSS69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 246480 TO BUS 246516 CKT 1 / 246480 05POKAGON 69.0 246516 05DAILEY 8 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246546 CKT 1 / 244216 05HOSP TAPSS69.0 246546 05STONELAK 69.0 1 OPEN BRANCH FROM BUS 244216 TO BUS 246555 CKT 1 / 244216 05HOSP TAPSS69.0 246555 05WOLVERIN 69.0 1 OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 REMOVE SWSHUNT FROM BUS 246480 / 246480 05POKAGON 69.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM453 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0507 | 1.0505 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_246428 05NILECTY 34.5 246476 05NILES 34.5 1 | OPEN BRANCH FROM BUS 246428 TO BUS 246476 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VM454 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245344 | 05SAN CAST | 34.5 | 205 | 0.8639 | 0.8635 | 1.05/0.92 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM455 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245328 | 05JACKSON8 | 34.5 | 205 | 0.8755 | 0.875 | 1.05/0.92 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM456 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245349 | 05TUNNHIL8 | 34.5 | 205 | 0.876 | 0.8755 | 1.05/0.92 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM457 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245352 | 05WARSAW | 34.5 | 205 | 0.9044 | 0.9039 | 1.05/0.92 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM458 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0517 | 1.0508 | 1.05/0.92 | FB | AEP_P4_#9063_05WMILLS 138_E | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 OPEN BRANCH FROM BUS 245374 TO BUS 247028 CKT 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 OPEN BRANCH FROM BUS 245368 TO BUS 245374 CKT 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 REMOVE SWSHUNT FROM BUS 245374 / 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM459 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0515 | 1.0506 | 1.05/0.92 | FB | AEP_P4_#9063_05WMILLS 138_E | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 OPEN BRANCH FROM BUS 245374 TO BUS 247028 CKT 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 OPEN BRANCH FROM BUS 245368 TO BUS 245374 CKT 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 REMOVE SWSHUNT FROM BUS 245374 / 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM460 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0519 | 1.051 | 1.05/0.92 | Single | AEP_P1-2_#5260_12478 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM461 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0519 | 1.051 | 1.05/0.92 | Single | AEP_P1-3_#12212_05SMILLB 138 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM462 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0519 | 1.051 | 1.05/0.92 | FB | AEP_P4_#10073_05OHIOCT 138_B2 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM463 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0517 | 1.0508 | 1.05/0.92 | Single | AEP_P1-2_#5260_12478 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM464 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0517 | 1.0508 | 1.05/0.92 | Single | AEP_P1-3_#12212_05SMILLB 138 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM465 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0517 | 1.0508 | 1.05/0.92 | FB | AEP_P4_#10073_05OHIOCT 138_B2 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM466 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.051 | - | 1.05/0.92 | N-1-1 | AEP_P1-2_#5260_12478 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 | Base Case |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan | #REF!
AEP-VM467 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0508 | - | 1.05/0.92 | N-1-1 | AEP_P1-3_#12212_05SMILLB 138 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 | Base Case |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan | #REF!
AEP-VM468 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.051 | - | 1.05/0.92 | N-1-1 | AEP_P1-3_#12212_05SMILLB 138 | OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 247253 CKT 1 / 243105 05SMILLB 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243145 TO BUS 247253 CKT 1 / 243145 05WCOSHC 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 242973 TO BUS 245359 CKT Z1 / 242973 05BUCKH8 138 245359 05BUCKHN8L 12.0 Z1 | Base Case |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan | #REF!
AEP-VM469 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246580 | 05HYATT | 34.5 | 205 | 1.0549 | 1.0552 | 1.05/0.92 | Single | AEP_P1-3_#7222_05MALIS 765_1 | OPEN BRANCH FROM BUS 242926 TO BUS 242928 CKT 1 / 242926 05MALIS 765 242928 05MARYSV 765 1 OPEN BRANCH FROM BUS 242926 TO BUS 246751 CKT 1 / 242926 05MALIS 765 246751 05VASSEL 765 1 OPEN BRANCH FROM BUS 242926 TO BUS 243538 CKT 1 / 242926 05MALIS 765 243538 05MALISX 138 1 OPEN BRANCH FROM BUS 243537 TO BUS 243538 CKT SR / 243537 05MALIS 138 243538 05MALISX 138 SR OPEN BRANCH FROM BUS 243537 TO BUS 243538 CKT ZB / 243537 05MALIS 138 243538 05MALISX 138 ZB |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VM470 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243946 | 05BASSETT | 69 | 205 | 1.0744 | 1.0741 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM471 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243996 | 05STNLY TW | 69 | 205 | 1.0662 | 1.0659 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM472 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243965 | 05FIELDALE | 69 | 205 | 1.0636 | 1.0634 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM473 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243959 | 05DUPONT | 69 | 205 | 1.053 | 1.0528 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM474 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244007 | 05WOOLWINE | 69 | 205 | 0.879 | 0.878 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM475 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243946 | 05BASSETT | 69 | 205 | 1.1066 | 1.1036 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM476 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243996 | 05STNLY TW | 69 | 205 | 1.0988 | 1.0959 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM477 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243965 | 05FIELDALE | 69 | 205 | 1.0944 | 1.0918 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM478 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243959 | 05DUPONT | 69 | 205 | 1.0728 | 1.0713 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM479 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 1.0624 | 1.0603 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM480 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 244007 | 05WOOLWINE | 69 | 205 | 1.0544 | 1.0535 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM481 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243946 | 05BASSETT | 69 | 205 | 1.0664 | 1.0659 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM482 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243996 | 05STNLY TW | 69 | 205 | 1.0581 | 1.0577 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM483 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243965 | 05FIELDALE | 69 | 205 | 1.0556 | 1.0551 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM484 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0599 | - | 1.05/0.92 | Base Case | Base Case |  |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM485 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0573 | 1.0572 | 1.05/0.92 | FB | AEP_P4_#13270_05STUART 69.0_E | OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 243997 TO BUS 244007 CKT 1 / 243997 05STUART A 69.0 244007 05WOOLWINE 69.0 1 REMOVE SWSHUNT FROM BUS 243997 / 243997 05STUART A 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM486 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.057 | 1.0569 | 1.05/0.92 | Single | AEP_P1-2_#11293_293 | OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 243997 TO BUS 244007 CKT 1 / 243997 05STUART A 69.0 244007 05WOOLWINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM487 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0568 | 1.0567 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM488 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0568 | 1.0567 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 | OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM489 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.056 | 1.0557 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM490 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0504 | 1.0502 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 | OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM491 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0504 | 1.0502 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 | OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM492 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 0.8599 | 0.8586 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM493 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0502 | 1.0501 | 1.05/0.92 | FB | AEP_P4_#13201_05HICKMAN 69.0_K | OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244136 TO BUS 244140 CKT 1 / 244136 05MORGAN C 69.0 244140 05HICKMAN 69.0 1 OPEN BRANCH FROM BUS 244140 TO BUS 244146 CKT 1 / 244140 05HICKMAN 69.0 244146 05RADFRD A 69.0 1 OPEN BRANCH FROM BUS 244140 TO BUS 244148 CKT 1 / 244140 05HICKMAN 69.0 244148 05RIVERBEN 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 OPEN BRANCH FROM BUS 244133 TO BUS 244148 CKT 1 / 244133 05INGLES 69.0 244148 05RIVERBEN 69.0 1 OPEN BRANCH FROM BUS 244133 TO BUS 244156 CKT 1 / 244133 05INGLES 69.0 244156 05INGLSTSS 34.5 1 REMOVE SWSHUNT FROM BUS 244133 / 244133 05INGLES 69.0 REMOVE SWSHUNT FROM BUS 244148 / 244148 05RIVERBEN 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM494 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0504 | 1.0502 | 1.05/0.92 | Tower | AEP_P7-1_#10807 | OPEN BRANCH FROM BUS 242583 TO BUS 244034 CKT 1 / 242583 05CATAWB 138 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244033 TO BUS 244034 CKT 1 / 244033 05CATAWBA 69.0 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 244032 TO BUS 244034 CKT 1 / 244032 05CATAWBA 34.5 244034 05CATAWBEQ 999 1 OPEN BRANCH FROM BUS 242572 TO BUS 242584 CKT 1 / 242572 05BURLHT 138 242584 05CATAWZ 138 1 OPEN BRANCH FROM BUS 242572 TO BUS 242607 CKT 1 / 242572 05BURLHT 138 242607 05CLOVRD 138 1 OPEN BRANCH FROM BUS 242583 TO BUS 242607 CKT 1 / 242583 05CATAWB 138 242607 05CLOVRD 138 1 OPEN BRANCH FROM BUS 242584 TO BUS 242852 CKT 1 / 242584 05CATAWZ 138 242852 05WSALEM 138 1 OPEN BRANCH FROM BUS 242708 TO BUS 242852 CKT 1 / 242708 05M FUNK 138 242852 05WSALEM 138 1 OPEN BRANCH FROM BUS 244033 TO BUS 244037 CKT 1 / 244033 05CATAWBA 69.0 244037 05CLEVEL 69.0 1 OPEN BRANCH FROM BUS 244033 TO BUS 244062 CKT 1 / 244033 05CATAWBA 69.0 244062 05MASON CR 69.0 1 OPEN BRANCH FROM BUS 244032 TO BUS 244079 CKT 1 / 244032 05CATAWBA 34.5 244079 05VETHOSPZ 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM495 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0526 | 1.0522 | 1.05/0.92 | FB | AEP_P4_#13270_05STUART 69.0_E | OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 243997 TO BUS 244007 CKT 1 / 243997 05STUART A 69.0 244007 05WOOLWINE 69.0 1 REMOVE SWSHUNT FROM BUS 243997 / 243997 05STUART A 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM496 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0522 | 1.0518 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM497 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0522 | 1.0518 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 | OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM498 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.052 | 1.0517 | 1.05/0.92 | Single | AEP_P1-2_#11293_293 | OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 243997 TO BUS 244007 CKT 1 / 243997 05STUART A 69.0 244007 05WOOLWINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM499 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0517 | 1.051 | 1.05/0.92 | FB | AEP_P4_#10235_05FIELDALE2 138_Q | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 242844 TO BUS 244001 CKT 1 / 242844 05W.BASS 138 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 244000 TO BUS 244001 CKT Z1 / 244000 05W.BASSET 69.0 244001 05WBASSTEQ 999 Z1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243999 TO BUS 244001 CKT 1 / 243999 05W.BASSET 34.5 244001 05WBASSTEQ 999 1 OPEN BRANCH FROM BUS 243799 TO BUS 244904 CKT Z2 / 243799 05FIELDALE2 138 244904 05FIELDALE4 138 Z2 OPEN BRANCH FROM BUS 242736 TO BUS 243799 CKT 1 / 242736 05OAKLEV 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242744 TO BUS 243799 CKT 1 / 242744 05PATCTR 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242844 TO BUS 243799 CKT 1 / 242844 05W.BASS 138 243799 05FIELDALE2 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 REMOVE SWSHUNT FROM BUS 243799 / 243799 05FIELDALE2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM500 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0484 | 1.0526 | 1.05/0.92 | N-1-1 | AEP_P1-2_#8518_92 | OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 | AEP_P1-3_#11341_05N.CLAYTOR 138_3 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 OPEN BRANCH FROM BUS 244138 TO BUS 244145 CKT 1 / 244138 05N.CLAYTO 34.5 244145 05RADFORD 34.5 1 OPEN BRANCH FROM BUS 244138 TO BUS 244150 CKT 1 / 244138 05N.CLAYTO 34.5 244150 05SMITH LA 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VM501 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0517 | - | 1.05/0.92 | N-1-1 | AEP_P1-2_#11293_293 | OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 243997 TO BUS 244007 CKT 1 / 243997 05STUART A 69.0 244007 05WOOLWINE 69.0 1 | Base Case |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan | #REF!
AEP-VM502 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243691 | 05HAYSBR | 138 | 205 | 0.9649 | 1.0948 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM503 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244008 | 05STANVILLE1 | 138 | 205 | 0.9686 | 1.0879 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM504 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242915 | 05STANVILLE2 | 138 | 205 | 0.9686 | 1.0879 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM505 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244008 | 05STANVILLE1 | 138 | 205 | 0.9686 | 1.0634 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM506 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242915 | 05STANVILLE2 | 138 | 205 | 0.9686 | 1.0634 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM507 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243691 | 05HAYSBR | 138 | 205 | 0.9649 | 1.0699 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM508 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243691 | 05HAYSBR | 138 | 205 | 0.9738 | 1.0949 | 1.05/0.92 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM509 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244008 | 05STANVILLE1 | 138 | 205 | 0.9791 | 1.088 | 1.05/0.92 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM510 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242915 | 05STANVILLE2 | 138 | 205 | 0.9791 | 1.088 | 1.05/0.92 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VM511 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 0.9721 | 0.9158 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM512 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 0.9723 | 0.916 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM513 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 0.9724 | 0.9161 | 1.05/0.92 | N-1-1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM514 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 0.9782 | 0.9157 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM515 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 0.9783 | 0.9159 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM516 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245726 | 05GRIFTHSS | 34.5 | 205 | 1.0673 | 1.0679 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM517 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245738 | 05DOWCHEM2 | 34.5 | 205 | 1.0661 | 1.0666 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM518 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245796 | 05WHIRLPOO | 34.5 | 205 | 1.0658 | 1.0663 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM519 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245762 | 05N BALTMR | 34.5 | 205 | 1.0654 | 1.066 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM520 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245779 | 05POE AVE TP | 34.5 | 205 | 1.0652 | 1.0658 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM521 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245752 | 05HENRY8 | 34.5 | 205 | 1.0649 | 1.0654 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM522 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245729 | 05CYGBUCK | 34.5 | 205 | 1.0638 | 1.0643 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM523 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245727 | 05BROWN RU | 34.5 | 205 | 1.0633 | 1.0638 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM524 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245737 | 05WRUTHFRDSS | 34.5 | 205 | 1.0619 | 1.0625 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM525 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245761 | 05MUNGEN | 34.5 | 205 | 1.0619 | 1.0624 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM526 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 1.0614 | 1.0619 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM527 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 1.0613 | 1.0618 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM528 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247317 | 05LIBHI 8 | 34.5 | 205 | 1.0607 | 1.0612 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM529 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245725 | 05ASH AVE | 34.5 | 205 | 1.0512 | 1.0517 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM530 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 0.9782 | 0.915 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM531 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 0.9783 | 0.9152 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM532 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245761 | 05MUNGEN | 34.5 | 205 | 0.9809 | 0.918 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM533 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245761 | 05MUNGEN | 34.5 | 205 | 0.9809 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM534 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 0.9722 | 0.916 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM535 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245761 | 05MUNGEN | 34.5 | 205 | 0.9749 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM536 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245737 | 05WRUTHFRDSS | 34.5 | 205 | 1.0506 | 1.0511 | 1.05/0.92 | FB | AEP_P4_#10110_05EBERSO 138_A | OPEN BRANCH FROM BUS 243004 TO BUS 245749 CKT 1 / 243004 05FINDLC 138 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 245747 TO BUS 245749 CKT 1 / 245747 05FINDLAY C 34.5 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 243033 TO BUS 247172 CKT 1 / 243033 05THORNWD SS 138 247172 05EBERSO 138 1 OPEN BRANCH FROM BUS 243004 TO BUS 243033 CKT 1 / 243004 05FINDLC 138 243033 05THORNWD SS 138 1 OPEN BRANCH FROM BUS 247172 TO BUS 247211 CKT 1 / 247172 05EBERSO 138 247211 05EBERSOLE 34.5 1 OPEN BRANCH FROM BUS 245754 TO BUS 247211 CKT 1 / 245754 05LANDMRK8 34.5 247211 05EBERSOLE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM537 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245726 | 05GRIFTHSS | 34.5 | 205 | 1.0505 | 1.051 | 1.05/0.92 | FB | AEP_P4_#10110_05EBERSO 138_A | OPEN BRANCH FROM BUS 243004 TO BUS 245749 CKT 1 / 243004 05FINDLC 138 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 245747 TO BUS 245749 CKT 1 / 245747 05FINDLAY C 34.5 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 243033 TO BUS 247172 CKT 1 / 243033 05THORNWD SS 138 247172 05EBERSO 138 1 OPEN BRANCH FROM BUS 243004 TO BUS 243033 CKT 1 / 243004 05FINDLC 138 243033 05THORNWD SS 138 1 OPEN BRANCH FROM BUS 247172 TO BUS 247211 CKT 1 / 247172 05EBERSO 138 247211 05EBERSOLE 34.5 1 OPEN BRANCH FROM BUS 245754 TO BUS 247211 CKT 1 / 245754 05LANDMRK8 34.5 247211 05EBERSOLE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM538 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245796 | 05WHIRLPOO | 34.5 | 205 | 1.0503 | 1.0508 | 1.05/0.92 | FB | AEP_P4_#10110_05EBERSO 138_A | OPEN BRANCH FROM BUS 243004 TO BUS 245749 CKT 1 / 243004 05FINDLC 138 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 245747 TO BUS 245749 CKT 1 / 245747 05FINDLAY C 34.5 245749 05FNDCTREQ 999 1 OPEN BRANCH FROM BUS 243033 TO BUS 247172 CKT 1 / 243033 05THORNWD SS 138 247172 05EBERSO 138 1 OPEN BRANCH FROM BUS 243004 TO BUS 243033 CKT 1 / 243004 05FINDLC 138 243033 05THORNWD SS 138 1 OPEN BRANCH FROM BUS 247172 TO BUS 247211 CKT 1 / 247172 05EBERSO 138 247211 05EBERSOLE 34.5 1 OPEN BRANCH FROM BUS 245754 TO BUS 247211 CKT 1 / 245754 05LANDMRK8 34.5 247211 05EBERSOLE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM539 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245791 | 05VANBURN8 | 34.5 | 205 | 1.0665 | 1.067 | 1.05/0.92 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VM540 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243758 | 05MIDDLECR | 46 | 205 | 0.9134 | 0.9098 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1 | OPEN BRANCH FROM BUS 243721 TO BUS 341461 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VM541 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 0.8145 | 0.8128 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1 | OPEN BRANCH FROM BUS 243721 TO BUS 341461 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VM542 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 0.8144 | 0.8128 | 1.05/0.92 | Bus | EKPC_P2-2_FALCON 69 | OPEN BUS 341461 /* 2FALCON EK |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VM543 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 0.7425 | 0.7389 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1 | OPEN BRANCH FROM BUS 243721 TO BUS 341461 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VM544 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 0.7493 | 0.735 | 1.05/0.92 | Bus | EKPC_P2-2_FALCON 69 | OPEN BUS 341461 /* 2FALCON EK |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VM545 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0088 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM546 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0088 | 0.9177 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM547 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 1.0039 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM548 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 1.0039 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM549 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.9186 | 1.05/0.92 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM550 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.9186 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VM551 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 69 | 205 | 0.6715 | 0.6556 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM552 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 69 | 205 | 0.7078 | 0.7056 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM553 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0118 | 0.8887 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM554 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0173 | 0.8887 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM555 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9891 | 0.8937 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM556 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9942 | 0.8938 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM557 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9992 | 0.905 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM558 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 1.0042 | 0.9051 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM559 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0072 | 0.8962 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM560 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0149 | 0.8962 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM561 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243759 | 05PRESTNSB | 46 | 205 | 0.9982 | 0.8787 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Line: Associated with AEP-2018-AP022, Station: Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM562 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243753 | 05ALLEN | 46 | 205 | 0.998 | 0.9116 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM563 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 0.9873 | 0.6605 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM564 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 1.0017 | 0.6489 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM565 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 1.0033 | 0.8319 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM566 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 1.0059 | 0.8319 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM567 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 0.9883 | 0.6603 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM568 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 1.0038 | 0.6591 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM569 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 0.9976 | 0.8386 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM570 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 1.0015 | 0.8386 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Identified internally as a need, awaiting field and engineering analysis
AEP-VM571 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.901 | 0.9002 | 1.05/0.92 | Single | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM572 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9014 | 0.9006 | 1.05/0.92 | Single | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM573 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9022 | 0.9014 | 1.05/0.92 | Single | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM574 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9026 | 0.9018 | 1.05/0.92 | Single | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM575 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.9156 | 0.915 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245627 05N FREMON 69.0 247523 05FE WFREMSS 69.0 1 | OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM576 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.916 | 0.9153 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245617 05FREMONT 69.0 247523 05FE WFREMSS 69.0 Z1 | OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM577 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9161 | 0.9155 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245627 05N FREMON 69.0 247523 05FE WFREMSS 69.0 1 | OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM578 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9164 | 0.9158 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245617 05FREMONT 69.0 247523 05FE WFREMSS 69.0 Z1 | OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM579 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9168 | 0.9162 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245627 05N FREMON 69.0 247523 05FE WFREMSS 69.0 1 | OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM580 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9171 | 0.9165 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245617 05FREMONT 69.0 247523 05FE WFREMSS 69.0 Z1 | OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM581 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9172 | 0.9166 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245627 05N FREMON 69.0 247523 05FE WFREMSS 69.0 1 | OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM582 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9175 | 0.9169 | 1.05/0.92 | Line w/o Fault | AEP_P2-1_245617 05FREMONT 69.0 247523 05FE WFREMSS 69.0 Z1 | OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM583 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 0.6508 | 0.6296 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM584 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.6559 | 0.5813 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM585 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.6559 | 0.5809 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM586 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.6564 | 0.5803 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM587 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.6576 | 0.58 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM588 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 0.6655 | 0.6519 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM589 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 0.6662 | 0.6522 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM590 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 0.6678 | 0.6532 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM591 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245623 | 05HOLRAN | 69 | 205 | 0.8092 | 0.803 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM592 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245625 | 05MAPLE GR | 69 | 205 | 0.829 | 0.8237 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM593 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.9072 | 0.9065 | 1.05/0.92 | FB | AEP_P4_#12322_05FREMONT 69.0_A | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245641 CKT 1 / 245614 05FREMNT C 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245634 TO BUS 245641 CKT 1 / 245634 05STONE ST 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245634 CKT 1 / 245631 05SBC CONT 69.0 245634 05STONE ST 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM594 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9077 | 0.9069 | 1.05/0.92 | FB | AEP_P4_#12322_05FREMONT 69.0_A | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245641 CKT 1 / 245614 05FREMNT C 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245634 TO BUS 245641 CKT 1 / 245634 05STONE ST 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245634 CKT 1 / 245631 05SBC CONT 69.0 245634 05STONE ST 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM595 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9084 | 0.9076 | 1.05/0.92 | FB | AEP_P4_#12322_05FREMONT 69.0_A | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245641 CKT 1 / 245614 05FREMNT C 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245634 TO BUS 245641 CKT 1 / 245634 05STONE ST 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245634 CKT 1 / 245631 05SBC CONT 69.0 245634 05STONE ST 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM596 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9088 | 0.908 | 1.05/0.92 | FB | AEP_P4_#12322_05FREMONT 69.0_A | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245641 CKT 1 / 245614 05FREMNT C 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245634 TO BUS 245641 CKT 1 / 245634 05STONE ST 69.0 245641 05BIRCHARDSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245634 CKT 1 / 245631 05SBC CONT 69.0 245634 05STONE ST 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM597 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.9098 | 0.9091 | 1.05/0.92 | FB | AEP_P4_#12321_05FREMONT 69.0_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245645 CKT 1 / 245614 05FREMNT C 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM598 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9103 | 0.9095 | 1.05/0.92 | FB | AEP_P4_#12321_05FREMONT 69.0_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245645 CKT 1 / 245614 05FREMNT C 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM599 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.911 | 0.9102 | 1.05/0.92 | FB | AEP_P4_#12321_05FREMONT 69.0_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245645 CKT 1 / 245614 05FREMNT C 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM600 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9114 | 0.9107 | 1.05/0.92 | FB | AEP_P4_#12321_05FREMONT 69.0_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245614 TO BUS 245645 CKT 1 / 245614 05FREMNT C 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM601 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9026 | 0.9018 | 1.05/0.92 | Bus | AEP_P2-2_#11861_05FREMONT 69.0_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM602 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9022 | 0.9014 | 1.05/0.92 | Bus | AEP_P2-2_#11861_05FREMONT 69.0_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM603 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9014 | 0.9006 | 1.05/0.92 | Bus | AEP_P2-2_#11861_05FREMONT 69.0_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM604 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.901 | 0.9002 | 1.05/0.92 | Bus | AEP_P2-2_#11861_05FREMONT 69.0_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM605 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.8668 | 0.9032 | 1.05/0.92 | Tower | AEP_P7-1_#10932 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM606 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.8664 | 0.9028 | 1.05/0.92 | Tower | AEP_P7-1_#10931 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 238884 TO BUS 238890 CKT ZB / 238884 02LEMO K 138 238890 02LEMOYN 138 ZB OPEN BRANCH FROM BUS 238884 TO BUS 239154 CKT 1 / 238884 02LEMO K 138 239154 02W.FREM 138 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM607 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.8664 | 0.9027 | 1.05/0.92 | Tower | AEP_P7-1_#10932 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM608 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.866 | 0.9024 | 1.05/0.92 | Tower | AEP_P7-1_#10931 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 238884 TO BUS 238890 CKT ZB / 238884 02LEMO K 138 238890 02LEMOYN 138 ZB OPEN BRANCH FROM BUS 238884 TO BUS 239154 CKT 1 / 238884 02LEMO K 138 239154 02W.FREM 138 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM609 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.8656 | 0.902 | 1.05/0.92 | Tower | AEP_P7-1_#10932 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM610 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.8652 | 0.9016 | 1.05/0.92 | Tower | AEP_P7-1_#10931 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 238884 TO BUS 238890 CKT ZB / 238884 02LEMO K 138 238890 02LEMOYN 138 ZB OPEN BRANCH FROM BUS 238884 TO BUS 239154 CKT 1 / 238884 02LEMO K 138 239154 02W.FREM 138 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM611 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.8651 | 0.9016 | 1.05/0.92 | Tower | AEP_P7-1_#10932 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM612 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.8647 | 0.9012 | 1.05/0.92 | Tower | AEP_P7-1_#10931 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 238884 TO BUS 238890 CKT ZB / 238884 02LEMO K 138 238890 02LEMOYN 138 ZB OPEN BRANCH FROM BUS 238884 TO BUS 239154 CKT 1 / 238884 02LEMO K 138 239154 02W.FREM 138 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM613 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 0.6787 | 0.6764 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM614 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.648 | 0.6458 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM615 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.6477 | 0.6456 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM616 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.6473 | 0.6451 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM617 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.6472 | 0.6451 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM618 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 0.7052 | 0.703 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM619 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 0.7054 | 0.7032 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM620 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 0.7061 | 0.7039 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM621 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245623 | 05HOLRAN | 69 | 205 | 0.842 | 0.8398 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM622 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245625 | 05MAPLE GR | 69 | 205 | 0.8599 | 0.8578 | 1.05/0.92 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM623 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9557 | 0.8137 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM624 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9717 | 0.8137 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM625 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9552 | 0.8284 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM626 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.97 | 0.8284 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM627 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0068 | 0.8228 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM628 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0137 | 0.8098 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM629 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9721 | 0.853 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM630 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0033 | 0.8469 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM631 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0088 | 0.833 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM632 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0091 | 0.8529 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM633 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0091 | 0.8557 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM634 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.014 | 0.8423 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM635 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0139 | 0.8452 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM636 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9664 | 0.877 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM637 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.976 | 0.877 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM638 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0021 | 0.8671 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM639 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0067 | 0.8527 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM640 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0092 | 0.8857 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM641 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.968 | 0.8844 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM642 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9772 | 0.8844 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM643 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9683 | 0.8847 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM644 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9774 | 0.8847 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM645 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0099 | 0.8865 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM646 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0101 | 0.8867 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM647 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0104 | 0.887 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM648 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0147 | 0.8857 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM649 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0155 | 0.8865 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM650 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0156 | 0.8867 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM651 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0118 | 0.8887 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM652 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0159 | 0.887 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM653 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.9889 | 0.8883 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM654 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.994 | 0.8883 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM655 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9891 | 0.8885 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM656 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9942 | 0.8886 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM657 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0173 | 0.8887 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM658 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9696 | 0.8888 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM659 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9772 | 0.8888 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM660 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.9706 | 0.8915 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM661 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.977 | 0.8915 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM662 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0109 | 0.8984 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM663 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0163 | 0.8984 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM664 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9888 | 0.9001 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM665 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9936 | 0.9001 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM666 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9708 | 0.899 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM667 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9772 | 0.899 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM668 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.9718 | 0.9014 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM669 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.977 | 0.9014 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM670 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9894 | 0.9055 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM671 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9944 | 0.9055 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM672 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0081 | 0.9073 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM673 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0119 | 0.9072 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM674 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9897 | 0.9084 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM675 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9947 | 0.9085 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM676 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0077 | 0.912 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM677 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.009 | 0.9123 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM678 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9694 | 0.9116 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM679 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0074 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM680 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9697 | 0.912 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM681 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0115 | 0.912 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM682 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0144 | 0.9123 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM683 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0111 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM684 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9636 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM685 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9639 | 0.9139 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM686 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9783 | 0.9151 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM687 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9786 | 0.9155 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM688 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9664 | 0.9168 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM689 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9607 | 0.9168 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM690 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9664 | 0.9172 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM691 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.961 | 0.9172 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM692 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.968 | 0.9175 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM693 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9597 | 0.9176 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM694 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9683 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM695 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.968 | 0.918 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM696 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.96 | 0.9178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM697 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.96 | 0.918 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM698 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9683 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM699 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9603 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM700 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 34.5 | 205 | 0.9908 | 0.9189 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM701 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 34.5 | 205 | 0.9958 | 0.9189 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM702 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 34.5 | 205 | 0.9912 | 0.9196 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM703 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 34.5 | 205 | 0.9956 | 0.9196 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM704 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0074 | 0.8213 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM705 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0152 | 0.8204 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM706 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9722 | 0.8604 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM707 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0046 | 0.8443 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM708 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0108 | 0.8435 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM709 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0078 | 0.8539 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM710 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0077 | 0.8568 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM711 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0147 | 0.8531 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM712 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.004 | 0.8639 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM713 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0146 | 0.856 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM714 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0092 | 0.8632 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM715 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9761 | 0.8832 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM716 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9681 | 0.8832 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM717 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9772 | 0.8902 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM718 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9774 | 0.8905 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM719 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9696 | 0.8902 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM720 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9699 | 0.8905 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM721 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.9991 | 0.8997 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM722 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 1.0041 | 0.8998 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM723 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9993 | 0.8999 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM724 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 1.0044 | 0.9001 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM725 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.9622 | 0.9115 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5874_185 | OPEN BRANCH FROM BUS 242622 TO BUS 242999 CKT 1 / 242622 05DARRH2 138 242999 05EPROCT 138 1 OPEN BRANCH FROM BUS 242999 TO BUS 243064 CKT 1 / 242999 05EPROCT 138 243064 05NPROCT 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM726 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.9665 | 0.9115 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#5874_185 | OPEN BRANCH FROM BUS 242622 TO BUS 242999 CKT 1 / 242622 05DARRH2 138 242999 05EPROCT 138 1 OPEN BRANCH FROM BUS 242999 TO BUS 243064 CKT 1 / 242999 05EPROCT 138 243064 05NPROCT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM727 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9992 | 0.9117 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM728 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 1.0039 | 0.9118 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM729 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0051 | 0.8939 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM730 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0129 | 0.8939 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM731 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9641 | 0.9191 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM732 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0054 | 0.8942 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM733 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0132 | 0.8942 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM734 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0058 | 0.8947 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM735 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0058 | 0.8947 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM736 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0136 | 0.8947 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM737 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0136 | 0.8947 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM738 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0072 | 0.8962 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM739 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0149 | 0.8962 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM740 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9992 | 0.9164 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM741 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 1.0041 | 0.9165 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM742 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246381 | 05BERCADO | 34.5 | 205 | 0.9179 | 0.9176 | 1.05/0.92 | Bus | AEP_P2-2_#14784_05KLINE 34.5_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM743 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246381 | 05BERCADO | 34.5 | 205 | 0.9179 | 0.9176 | 1.05/0.92 | FB | AEP_P4_#14782_05KLINE 34.5_CB1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM744 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246381 | 05BERCADO | 34.5 | 205 | 0.9182 | 0.9178 | 1.05/0.92 | FB | AEP_P4_#14141_05KLINE 34.5_B | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 246415 TO BUS 246416 CKT 1 / 246415 05KLINE 34.5 246416 05TWIN BRCH134.5 1 OPEN BRANCH FROM BUS 246381 TO BUS 246415 CKT 1 / 246381 05BERCADO 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246415 CKT 1 / 246300 05BEIGER 34.5 246415 05KLINE 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246368 CKT 1 / 246300 05BEIGER 34.5 246368 05VIRGIL S 34.5 1 OPEN BRANCH FROM BUS 246300 TO BUS 246302 CKT 1 / 246300 05BEIGER 34.5 246302 05MILES MISH34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM745 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.006 | 0.9049 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM746 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0034 | 0.9133 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM747 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0049 | 0.9164 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM748 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0027 | 0.9173 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM749 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9608 | 0.78 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM750 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.954 | 0.7848 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM751 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9557 | 0.7867 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM752 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9567 | 0.7926 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM753 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9586 | 0.8236 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM754 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9578 | 0.837 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM755 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9625 | 0.8604 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM756 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9578 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM757 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9625 | 0.9191 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM758 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9733 | 0.9149 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM759 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9702 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM760 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.969 | 0.9192 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM761 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0133 | 0.9049 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM762 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0089 | 0.9133 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM763 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0117 | 0.9164 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM764 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0081 | 0.9172 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM765 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.935 | 0.78 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM766 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9392 | 0.7848 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM767 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9409 | 0.7867 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM768 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9459 | 0.7926 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM769 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.972 | 0.8236 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM770 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9701 | 0.837 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM771 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.935 | 0.914 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM772 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.935 | 0.9149 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM773 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9392 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM774 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9392 | 0.9192 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM775 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9726 | 0.914 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM776 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9695 | 0.9174 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM777 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9684 | 0.9183 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM778 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9587 | 0.7683 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM779 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9511 | 0.773 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM780 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9528 | 0.7749 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM781 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9538 | 0.7813 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM782 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9604 | 0.853 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM783 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246381 | 05BERCADO | 34.5 | 205 | 0.9737 | 0.919 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM784 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9552 | 0.912 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM785 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9604 | 0.9135 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM786 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9604 | 0.9139 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM787 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9557 | 0.915 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM788 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9557 | 0.9154 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM789 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.9574 | 0.9055 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5874_185 | OPEN BRANCH FROM BUS 242622 TO BUS 242999 CKT 1 / 242622 05DARRH2 138 242999 05EPROCT 138 1 OPEN BRANCH FROM BUS 242999 TO BUS 243064 CKT 1 / 242999 05EPROCT 138 243064 05NPROCT 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM790 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.9624 | 0.9055 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#5874_185 | OPEN BRANCH FROM BUS 242622 TO BUS 242999 CKT 1 / 242622 05DARRH2 138 242999 05EPROCT 138 1 OPEN BRANCH FROM BUS 242999 TO BUS 243064 CKT 1 / 242999 05EPROCT 138 243064 05NPROCT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM791 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.966 | 0.9164 | 1.05/0.92 | N-1-1 | AEP_P1-2_#6021_108 | OPEN BRANCH FROM BUS 242621 TO BUS 242835 CKT 1 / 242621 05DARRH1 138 242835 05TRISTA 138 1 | AEP_P1-3_#1267_05NPROCT 765_1 | OPEN BRANCH FROM BUS 242929 TO BUS 243064 CKT 2 / 242929 05NPROCT 765 243064 05NPROCT 138 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM792 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244716 | 05INCO FUR | 34.5 | 205 | 0.9678 | 0.9176 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-3_#1267_05NPROCT 765_1 | OPEN BRANCH FROM BUS 242929 TO BUS 243064 CKT 2 / 242929 05NPROCT 765 243064 05NPROCT 138 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM793 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9728 | 0.9104 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM794 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.968 | 0.9147 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM795 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9697 | 0.9164 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11960_05KLINE 138_1 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM796 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246381 | 05BERCADO | 34.5 | 205 | 0.98 | 0.919 | 1.05/0.92 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM797 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9726 | 0.91 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM798 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9678 | 0.9143 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM799 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9695 | 0.916 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14779 | OPEN BRANCH FROM BUS 247609 TO BUS 247780 CKT 2 / 247609 05KLINE 2EQ 999 247780 05KLINE 138 2 OPEN BRANCH FROM BUS 247609 TO BUS 247610 CKT 2 / 247609 05KLINE 2EQ 999 247610 05KLINE 69.0 2 OPEN BRANCH FROM BUS 246415 TO BUS 247609 CKT 2 / 246415 05KLINE 34.5 247609 05KLINE 2EQ 999 2 OPEN BRANCH FROM BUS 243385 TO BUS 247780 CKT 1 / 243385 05TWIN B 138 247780 05KLINE 138 1 OPEN BRANCH FROM BUS 247780 TO BUS 255163 CKT 1 / 247780 05KLINE 138 255163 17NORTHEAST 138 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM800 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0024 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM801 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9802 | 0.9156 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM802 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9915 | 0.9156 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM803 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0078 | 0.9187 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM804 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 1.003 | 0.8945 | 1.05/0.92 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM805 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 1.0015 | 0.895 | 1.05/0.92 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM806 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 1.0009 | 0.8957 | 1.05/0.92 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM807 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 1.0007 | 0.8961 | 1.05/0.92 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-3_#11861_05FRMNT 138_1 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245645 CKT 1 / 245617 05FREMONT 69.0 245645 05CLYDE 69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 247523 CKT Z1 / 245617 05FREMONT 69.0 247523 05FE WFREMSS69.0 Z1 OPEN BRANCH FROM BUS 245627 TO BUS 247523 CKT 1 / 245627 05N FREMON 69.0 247523 05FE WFREMSS69.0 1 OPEN BRANCH FROM BUS 245617 TO BUS 245631 CKT 1 / 245617 05FREMONT 69.0 245631 05SBC CONT 69.0 1 REMOVE SWSHUNT FROM BUS 245617 / 245617 05FREMONT 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM808 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245722 | 05ARLINGTO | 34.5 | 205 | 0.9331 | 0.7616 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM809 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245720 | 05ARLINGT8 | 34.5 | 205 | 0.9331 | 0.7616 | 1.05/0.92 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM810 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245722 | 05ARLINGTO | 34.5 | 205 | 0.9075 | 0.9195 | 1.05/0.92 | Single | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM811 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245720 | 05ARLINGT8 | 34.5 | 205 | 0.9075 | 0.9195 | 1.05/0.92 | Single | AEP_P1-3_#12467_05SKENTO 138_2-3 | OPEN BRANCH FROM BUS 243031 TO BUS 243103 CKT 1 / 243031 05LYNN Z 138 243103 05SKENTO 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 246879 CKT 1 / 243103 05SKENTO 138 246879 05S KENTN1 69.0 1 OPEN BRANCH FROM BUS 243103 TO BUS 246880 CKT 1 / 243103 05SKENTO 138 246880 05S KENTN2 69.0 1 OPEN BRANCH FROM BUS 246873 TO BUS 246880 CKT 1 / 246873 05FONTAINE 69.0 246880 05S KENTN2 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM812 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246970 | 05MAYOTRL | 69 | 205 | 1.0258 | 0.7192 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM813 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244632 | 05W.PNTSVL | 69 | 205 | 1.0275 | 0.7202 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM814 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244608 | 05KENWOOD | 46 | 205 | 1.0144 | 0.7767 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Line: Associated with AEP-2018-AP022, Station: Potential M-3 need identified, awaiting field and engineering analysis
AEP-VM815 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243754 | 05EPRESTNS | 46 | 205 | 0.9969 | 0.8868 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM816 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243758 | 05MIDDLECR | 46 | 205 | 1.0033 | 0.9041 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM817 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9994 | 0.9192 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM818 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.9815 | 0.9185 | 1.05/0.92 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM819 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 1.0043 | 0.9194 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM820 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.9917 | 0.9185 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM821 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.8835 | 0.9072 | 1.05/0.92 | FB | DVP_P4-5: L542-2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314794 CKT 1 /* 3DOOMS 115.00 - 6DOOMS 230.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM822 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.8835 | 0.9072 | 1.05/0.92 | FB | DVP_P4-5: L842-2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314794 CKT 3 /* 3DOOMS 115.00 - 6DOOMS 230.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM823 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.8836 | 0.9073 | 1.05/0.92 | FB | DVP_P4-2: 16042 | OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM824 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.8838 | 0.9075 | 1.05/0.92 | FB | DVP_P4-2: 10242 | OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314812 CKT 1 /* 3BRND DP 115.00 - 3STAUNTN 115.00 OPEN BUS 314791 /* ISLAND: 3BRND DP 115.00 OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM825 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.8836 | 0.9073 | 1.05/0.92 | Bus | DVP_P2-2: DOOMS B2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM826 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 0.985 | 0.6583 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM827 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 1.0029 | 0.6466 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM828 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 0.9972 | 0.7177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM829 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 0.9972 | 0.7177 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM830 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.006 | 0.7178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM831 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.006 | 0.7178 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM832 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0019 | 0.8302 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM833 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0019 | 0.8303 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM834 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0067 | 0.8302 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM835 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0067 | 0.8302 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM836 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 0.986 | 0.658 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM837 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 1.0049 | 0.6568 | 1.05/0.92 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM838 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.0009 | 0.727 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM839 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.0009 | 0.7271 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM840 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.0088 | 0.7273 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM841 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.0089 | 0.7273 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM842 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 0.9962 | 0.8369 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM843 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0022 | 0.8369 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM844 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0022 | 0.8369 | 1.05/0.92 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM845 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 0.9962 | 0.8369 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM846 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 0.9957 | 0.892 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM847 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 0.9942 | 0.9034 | 1.05/0.92 | N-1-1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM848 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 0.9976 | 0.9148 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7563_2802421 | OPEN BRANCH FROM BUS 242594 TO BUS 242604 CKT 1 / 242594 05CHERCK 138 242604 05CLIFFT 138 1 OPEN BRANCH FROM BUS 242604 TO BUS 939800 CKT 1 / 242604 05CLIFFT 138 939800 AE1-212 TAP 138 1 OPEN BRANCH FROM BUS 939800 TO BUS 242653 CKT 1 / 939800 AE1-212 TAP 138 242653 05GRANDV 138 1 | AEP_P1-2_#14911 | OPEN BRANCH FROM BUS 242747 TO BUS 242818 CKT 1 / 242747 05PEMBRT 138 242818 05STOTES 138 1 OPEN BRANCH FROM BUS 242818 TO BUS 242824 CKT 1 / 242818 05STOTES 138 242824 05TAMSM1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM849 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 1.0066 | 0.8921 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM850 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 1.0037 | 0.9034 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM851 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 1.0054 | 0.9148 | 1.05/0.92 | N-1-1 | AEP_P1-2_#14911 | OPEN BRANCH FROM BUS 242747 TO BUS 242818 CKT 1 / 242747 05PEMBRT 138 242818 05STOTES 138 1 OPEN BRANCH FROM BUS 242818 TO BUS 242824 CKT 1 / 242818 05STOTES 138 242824 05TAMSM1 138 1 | AEP_P1-2_#7563_2802421 | OPEN BRANCH FROM BUS 242594 TO BUS 242604 CKT 1 / 242594 05CHERCK 138 242604 05CLIFFT 138 1 OPEN BRANCH FROM BUS 242604 TO BUS 939800 CKT 1 / 242604 05CLIFFT 138 939800 AE1-212 TAP 138 1 OPEN BRANCH FROM BUS 939800 TO BUS 242653 CKT 1 / 939800 AE1-212 TAP 138 242653 05GRANDV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM852 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242707 | 05LOWESM | 138 | 205 | 0.9983 | 1.0584 | 1.05/0.92 | N-1-1 | AEP_P1-2_#13625_26498 | OPEN BRANCH FROM BUS 242630 TO BUS 242784 CKT 1 / 242630 05E.RIVE 138 242784 05S.BLUE 138 1 OPEN BRANCH FROM BUS 242630 TO BUS 242786 CKT 1 / 242630 05E.RIVE 138 242786 05S.PRINCETN 138 1 | AEP_P1-2_#9197_25159 | OPEN BRANCH FROM BUS 242760 TO BUS 247850 CKT 1 / 242760 05PROGPK 138 247850 05TOWN CREEK 138 1 OPEN BRANCH FROM BUS 242784 TO BUS 247850 CKT 1 / 242784 05S.BLUE 138 247850 05TOWN CREEK 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM853 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 1.0044 | 0.9125 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM854 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 1.0073 | 0.9015 | 1.05/0.92 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM855 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244446 | 05SOAPSTONE | 138 | 205 | 0.9975 | 0.8535 | 1.05/0.92 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM856 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244423 | 05JAMES RIVR | 138 | 205 | 1.0007 | 0.8982 | 1.05/0.92 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM857 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 1.0015 | 0.9068 | 1.05/0.92 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM858 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244446 | 05SOAPSTONE | 138 | 205 | 0.9916 | 0.8541 | 1.05/0.92 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM859 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244423 | 05JAMES RIVR | 138 | 205 | 0.9966 | 0.8987 | 1.05/0.92 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VM860 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 0.9977 | 0.9073 | 1.05/0.92 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Voltage Drop
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Vdrop(%) | Delta Voltage Limit | Cont Type | Cont 1 Name | Contingency 1 description | Cont 2 Name | Contingency 2 description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment | M3 Process Status
AEP-VD1 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246970 | 05MAYOTRL | 69 | 205 | 1.0258 | 0.9311 | 9.47 | 8 | N-1-1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | AEP_P1-2_#7389_17037 | OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT SR / 243669 05B SAND 138 243678 05BSANDX 138 SR OPEN BRANCH FROM BUS 243669 TO BUS 243678 CKT ZB / 243669 05B SAND 138 243678 05BSANDX 138 ZB OPEN BRANCH FROM BUS 243678 TO BUS 243679 CKT 1 / 243678 05BSANDX 138 243679 05BUSSYV 138 1 OPEN BRANCH FROM BUS 243679 TO BUS 243702 CKT 1 / 243679 05BUSSYV 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243702 TO BUS 246971 CKT 1 / 243702 05THELMA 138 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246970 TO BUS 246971 CKT 1 / 246970 05MAYOTRL 69.0 246971 05THELM2 69.0 1 OPEN BRANCH FROM BUS 246971 TO BUS 342343 CKT 1 / 246971 05THELM2 69.0 342343 2THELMA 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD2 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9953 | 0.9094 | 8.59 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VD3 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9929 | 0.9083 | 8.46 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD4 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9921 | 0.9097 | 8.24 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD5 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9878 | 0.8908 | 9.7 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VD6 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9839 | 0.8881 | 9.58 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD7 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9811 | 0.8874 | 9.37 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD8 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9803 | 0.8894 | 9.09 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD9 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9791 | 0.8891 | 9 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD10 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9793 | 0.8894 | 8.99 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD11 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9788 | 0.8913 | 8.75 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD12 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9878 | 0.9017 | 8.61 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VD13 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243822 | 05ROSEMOUN | 69 | 205 | 0.9749 | 0.8892 | 8.57 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH015 | Need
AEP-VD14 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9839 | 0.8988 | 8.51 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD15 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243824 | 05SUGARHIL | 69 | 205 | 0.9719 | 0.8864 | 8.55 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD16 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9704 | 0.8856 | 8.48 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD17 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244921 | 05FRIENDSH | 69 | 205 | 0.9811 | 0.8979 | 8.32 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD18 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9713 | 0.8878 | 8.35 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD19 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243816 | 05MILL ST | 69 | 205 | 0.9705 | 0.8874 | 8.31 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD20 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246916 | 05CORNRSTN | 69 | 205 | 0.9708 | 0.8878 | 8.3 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD21 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246917 | 05RUHLMAN | 69 | 205 | 0.9712 | 0.8897 | 8.15 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD22 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243815 | 05CENPORTS | 69 | 205 | 0.9803 | 0.8996 | 8.07 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#13646_21537 | OPEN BRANCH FROM BUS 243047 TO BUS 243087 CKT 1 / 243047 05N PORT 138 243087 05S LUCA 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD23 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 1.0091 | 0.9134 | 9.57 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VD24 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 1.004 | 0.892 | 11.2 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VD25 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243087 | 05S LUCA | 138 | 205 | 0.9796 | 0.8904 | 8.92 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2018-OH030 | Need
AEP-VD26 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243173 | 05MILLBRK | 69 | 205 | 0.9782 | 0.8961 | 8.21 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD27 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 1.0089 | 0.8405 | 16.84 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD28 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 1.0089 | 0.8406 | 16.83 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD29 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 0.978 | 0.8402 | 13.78 | 8 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD30 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 0.9781 | 0.8403 | 13.78 | 8 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD31 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246984 | 05HEMLOCK | 69 | 205 | 1.0108 | 0.8959 | 11.49 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD32 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 1.0065 | 0.8822 | 12.43 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD33 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 1.0065 | 0.8899 | 11.66 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD34 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 0.981 | 0.8795 | 10.15 | 8 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD35 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246732 | 05BASHAN | 69 | 205 | 0.9811 | 0.8796 | 10.15 | 8 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD36 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246984 | 05HEMLOCK | 69 | 205 | 9.42 | 9.3258 | 9.42 | 8 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD37 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9894 | 0.8168 | 17.26 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-OH028 | Need
AEP-VD38 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9578 | 0.8164 | 14.14 | 8 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-OH028 | Need
AEP-VD39 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9901 | 0.8718 | 11.83 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-OH028 | Need
AEP-VD40 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9642 | 0.8606 | 10.36 | 8 | N-1-1 | AEP_P1-3_#13818_05RIPLEY 138_3 | OPEN BRANCH FROM BUS 243947 TO BUS 247572 CKT 3 / 243947 05RIPLEY 138 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 244763 TO BUS 247572 CKT 3 / 244763 05RIPLEY 69.0 247572 05RIPLEY 3EQ 999 3 OPEN BRANCH FROM BUS 247572 TO BUS 247573 CKT 3 / 247572 05RIPLEY 3EQ 999 247573 05RIPLEY 13.0 3 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2019-OH028 | Need
AEP-VD41 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9972 | 0.89983 | 9.737 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD42 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9984 | 0.89125 | 10.715 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD43 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9929 | 0.8873 | 10.56 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD44 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9917 | 0.8877 | 10.4 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD45 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9929 | 0.8922 | 10.07 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD46 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9906 | 0.8922 | 9.84 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD47 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9916 | 0.8839 | 10.77 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD48 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9907 | 0.8842 | 10.65 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD49 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9916 | 0.9012 | 9.04 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD50 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244753 | 05BEALE | 69 | 205 | 0.9908 | 0.9008 | 9 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD51 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 1.0032 | 0.8454 | 15.78 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD52 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 1.0064 | 0.83777 | 16.863 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD53 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 1.017 | 0.92241 | 9.459 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD54 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 1.0081 | 0.82596 | 18.214 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD55 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9982 | 0.8203 | 17.79 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD56 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9982 | 0.8203 | 17.79 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD57 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9982 | 0.8254 | 17.28 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD58 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9982 | 0.8254 | 17.28 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD59 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9964 | 0.8207 | 17.57 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD60 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9964 | 0.8208 | 17.56 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD61 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9943 | 0.8254 | 16.89 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD62 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9943 | 0.8255 | 16.88 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD63 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9959 | 0.813 | 18.29 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD64 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9959 | 0.813 | 18.29 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD65 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9949 | 0.8131 | 18.18 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD66 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9949 | 0.8131 | 18.18 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD67 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9959 | 0.8393 | 15.66 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD68 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9959 | 0.8393 | 15.66 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD69 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242541 | 05APPLE2 | 138 | 205 | 0.9949 | 0.8387 | 15.62 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD70 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 0.9949 | 0.8387 | 15.62 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD71 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 1.0064 | 0.83778 | 16.862 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD72 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 1.017 | 0.92241 | 9.459 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD73 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242540 | 05APPLE1 | 138 | 205 | 1.0081 | 0.82596 | 18.214 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP016, AEP-2020-AP018 | Need
AEP-VD74 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8038 | 18.52 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD75 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8038 | 18.52 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD76 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.989 | 0.8032 | 18.58 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD77 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8303 | 16.39 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD78 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8303 | 16.39 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD79 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9942 | 0.8297 | 16.45 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD80 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244268 | 05MEDALLIN | 69 | 205 | 1.0067 | 0.8715 | 13.52 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD81 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244268 | 05MEDALLIN | 69 | 205 | 1.0067 | 0.8715 | 13.52 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD82 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244268 | 05MEDALLIN | 69 | 205 | 1.0067 | 0.8709 | 13.58 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD83 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244231 | 05DAMASCUS | 69 | 205 | 0.9946 | 0.8794 | 11.52 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD84 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244231 | 05DAMASCUS | 69 | 205 | 0.9946 | 0.8794 | 11.52 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD85 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247063 | 05ARROWHD | 69 | 205 | 1.0031 | 0.889 | 11.41 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD86 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247063 | 05ARROWHD | 69 | 205 | 1.0031 | 0.889 | 11.41 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD87 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244241 | 05HILLMAN | 69 | 205 | 1.0128 | 0.9001 | 11.27 | 8 | N-1-1 | AEP_P1-2_#11352_271 | OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD88 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244241 | 05HILLMAN | 69 | 205 | 1.0128 | 0.9001 | 11.27 | 8 | N-1-1 | AEP_P1-3_#11969_05ABINGD 138_1 | OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD89 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244231 | 05DAMASCUS | 69 | 205 | 0.9946 | 0.8788 | 11.58 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD90 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247063 | 05ARROWHD | 69 | 205 | 1.0031 | 0.8884 | 11.47 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD91 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244241 | 05HILLMAN | 69 | 205 | 1.0129 | 0.8995 | 11.34 | 8 | N-1-1 | AEP_P1-2_#5702_11457 | OPEN BRANCH FROM BUS 242533 TO BUS 242605 CKT 1 / 242533 05ABINGD 138 242605 05CLNCHR 138 1 OPEN BRANCH FROM BUS 242533 TO BUS 242861 CKT 1 / 242533 05ABINGD 138 242861 05ABINGDON 69.0 1 OPEN BRANCH FROM BUS 242861 TO BUS 244241 CKT 1 / 242861 05ABINGDON 69.0 244241 05HILLMAN 69.0 1 | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD92 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.8788 | 11.19 | 8 | FB | AEP_P4_#10335_05SALTV2 138_U | OPEN BRANCH FROM BUS 242566 TO BUS 242788 CKT 2 / 242566 05BROADF 138 242788 05SALTV1 138 2 OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 246766 CKT 1 / 242788 05SALTV1 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242788 TO BUS 242827 CKT 1 / 242788 05SALTV1 138 242827 05TAZEWE 138 1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD93 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.88092 | 10.978 | 8 | Single | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD94 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.88092 | 10.978 | 8 | Bus | AEP_P2-2_#10333_05SALTV2 138_2 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD95 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.88092 | 10.978 | 8 | FB | AEP_P4_#10333_05SALTV2 138_L | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD96 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.90772 | 8.298 | 8 | Line w/o Fault | AEP_P2-1_242789 05SALTV2 138 242885 05SALTVILL 69.0 1 | OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD97 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244236 | 05GLADE | 69 | 205 | 0.9907 | 0.90765 | 8.305 | 8 | Line w/o Fault | AEP_P2-1_242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 | OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD98 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9961 | 0.90493 | 9.117 | 8 | Single | AEP_P1-3_#11372_05SALTV2 138_1 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD99 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9961 | 0.90493 | 9.117 | 8 | Bus | AEP_P2-2_#10333_05SALTV2 138_2 | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD100 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9961 | 0.90493 | 9.117 | 8 | FB | AEP_P4_#10333_05SALTV2 138_L | OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD101 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247871 | 05OWENSDRIVE | 69 | 205 | 0.9961 | 0.90253 | 9.357 | 8 | FB | AEP_P4_#10335_05SALTV2 138_U | OPEN BRANCH FROM BUS 242566 TO BUS 242788 CKT 2 / 242566 05BROADF 138 242788 05SALTV1 138 2 OPEN BRANCH FROM BUS 242566 TO BUS 242789 CKT 1 / 242566 05BROADF 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 246766 CKT 1 / 242788 05SALTV1 138 246766 05ELKGAZ 138 1 OPEN BRANCH FROM BUS 242714 TO BUS 242789 CKT 1 / 242714 05MEADWV 138 242789 05SALTV2 138 1 OPEN BRANCH FROM BUS 242788 TO BUS 242789 CKT Z1 / 242788 05SALTV1 138 242789 05SALTV2 138 Z1 OPEN BRANCH FROM BUS 242788 TO BUS 242827 CKT 1 / 242788 05SALTV1 138 242827 05TAZEWE 138 1 OPEN BRANCH FROM BUS 242789 TO BUS 242885 CKT 1 / 242789 05SALTV2 138 242885 05SALTVILL 69.0 1 OPEN BRANCH FROM BUS 242885 TO BUS 244236 CKT 1 / 242885 05SALTVILL 69.0 244236 05GLADE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-AP025 | Need
AEP-VD102 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 1.0109 | 0.9179 | 9.3 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD103 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246213 | 05WOLFLAKE | 69 | 205 | 1.0109 | 0.9181 | 9.28 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD104 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246226 | 05ALBION Z | 69 | 205 | 1.0139 | 0.9211 | 9.28 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD105 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246226 | 05ALBION Z | 69 | 205 | 9.26 | 9.1674 | 9.26 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD106 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246216 | 05PHILIPSZ | 69 | 205 | 1.0161 | 0.9236 | 9.25 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD107 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246216 | 05PHILIPSZ | 69 | 205 | 1.0161 | 0.9237 | 9.24 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD108 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246184 | 05BRIMFLD8 | 69 | 205 | 1.0184 | 0.9261 | 9.23 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD109 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246184 | 05BRIMFLD8 | 69 | 205 | 1.0184 | 0.9263 | 9.21 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD110 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246204 | 05N KENDLV | 69 | 205 | 1.0209 | 0.9289 | 9.2 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-IM008, AEP-2019-IM015 | Need
AEP-VD111 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246200 | 05KENDALVI | 69 | 205 | 1.0224 | 0.9305 | 9.19 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-2_#7913 | OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD112 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246204 | 05N KENDLV | 69 | 205 | 1.0209 | 0.9291 | 9.18 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-IM008, AEP-2019-IM015 | Need
AEP-VD113 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246200 | 05KENDALVI | 69 | 205 | 1.0224 | 0.9306 | 9.18 | 8 | N-1-1 | AEP_P1-3_#11932_05ALBION 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 246180 CKT 1 / 243241 05ALBION 138 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246180 CKT 1 / 246179 05ALBION- 69.0 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246178 TO BUS 246180 CKT 1 / 246178 05ALBION 34.5 246180 05ALBIONEQ 999 1 OPEN BRANCH FROM BUS 246179 TO BUS 246226 CKT 1 / 246179 05ALBION- 69.0 246226 05ALBION Z 69.0 1 | AEP_P1-3_#12370_05KENDAL 138_1 | OPEN BRANCH FROM BUS 243241 TO BUS 243375 CKT 1 / 243241 05ALBION 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243251 TO BUS 243252 CKT 1 / 243251 05BIXLER 138 243252 05BIXLRT 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 243321 CKT 1 / 243252 05BIXLRT 138 243321 05KENDAL 138 1 OPEN BRANCH FROM BUS 243252 TO BUS 246769 CKT 1 / 243252 05BIXLRT 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243295 TO BUS 246769 CKT 1 / 243295 05GARRETT N 138 246769 05MINERR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 243375 CKT 1 / 243321 05KENDAL 138 243375 05SKINNR 138 1 OPEN BRANCH FROM BUS 243321 TO BUS 246200 CKT 3 / 243321 05KENDAL 138 246200 05KENDALVI 69.0 3 REMOVE SWSHUNT FROM BUS 243321 / 243321 05KENDAL 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD114 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.994 | 0.88967 | 10.433 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD115 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 1.0089 | 0.87367 | 13.523 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD116 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 1.0076 | 0.87258 | 13.502 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD117 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 1.0085 | 0.87496 | 13.354 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD118 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 1.0073 | 0.87856 | 12.874 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD119 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245778 | 05PANDORA | 69 | 205 | 0.996 | 0.91144 | 8.456 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD120 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9845 | 0.7758 | 20.87 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD121 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9858 | 0.7768 | 20.9 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD122 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9857 | 0.7789 | 20.68 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD123 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9853 | 0.785 | 20.03 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD124 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9909 | 0.8063 | 18.46 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD125 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9921 | 0.8075 | 18.46 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD126 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9919 | 0.8091 | 18.28 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD127 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9913 | 0.8141 | 17.72 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD128 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9839 | 0.7129 | 27.1 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD129 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9851 | 0.7137 | 27.14 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD130 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9852 | 0.716 | 26.92 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD131 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9857 | 0.7228 | 26.29 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD132 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245730 | 05CAIRO | 69 | 205 | 0.9863 | 0.8019 | 18.44 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD133 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.989 | 0.8053 | 18.37 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD134 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245732 | 05COLGRVE8 | 69 | 205 | 0.9905 | 0.8072 | 18.33 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD135 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245801 | 05PHILIPS2 | 69 | 205 | 0.9941 | 0.8117 | 18.24 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD136 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 69 | 205 | 0.996 | 0.8142 | 18.18 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD137 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244735 | 05GLANDORF | 69 | 205 | 0.9981 | 0.8322 | 16.59 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD138 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.978 | 0.8309 | 14.71 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD139 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245889 | 05MILLER8 | 69 | 205 | 0.998 | 0.8441 | 15.39 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD140 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245735 | 05CRAWFIS | 69 | 205 | 0.9964 | 0.8455 | 15.09 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD141 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245778 | 05PANDORA | 69 | 205 | 0.9972 | 0.8822 | 11.5 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD142 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245811 | 05NLEIPSIC | 69 | 205 | 0.9806 | 0.6843 | 29.63 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD143 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245792 | 05E.LEIPSC | 69 | 205 | 0.9818 | 0.6851 | 29.67 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD144 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245806 | 05DSCHLERT | 69 | 205 | 0.9817 | 0.6874 | 29.43 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD145 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245805 | 05LEIPSIC | 69 | 205 | 0.9813 | 0.6941 | 28.72 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD146 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245730 | 05CAIRO | 69 | 205 | 0.991 | 0.774 | 21.7 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD147 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245731 | 05COL GROV | 69 | 205 | 0.9834 | 0.7775 | 20.59 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD148 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245732 | 05COLGRVE8 | 69 | 205 | 0.9834 | 0.7793 | 20.41 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD149 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245801 | 05PHILIPS2 | 69 | 205 | 0.9834 | 0.7837 | 19.97 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD150 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245743 | 05E OTTAWA | 69 | 205 | 0.9845 | 0.7862 | 19.83 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD151 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244735 | 05GLANDORF | 69 | 205 | 0.9876 | 0.8071 | 18.05 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD152 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.9781 | 0.8195 | 15.86 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD153 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245889 | 05MILLER8 | 69 | 205 | 0.9883 | 0.8212 | 16.71 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD154 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245735 | 05CRAWFIS | 69 | 205 | 0.9857 | 0.8227 | 16.3 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD155 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245778 | 05PANDORA | 69 | 205 | 0.9877 | 0.8653 | 12.24 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD156 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.9865 | 0.69712 | 28.938 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD157 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9865 | 0.69713 | 28.937 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD158 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9863 | 0.69742 | 28.888 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD159 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9869 | 0.69888 | 28.802 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD160 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 1.0122 | 0.91889 | 9.331 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD161 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 1.0122 | 0.9189 | 9.33 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD162 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 1.012 | 0.91906 | 9.294 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD163 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 1.0127 | 0.92042 | 9.228 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD164 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.9926 | 0.82037 | 17.223 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD165 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9926 | 0.82038 | 17.222 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD166 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9926 | 0.82072 | 17.188 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD167 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9935 | 0.82235 | 17.115 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD168 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9649 | 0.721 | 24.39 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD169 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.965 | 0.7212 | 24.38 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD170 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9662 | 0.7224 | 24.38 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD171 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9732 | 0.7591 | 21.41 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD172 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9741 | 0.7602 | 21.39 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD173 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242957 | 05BASEL8 | 138 | 205 | 30.42 | 30.1158 | 30.42 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD174 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247000 | 05YELLOW CK1 | 138 | 205 | 0.9565 | 0.6524 | 30.41 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD175 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9565 | 0.6524 | 30.41 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD176 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9569 | 0.6527 | 30.42 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD177 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9583 | 0.6541 | 30.42 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD178 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9766 | 0.8714 | 10.52 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD179 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9763 | 0.8716 | 10.47 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD180 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9768 | 0.8729 | 10.39 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD181 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9768 | 0.8729 | 10.39 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD182 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.985 | 0.8708 | 11.42 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD183 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.9851 | 0.871 | 11.41 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD184 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9862 | 0.8722 | 11.4 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD185 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9863 | 0.8723 | 11.4 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD186 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247001 | 05YELLOW CK2 | 138 | 205 | 0.9635 | 0.7219 | 24.16 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD187 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.963 | 0.722 | 24.1 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD188 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9631 | 0.7233 | 23.98 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD189 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9631 | 0.7233 | 23.98 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD190 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245456 | 05NEWBERY | 138 | 205 | 0.963 | 0.7562 | 20.68 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD191 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246354 | 05E.LEIPSIC1 | 138 | 205 | 0.9631 | 0.7572 | 20.59 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD192 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9631 | 0.7573 | 20.58 | 8 | N-1-1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD193 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9869 | 0.69889 | 28.801 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD194 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 1.0127 | 0.92044 | 9.226 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD195 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9935 | 0.82237 | 17.113 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD196 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9662 | 0.7225 | 24.37 | 8 | N-1-1 | AEP_P1-2_#5245_17717 | OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 OPEN BRANCH FROM BUS 247000 TO BUS 247001 CKT Z1 / 247000 05YELLOW CK1 138 247001 05YELLOW CK2 138 Z1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD197 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9741 | 0.7602 | 21.39 | 8 | N-1-1 | AEP_P1-2_#14270_28878 | OPEN BRANCH FROM BUS 245456 TO BUS 247001 CKT 1 / 245456 05NEWBERY 138 247001 05YELLOW CK2 138 1 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD198 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243121 | 05ROCKPO | 138 | 205 | 0.9554 | 0.6513 | 30.41 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD199 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242993 | 05E.LEIPSIC2 | 138 | 205 | 0.9584 | 0.6542 | 30.42 | 8 | N-1-1 | AEP_P1-3_#15306_05E LIMA 138_3 | OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 245740 CKT 3 / 242989 05E LIMA 138 245740 05E LIMA 69.0 3 OPEN BRANCH FROM BUS 245730 TO BUS 245740 CKT 1 / 245730 05CAIRO 69.0 245740 05E LIMA 69.0 1 OPEN BRANCH FROM BUS 245740 TO BUS 247520 CKT 1 / 245740 05E LIMA 69.0 247520 05BEAVERDAM 69.0 1 REMOVE SWSHUNT FROM BUS 242989 / 242989 05E LIMA 138 | AEP_P1-2_#7097_4883 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with AEP-2020-OH020 | Need
AEP-VD200 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0205 | 0.8446 | 17.59 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD201 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 34.5 | 205 | 1.0169 | 0.8689 | 14.8 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD202 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 34.5 | 205 | 1.0226 | 0.8948 | 12.78 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD203 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244213 | 05SEWAGEPL | 34.5 | 205 | 1.0269 | 0.9145 | 11.24 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD204 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244185 | 05BORDENML | 34.5 | 205 | 1.0322 | 0.9204 | 11.18 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD205 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244184 | 05BLUERDGE | 34.5 | 205 | 1.0323 | 0.921 | 11.13 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD206 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244199 | 05KYLEHILL | 34.5 | 205 | 1.0195 | 0.9219 | 9.76 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD207 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244186 | 05CUMBRLND | 34.5 | 205 | 1.034 | 0.9256 | 10.84 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD208 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0121 | 0.8508 | 16.13 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD209 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 34.5 | 205 | 1.0028 | 0.8737 | 12.91 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD210 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 34.5 | 205 | 1.0141 | 0.899 | 11.51 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD211 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244213 | 05SEWAGEPL | 34.5 | 205 | 1.0169 | 0.918 | 9.89 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD212 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244185 | 05BORDENML | 34.5 | 205 | 1.014 | 0.9236 | 9.04 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD213 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244184 | 05BLUERDGE | 34.5 | 205 | 1.0145 | 0.9242 | 9.03 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD214 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244199 | 05KYLEHILL | 34.5 | 205 | 1.0136 | 0.9248 | 8.88 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD215 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244186 | 05CUMBRLND | 34.5 | 205 | 1.0186 | 0.9288 | 8.98 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD216 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242722 | 05MORLAN | 138 | 205 | 1.0028 | 0.905 | 9.78 | 8 | N-1-1 | AEP_P1-2_#5689_173 | OPEN BRANCH FROM BUS 242605 TO BUS 242793 CKT 1 / 242605 05CLNCHR 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242624 TO BUS 242793 CKT 1 / 242624 05DICKEN 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242722 TO BUS 245222 CKT 1 / 242722 05MORLAN 138 245222 05W.KINGS_BP 138 1 OPEN BRANCH FROM BUS 242793 TO BUS 245222 CKT 1 / 242793 05SEXTON 138 245222 05W.KINGS_BP 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD217 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.0068 | 0.7321 | 27.47 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD218 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242798 | 05SHORT | 138 | 205 | 1.0101 | 0.7334 | 27.67 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD219 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242739 | 05OREBANK | 138 | 205 | 1.0008 | 0.7435 | 25.73 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD220 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242798 | 05SHORT | 138 | 205 | 25.71 | 25.4529 | 25.71 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD221 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242722 | 05MORLAN | 138 | 205 | 0.9936 | 0.8943 | 9.93 | 8 | N-1-1 | AEP_P1-2_#5689_173 | OPEN BRANCH FROM BUS 242605 TO BUS 242793 CKT 1 / 242605 05CLNCHR 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242624 TO BUS 242793 CKT 1 / 242624 05DICKEN 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242722 TO BUS 245222 CKT 1 / 242722 05MORLAN 138 245222 05W.KINGS_BP 138 1 OPEN BRANCH FROM BUS 242793 TO BUS 245222 CKT 1 / 242793 05SEXTON 138 245222 05W.KINGS_BP 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD222 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242829 | 05TENNE1 | 138 | 205 | 0.9955 | 0.8964 | 9.91 | 8 | N-1-1 | AEP_P1-2_#5689_173 | OPEN BRANCH FROM BUS 242605 TO BUS 242793 CKT 1 / 242605 05CLNCHR 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242624 TO BUS 242793 CKT 1 / 242624 05DICKEN 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242722 TO BUS 245222 CKT 1 / 242722 05MORLAN 138 245222 05W.KINGS_BP 138 1 OPEN BRANCH FROM BUS 242793 TO BUS 245222 CKT 1 / 242793 05SEXTON 138 245222 05W.KINGS_BP 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD223 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242830 | 05TENNE2 | 138 | 205 | 0.9955 | 0.8964 | 9.91 | 8 | N-1-1 | AEP_P1-2_#5689_173 | OPEN BRANCH FROM BUS 242605 TO BUS 242793 CKT 1 / 242605 05CLNCHR 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242624 TO BUS 242793 CKT 1 / 242624 05DICKEN 138 242793 05SEXTON 138 1 OPEN BRANCH FROM BUS 242722 TO BUS 245222 CKT 1 / 242722 05MORLAN 138 245222 05W.KINGS_BP 138 1 OPEN BRANCH FROM BUS 242793 TO BUS 245222 CKT 1 / 242793 05SEXTON 138 245222 05W.KINGS_BP 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD224 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244212 | 05ROTHERWD | 34.5 | 205 | 1.0241 | 0.9215 | 10.26 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD225 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 34.5 | 205 | 1.0299 | 0.928 | 10.19 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD226 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244212 | 05ROTHERWD | 34.5 | 205 | 1.0131 | 0.9245 | 8.86 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD227 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 34.5 | 205 | 1.0189 | 0.931 | 8.79 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by b3099
AEP-VD228 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 0.9991 | 0.9123 | 8.68 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD229 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244315 | 05TOWNOF R | 69 | 205 | 0.9989 | 0.9124 | 8.65 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD230 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 1.0006 | 0.911 | 8.96 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD231 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244315 | 05TOWNOF R | 69 | 205 | 1.0005 | 0.9112 | 8.93 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD232 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 1.0006 | 0.9116 | 8.9 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD233 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244315 | 05TOWNOF R | 69 | 205 | 1.0005 | 0.9118 | 8.87 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD234 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 1.0021 | 0.9218 | 8.03 | 8 | N-1-1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD235 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 0.998 | 0.91 | 8.8 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD236 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244315 | 05TOWNOF R | 69 | 205 | 0.9978 | 0.9102 | 8.76 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD237 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244305 | 05RICHLNDS | 69 | 205 | 0.9986 | 0.917 | 8.16 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD238 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244315 | 05TOWNOF R | 69 | 205 | 0.9984 | 0.9171 | 8.13 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD239 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242654 | 05GRASCK | 138 | 205 | 0.9932 | 0.9042 | 8.9 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD240 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9932 | 0.9042 | 8.9 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD241 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242794 | 05SHACKM | 138 | 205 | 0.9952 | 0.9045 | 9.07 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD242 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242654 | 05GRASCK | 138 | 205 | 0.9932 | 0.8936 | 9.96 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD243 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9932 | 0.8936 | 9.96 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD244 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242794 | 05SHACKM | 138 | 205 | 0.9952 | 0.8939 | 10.13 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD245 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9847 | 0.8929 | 9.18 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD246 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9941 | 0.8916 | 10.25 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD247 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9941 | 0.8922 | 10.19 | 8 | N-1-1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD248 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9868 | 0.9026 | 8.42 | 8 | N-1-1 | AEP_P1-2_#5330_163 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD249 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242654 | 05GRASCK | 138 | 205 | 0.9864 | 0.9007 | 8.57 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD250 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242570 | 05BUCHAN | 138 | 205 | 0.9864 | 0.9007 | 8.57 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD251 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242794 | 05SHACKM | 138 | 205 | 0.9867 | 0.901 | 8.57 | 8 | N-1-1 | AEP_P1-3_#11387_05HALES1 138_1 | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 | AEP_P1-2_#5290_75 | OPEN BRANCH FROM BUS 242566 TO BUS 242600 CKT 1 / 242566 05BROADF 138 242600 05CLAYPL 138 1 OPEN BRANCH FROM BUS 242600 TO BUS 242766 CKT 1 / 242600 05CLAYPL 138 242766 05RICHLA 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3220
AEP-VD252 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246240 | 05FERGUSON | 69 | 205 | 1.0174 | 0.9236 | 9.38 | 8 | N-1-1 | AEP_P1-2_#11907_9398 | OPEN BRANCH FROM BUS 246245 TO BUS 246250 CKT 1 / 246245 05KINGSLAN 69.0 246250 05MAGLEY 69.0 1 | AEP_P1-3_#11948_05HILLCR 138_3 | OPEN BRANCH FROM BUS 243309 TO BUS 246124 CKT 3 / 243309 05HILLCR 138 246124 05HILLCREQ 999 3 OPEN BRANCH FROM BUS 246124 TO BUS 246242 CKT 3 / 246124 05HILLCREQ 999 246242 05HILLCRES 69.0 3 OPEN BRANCH FROM BUS 246240 TO BUS 246242 CKT 1 / 246240 05FERGUSON 69.0 246242 05HILLCRES 69.0 1 OPEN BRANCH FROM BUS 246242 TO BUS 246246 CKT 1 / 246242 05HILLCRES 69.0 246246 05KINNERK8 69.0 1 OPEN BRANCH FROM BUS 246148 TO BUS 246242 CKT 1 / 246148 05PETTIT AVE69.0 246242 05HILLCRES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3150
AEP-VD253 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246258 | 05PLEASNT | 69 | 205 | 1.0151 | 0.9268 | 8.83 | 8 | N-1-1 | AEP_P1-2_#11907_9398 | OPEN BRANCH FROM BUS 246245 TO BUS 246250 CKT 1 / 246245 05KINGSLAN 69.0 246250 05MAGLEY 69.0 1 | AEP_P1-3_#11948_05HILLCR 138_3 | OPEN BRANCH FROM BUS 243309 TO BUS 246124 CKT 3 / 243309 05HILLCR 138 246124 05HILLCREQ 999 3 OPEN BRANCH FROM BUS 246124 TO BUS 246242 CKT 3 / 246124 05HILLCREQ 999 246242 05HILLCRES 69.0 3 OPEN BRANCH FROM BUS 246240 TO BUS 246242 CKT 1 / 246240 05FERGUSON 69.0 246242 05HILLCRES 69.0 1 OPEN BRANCH FROM BUS 246242 TO BUS 246246 CKT 1 / 246242 05HILLCRES 69.0 246246 05KINNERK8 69.0 1 OPEN BRANCH FROM BUS 246148 TO BUS 246242 CKT 1 / 246148 05PETTIT AVE69.0 246242 05HILLCRES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3150
AEP-VD254 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9864 | 0.90297 | 8.343 | 8 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD255 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9883 | 0.90499 | 8.331 | 8 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD256 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9909 | 0.90775 | 8.315 | 8 | Line w/o Fault | AEP_P2-1_246165 05WALLEN 34.5 246269 05CARROLL 34.5 1 | OPEN BRANCH FROM BUS 246165 TO BUS 246269 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD257 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9841 | 0.7354 | 24.87 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD258 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.988 | 0.74 | 24.8 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD259 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9938 | 0.7468 | 24.7 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD260 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9939 | 0.7468 | 24.71 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD261 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9998 | 0.7538 | 24.6 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD262 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 1.0008 | 0.7342 | 26.66 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD263 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9987 | 0.7388 | 25.99 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD264 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 1.0009 | 0.7456 | 25.53 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD265 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 1.0009 | 0.7456 | 25.53 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD266 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 1.0063 | 0.7526 | 25.37 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD267 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0048 | 0.8141 | 19.07 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD268 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0135 | 0.8132 | 20.03 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD269 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0123 | 0.7956 | 21.67 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD270 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 21.67 | 21.4533 | 21.67 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD271 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0016 | 0.7958 | 20.58 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD272 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0017 | 0.7958 | 20.59 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD273 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9997 | 0.8886 | 11.11 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD274 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0041 | 0.8881 | 11.6 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD275 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0036 | 0.8743 | 12.93 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD276 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0036 | 0.8743 | 12.93 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD277 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9982 | 0.8744 | 12.38 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD278 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9983 | 0.8745 | 12.38 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD279 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9946 | 0.9073 | 8.73 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD280 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9971 | 0.91 | 8.71 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD281 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9991 | 0.9122 | 8.69 | 8 | N-1-1 | AEP_P1-2_#11898_1780 | OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246286 TO BUS 247259 CKT 1 / 246286 05LINC W 8 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD282 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9941 | 0.8962 | 9.79 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD283 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9941 | 0.8962 | 9.79 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD284 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9966 | 0.8989 | 9.77 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD285 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9966 | 0.899 | 9.76 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD286 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9986 | 0.9011 | 9.75 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD287 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9986 | 0.9012 | 9.74 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD288 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.99 | 0.8963 | 9.37 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD289 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.99 | 0.8963 | 9.37 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD290 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9925 | 0.899 | 9.35 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD291 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9925 | 0.899 | 9.35 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD292 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9945 | 0.9012 | 9.33 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD293 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9945 | 0.9013 | 9.32 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD294 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.6852 | 26.6 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD295 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9512 | 0.6852 | 26.6 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD296 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9723 | 0.686 | 28.63 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD297 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9723 | 0.686 | 28.63 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD298 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9671 | 0.8084 | 15.87 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD299 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9671 | 0.8084 | 15.87 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD300 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9796 | 0.8088 | 17.08 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD301 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9796 | 0.8089 | 17.07 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD302 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246906 | 05WOODLND8 | 69 | 205 | 1.0189 | 0.8385 | 18.04 | 8 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD303 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246904 | 05PERRY8 | 69 | 205 | 1.0214 | 0.8416 | 17.98 | 8 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD304 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246903 | 05DIEBOLD | 69 | 205 | 1.0233 | 0.8438 | 17.95 | 8 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD305 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246906 | 05WOODLND8 | 69 | 205 | 1.0136 | 0.8428 | 17.08 | 8 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD306 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246904 | 05PERRY8 | 69 | 205 | 1.0085 | 0.8457 | 16.28 | 8 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD307 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246903 | 05DIEBOLD | 69 | 205 | 1.0104 | 0.8479 | 16.25 | 8 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD308 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9681 | 0.8493 | 11.88 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD309 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9681 | 0.8493 | 11.88 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD310 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.97 | 0.8515 | 11.85 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD311 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.97 | 0.8515 | 11.85 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD312 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9727 | 0.8546 | 11.81 | 8 | N-1-1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD313 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9727 | 0.8546 | 11.81 | 8 | N-1-1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD314 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.978 | 0.8496 | 12.84 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD315 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.978 | 0.8496 | 12.84 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD316 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9799 | 0.8518 | 12.81 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD317 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9799 | 0.8518 | 12.81 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD318 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9826 | 0.8549 | 12.77 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD319 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9826 | 0.8549 | 12.77 | 8 | N-1-1 | AEP_P1-2_#11897_1778 | OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 247259 CKT 1 / 246279 05GATWY P8 69.0 247259 05LINCWTAPSS69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246292 CKT 1 / 246279 05GATWY P8 69.0 246292 05TRI-LAKE 69.0 1 OPEN BRANCH FROM BUS 246279 TO BUS 246280 CKT 1 / 246279 05GATWY P8 69.0 246280 05GATEWY P 34.5 1 REMOVE SWSHUNT FROM BUS 246279 / 246279 05GATWY P8 69.0 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD320 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246198 | 05HARLAN | 69 | 205 | 12.43 | 12.3057 | 12.43 | 8 | N-1-1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD321 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9791 | 0.8672 | 11.19 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD322 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9757 | 0.8672 | 10.85 | 8 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD323 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246198 | 05HARLAN | 69 | 205 | 1.0034 | 0.8918 | 11.16 | 8 | N-1-1 | AEP_P1-3_#12444_05ROB PK34 138_4 | OPEN BRANCH FROM BUS 245476 TO BUS 246157 CKT 1 / 245476 05ROB PK34 138 246157 05ROBPK4EQ 999 1 OPEN BRANCH FROM BUS 246157 TO BUS 246208 CKT 1 / 246157 05ROBPK4EQ 999 246208 05ROBISONP 69.0 1 OPEN BRANCH FROM BUS 246156 TO BUS 246157 CKT 1 / 246156 05ROBISONP 34.5 246157 05ROBPK4EQ 999 1 | AEP_P1-3_#11927_05WALLEN 138_2 | OPEN BRANCH FROM BUS 243389 TO BUS 246116 CKT 2 / 243389 05WALLEN 138 246116 05WALLENEQ 999 2 OPEN BRANCH FROM BUS 246116 TO BUS 246118 CKT 1 / 246116 05WALLENEQ 999 246118 05WALLEN 69.0 1 OPEN BRANCH FROM BUS 246116 TO BUS 246165 CKT 1 / 246116 05WALLENEQ 999 246165 05WALLEN 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD324 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9811 | 0.8894 | 9.17 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-3_#12145_05COLUMBIA 138_1 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 REMOVE LOAD T1 FROM BUS 243372 / 243372 05SATURN 138 T1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD325 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 0.9811 | 0.8894 | 9.17 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#10597_1731 | OPEN BRANCH FROM BUS 243263 TO BUS 243361 CKT 1 / 243263 05COLUMBIA 138 243361 05RABER 138 1 OPEN BRANCH FROM BUS 243361 TO BUS 243372 CKT 1 / 243361 05RABER 138 243372 05SATURN 138 1 OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 243263 TO BUS 246277 CKT 1 / 243263 05COLUMBIA 138 246277 05COLUMBIA1 34.5 1 OPEN BRANCH FROM BUS 246277 TO BUS 246295 CKT 1 / 246277 05COLUMBIA1 34.5 246295 05WHITLEY 34.5 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD326 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9953 | 0.6812 | 31.41 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD327 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.9928 | 0.6853 | 30.75 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD328 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9947 | 0.6913 | 30.34 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD329 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9948 | 0.6913 | 30.35 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD330 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 0.9972 | 0.6945 | 30.27 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD331 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 1.0001 | 0.6976 | 30.25 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD332 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0095 | 0.7808 | 22.87 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD333 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 1.0014 | 0.8689 | 13.25 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD334 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9925 | 0.8931 | 9.94 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD335 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.995 | 0.8958 | 9.92 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD336 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.997 | 0.898 | 9.9 | 8 | N-1-1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD337 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246271 | 05CLEVLND8 | 69 | 205 | 0.9841 | 0.6813 | 30.28 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD338 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246289 | 05RICHLND8 | 69 | 205 | 0.988 | 0.6854 | 30.26 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD339 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246293 | 05UMMEL 8 | 69 | 205 | 0.9938 | 0.6914 | 30.24 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD340 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246292 | 05TRI-LAKE | 69 | 205 | 0.9939 | 0.6914 | 30.25 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD341 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246286 | 05LINC W 8 | 69 | 205 | 1.0001 | 0.6946 | 30.55 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD342 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246279 | 05GATWY P8 | 69 | 205 | 0.9998 | 0.6977 | 30.21 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD343 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246295 | 05WHITLEY | 34.5 | 205 | 1.0048 | 0.7809 | 22.39 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD344 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246270 | 05CHURBUSC | 34.5 | 205 | 0.9997 | 0.8689 | 13.08 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD345 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246278 | 05EEL R 8 | 34.5 | 205 | 0.9911 | 0.8931 | 9.8 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD346 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246294 | 05UNION 8 | 34.5 | 205 | 0.9936 | 0.8958 | 9.78 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD347 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246269 | 05CARROLL | 34.5 | 205 | 0.9956 | 0.898 | 9.76 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#5601_2641 | OPEN BRANCH FROM BUS 243315 TO BUS 246282 CKT 1 / 243315 05ILLINO 138 246282 05ILLIN EQ 999 1 OPEN BRANCH FROM BUS 246282 TO BUS 246284 CKT 1 / 246282 05ILLIN EQ 999 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 243315 TO BUS 243316 CKT 1 / 243315 05ILLINO 138 243316 05INDUST PK1 138 1 OPEN BRANCH FROM BUS 243315 TO BUS 243377 CKT 1 / 243315 05ILLINO 138 243377 05SORENS 138 1 OPEN BRANCH FROM BUS 246110 TO BUS 246284 CKT 1 / 246110 05ABOITE 8 69.0 246284 05ILLINOIS 69.0 1 OPEN BRANCH FROM BUS 246284 TO BUS 247259 CKT 1 / 246284 05ILLINOIS 69.0 247259 05LINCWTAPSS69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD348 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243372 | 05SATURN | 138 | 205 | 1.0062 | 0.8171 | 18.91 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD349 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243361 | 05RABER | 138 | 205 | 1.0047 | 0.8174 | 18.73 | 8 | N-1-1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD350 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243372 | 05SATURN | 138 | 205 | 0.9807 | 0.8171 | 16.36 | 8 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD351 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243361 | 05RABER | 138 | 205 | 0.981 | 0.8174 | 16.36 | 8 | N-1-1 | AEP_P1-2_#10596 | OPEN BRANCH FROM BUS 243372 TO BUS 243377 CKT 1 / 243372 05SATURN 138 243377 05SORENS 138 1 | AEP_P1-2_#5498_1722 | OPEN BRANCH FROM BUS 243263 TO BUS 246276 CKT 2 / 243263 05COLUMBIA 138 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246274 TO BUS 246276 CKT 2 / 246274 05COLUMBIA 69.0 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 246275 TO BUS 246276 CKT 2 / 246275 05COLUMBIA2 34.5 246276 05COLUMB2 EQ 999 2 OPEN BRANCH FROM BUS 243263 TO BUS 255163 CKT 1 / 243263 05COLUMBIA 138 255163 17NORTHEAST 138 1 OPEN BRANCH FROM BUS 246271 TO BUS 246274 CKT 1 / 246271 05CLEVLND8 69.0 246274 05COLUMBIA 69.0 1 OPEN BRANCH FROM BUS 246274 TO BUS 246279 CKT 1 / 246274 05COLUMBIA 69.0 246279 05GATWY P8 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3151
AEP-VD352 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244899 | 05SCARBRO | 46 | 205 | 1.0113 | 0.91613 | 9.517 | 8 | FB | AEP_P4_#7808_05BRADL1 138_E | OPEN BRANCH FROM BUS 242564 TO BUS 244877 CKT 1 / 242564 05BRADL1 138 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 244380 TO BUS 244877 CKT 1 / 244380 05BRADLEY 69.0 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 244876 TO BUS 244877 CKT 1 / 244876 05BRADLEY 46.0 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 242564 TO BUS 242565 CKT Z1 / 242564 05BRADL1 138 242565 05BRADL2 138 Z1 OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 247826 CKT 1 / 242564 05BRADL1 138 247826 05MOLLYS CRK 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 242758 CKT 1 / 242564 05BRADL1 138 242758 05POLEYD 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 REMOVE SWSHUNT FROM BUS 242564 / 242564 05BRADL1 138 OPEN BRANCH FROM BUS 244380 TO BUS 244442 CKT 1 / 244380 05BRADLEY 69.0 244442 05PRINCE 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD353 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9973 | 0.89921 | 9.809 | 8 | FB | AEP_P4_#7808_05BRADL1 138_E | OPEN BRANCH FROM BUS 242564 TO BUS 244877 CKT 1 / 242564 05BRADL1 138 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 244380 TO BUS 244877 CKT 1 / 244380 05BRADLEY 69.0 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 244876 TO BUS 244877 CKT 1 / 244876 05BRADLEY 46.0 244877 05BRDLEYEQ 999 1 OPEN BRANCH FROM BUS 242564 TO BUS 242565 CKT Z1 / 242564 05BRADL1 138 242565 05BRADL2 138 Z1 OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 247826 CKT 1 / 242564 05BRADL1 138 247826 05MOLLYS CRK 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242564 TO BUS 242758 CKT 1 / 242564 05BRADL1 138 242758 05POLEYD 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 REMOVE SWSHUNT FROM BUS 242564 / 242564 05BRADL1 138 OPEN BRANCH FROM BUS 244380 TO BUS 244442 CKT 1 / 244380 05BRADLEY 69.0 244442 05PRINCE 69.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD354 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245344 | 05SAN CAST | 34.5 | 205 | 1.0218 | 0.87298 | 14.882 | 8 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD355 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245346 | 05STILLWL8 | 34.5 | 205 | 1.0127 | 0.88441 | 12.829 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD356 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0201 | 0.89287 | 12.723 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD357 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245785 | 05SHAWTWN8 | 34.5 | 205 | 0.9889 | 0.85832 | 13.058 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD358 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0199 | 0.89294 | 12.696 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD359 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245328 | 05JACKSON8 | 34.5 | 205 | 1.01 | 0.88383 | 12.617 | 8 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD360 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245349 | 05TUNNHIL8 | 34.5 | 205 | 0.9958 | 0.8842 | 11.16 | 8 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD361 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245346 | 05STILLWL8 | 34.5 | 205 | 1.0127 | 0.90662 | 10.608 | 8 | Single | AEP_P1-2_#14822 | OPEN BRANCH FROM BUS 245330 TO BUS 245343 CKT 1 / 245330 05KILBUCK 34.5 245343 05S MILLBR 34.5 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD362 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0201 | 0.91469 | 10.541 | 8 | Single | AEP_P1-2_#14822 | OPEN BRANCH FROM BUS 245330 TO BUS 245343 CKT 1 / 245330 05KILBUCK 34.5 245343 05S MILLBR 34.5 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD363 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245331 | 05KILBUCK8 | 34.5 | 205 | 1.0199 | 0.91477 | 10.513 | 8 | Single | AEP_P1-2_#14822 | OPEN BRANCH FROM BUS 245330 TO BUS 245343 CKT 1 / 245330 05KILBUCK 34.5 245343 05S MILLBR 34.5 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD364 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244629 | 05CONSOL MTR | 46 | 205 | 0.9967 | 0.90969 | 8.701 | 8 | FB | AEP_P4_#9507_05BEAVER CR2 138_P | OPEN BRANCH FROM BUS 243656 TO BUS 243671 CKT 1 / 243656 05BEAVC1EQ 999 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243656 TO BUS 243708 CKT 1 / 243656 05BEAVC1EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243656 TO BUS 243808 CKT 1 / 243656 05BEAVC1EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 245913 CKT 1 / 243671 05BEAVER CR1 138 245913 05KEWANEE 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 243683 CKT 1 / 243671 05BEAVER CR1 138 243683 05CONSTP 138 1 OPEN BRANCH FROM BUS 242645 TO BUS 243671 CKT 1 / 242645 05FREMO2 138 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 243671 / 243671 05BEAVER CR1 138 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3160 Associated with S2188
AEP-VD365 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243761 | 05SPRINGFK | 46 | 205 | 0.9968 | 0.90979 | 8.701 | 8 | FB | AEP_P4_#9507_05BEAVER CR2 138_P | OPEN BRANCH FROM BUS 243656 TO BUS 243671 CKT 1 / 243656 05BEAVC1EQ 999 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243656 TO BUS 243708 CKT 1 / 243656 05BEAVC1EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243656 TO BUS 243808 CKT 1 / 243656 05BEAVC1EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 245913 CKT 1 / 243671 05BEAVER CR1 138 245913 05KEWANEE 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 243683 CKT 1 / 243671 05BEAVER CR1 138 243683 05CONSTP 138 1 OPEN BRANCH FROM BUS 242645 TO BUS 243671 CKT 1 / 242645 05FREMO2 138 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 243671 / 243671 05BEAVER CR1 138 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3160 Associated with S2188
AEP-VD366 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244592 | 05BURTON | 46 | 205 | 1.0152 | 0.92899 | 8.621 | 8 | FB | AEP_P4_#9507_05BEAVER CR2 138_P | OPEN BRANCH FROM BUS 243656 TO BUS 243671 CKT 1 / 243656 05BEAVC1EQ 999 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243656 TO BUS 243708 CKT 1 / 243656 05BEAVC1EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243656 TO BUS 243808 CKT 1 / 243656 05BEAVC1EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 245913 CKT 1 / 243671 05BEAVER CR1 138 245913 05KEWANEE 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 243683 CKT 1 / 243671 05BEAVER CR1 138 243683 05CONSTP 138 1 OPEN BRANCH FROM BUS 242645 TO BUS 243671 CKT 1 / 242645 05FREMO2 138 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 243671 / 243671 05BEAVER CR1 138 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3160 Associated with S2188
AEP-VD367 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244603 | 05GARRETT | 46 | 205 | 0.9987 | 0.91308 | 8.562 | 8 | FB | AEP_P4_#9507_05BEAVER CR2 138_P | OPEN BRANCH FROM BUS 243656 TO BUS 243671 CKT 1 / 243656 05BEAVC1EQ 999 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243656 TO BUS 243708 CKT 1 / 243656 05BEAVC1EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243656 TO BUS 243808 CKT 1 / 243656 05BEAVC1EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 245913 CKT 1 / 243671 05BEAVER CR1 138 245913 05KEWANEE 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 243683 CKT 1 / 243671 05BEAVER CR1 138 243683 05CONSTP 138 1 OPEN BRANCH FROM BUS 242645 TO BUS 243671 CKT 1 / 242645 05FREMO2 138 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 243671 / 243671 05BEAVER CR1 138 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project Reliability Violations on Transmission Facilities Below 200 kV exclusion | Solved by B3160 Associated with S2188
AEP-VD368 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9972 | 0.89845 | 9.875 | 8 | Bus | AEP_P2-2_#13751_05PAX BRANCH46.0_2 | OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 / 247208 05MOSSYCRK 46.0 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 244899 TO BUS 247334 CKT 1 / 244899 05SCARBRO 46.0 247334 05PAX BRANCH46.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD369 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9972 | 0.89845 | 9.875 | 8 | FB | AEP_P4_#13751_05PAX BRANCH46.0_B | OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 / 247208 05MOSSYCRK 46.0 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 244899 TO BUS 247334 CKT 1 / 244899 05SCARBRO 46.0 247334 05PAX BRANCH46.0 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD370 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9972 | 0.89864 | 9.856 | 8 | Line w/o Fault | AEP_P2-1_247208 05MOSSYCRK 46.0 247334 05PAX BRANCH 46.0 1 | OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD371 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9972 | 0.89864 | 9.856 | 8 | Line w/o Fault | AEP_P2-1_247206 05EKINGS Z 46.0 247208 05MOSSYCRK 46.0 1 | OPEN BRANCH FROM BUS 247206 TO BUS 247208 CKT 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD372 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245352 | 05WARSAW | 34.5 | 205 | 1.0089 | 0.91117 | 9.773 | 8 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD373 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245329 | 05JEFFRSN8 | 34.5 | 205 | 1.0115 | 0.91834 | 9.316 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD374 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245757 | 05MCCOMB OP | 34.5 | 205 | 0.9884 | 0.89613 | 9.227 | 8 | Tower | AEP_P7-1_#10984 | OPEN BRANCH FROM BUS 239269 TO BUS 242993 CKT 1 / 239269 02RICHLJ 138 242993 05E.LEIPSIC2 138 1 OPEN BRANCH FROM BUS 242957 TO BUS 243080 CKT 1 / 242957 05BASEL8 138 243080 05RILEYC 138 1 OPEN BRANCH FROM BUS 242989 TO BUS 243083 CKT 1 / 242989 05E LIMA 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 243083 CKT 1 / 243080 05RILEYC 138 243083 05CAMPSS 138 1 OPEN BRANCH FROM BUS 243083 TO BUS 243121 CKT 1 / 243083 05CAMPSS 138 243121 05ROCKPO 138 1 OPEN BRANCH FROM BUS 243080 TO BUS 247000 CKT 1 / 243080 05RILEYC 138 247000 05YELLOW CK1 138 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD375 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245329 | 05JEFFRSN8 | 34.5 | 205 | 1.0115 | 0.92777 | 8.373 | 8 | FB | AEP_P4_#9049_05SCOSHC 138_I | OPEN BRANCH FROM BUS 243056 TO BUS 243094 CKT 1 / 243056 05NEWCOM 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243094 TO BUS 245342 CKT 1 / 243094 05SCOSHC 138 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 243094 TO BUS 245341 CKT 1 / 243094 05SCOSHC 138 245341 05S COSHCT 34.5 1 OPEN BRANCH FROM BUS 245319 TO BUS 245342 CKT 1 / 245319 05COSHCTN 69.0 245342 05S COSHCT 69.0 1 OPEN BRANCH FROM BUS 245341 TO BUS 245342 CKT 3 / 245341 05S COSHCT 34.5 245342 05S COSHCT 69.0 3 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD376 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0185 | 0.904 | 11.45 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD377 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0184 | 0.9035 | 11.49 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD378 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0211 | 0.9088 | 11.23 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD379 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.021 | 0.9083 | 11.27 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD380 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0235 | 0.9132 | 11.03 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD381 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0234 | 0.9127 | 11.07 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD382 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0008 | 0.9191 | 8.17 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD383 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0007 | 0.9187 | 8.2 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD384 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 1.0042 | 0.9235 | 8.07 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD385 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 1.004 | 0.9231 | 8.09 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD386 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 13.58 | 13.4442 | 13.58 | 8 | N-1-1 | AEP_P1-2_#11884_1789 | OPEN BRANCH FROM BUS 246464 TO BUS 247020 CKT 1 / 246464 05LAKE ST 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246466 TO BUS 247020 CKT 1 / 246466 05LAKEHEAD 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD387 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0273 | 0.9027 | 12.46 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD388 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.0271 | 0.9028 | 12.43 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD389 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0249 | 0.9007 | 12.42 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD390 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0247 | 0.9008 | 12.39 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD391 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0221 | 0.8985 | 12.36 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD392 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.022 | 0.8986 | 12.34 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD393 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 1.0079 | 0.8849 | 12.3 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD394 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 1.0077 | 0.885 | 12.27 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD395 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0044 | 0.8897 | 11.47 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD396 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246466 | 05LAKEHEAD | 69 | 205 | 1.0043 | 0.8898 | 11.45 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD397 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246463 | 05LAKE ST | 34.5 | 205 | 1.024 | 0.9258 | 9.82 | 8 | N-1-1 | AEP_P1-2_#11884_1789 | OPEN BRANCH FROM BUS 246464 TO BUS 247020 CKT 1 / 246464 05LAKE ST 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246466 TO BUS 247020 CKT 1 / 246466 05LAKEHEAD 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD398 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246488 | 05SIMPLICT | 34.5 | 205 | 1.0215 | 0.9273 | 9.42 | 8 | N-1-1 | AEP_P1-2_#11884_1789 | OPEN BRANCH FROM BUS 246464 TO BUS 247020 CKT 1 / 246464 05LAKE ST 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246466 TO BUS 247020 CKT 1 / 246466 05LAKEHEAD 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD399 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246428 | 05NILECTY | 34.5 | 205 | 1.0187 | 0.9292 | 8.95 | 8 | N-1-1 | AEP_P1-2_#11884_1789 | OPEN BRANCH FROM BUS 246464 TO BUS 247020 CKT 1 / 246464 05LAKE ST 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246466 TO BUS 247020 CKT 1 / 246466 05LAKEHEAD 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD400 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246464 | 05LAKE ST | 69 | 205 | 0.9985 | 0.9149 | 8.36 | 8 | N-1-1 | AEP_P1-2_#12259 | OPEN BRANCH FROM BUS 246432 TO BUS 246997 CKT 1 / 246432 05BUCHANAN 69.0 246997 05PLETCHER 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD401 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245378 | 05GLENMONT | 34.5 | 205 | 1.0126 | 0.8843 | 12.83 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD402 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245378 | 05GLENMONT | 34.5 | 205 | 1.0126 | 0.90651 | 10.609 | 8 | Single | AEP_P1-2_#14822 | OPEN BRANCH FROM BUS 245330 TO BUS 245343 CKT 1 / 245330 05KILBUCK 34.5 245343 05S MILLBR 34.5 1 |  |  | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD403 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0189 | 0.9044 | 11.45 | 8 | N-1-1 | AEP_P1-2_#6125_14517 | OPEN BRANCH FROM BUS 243322 TO BUS 243360 CKT 1 / 243322 05KENZIE 138 243360 05POKAGO 138 1 OPEN BRANCH FROM BUS 243355 TO BUS 246764 CKT 1 / 243355 05ONTWA8 SS 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246764 CKT 1 / 243360 05POKAGO 138 246764 05SAUKTR 138 1 OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD404 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0188 | 0.9039 | 11.49 | 8 | N-1-1 | AEP_P1-3_#12428_05POKAGO 138_1 | OPEN BRANCH FROM BUS 243360 TO BUS 246480 CKT 1 / 243360 05POKAGO 138 246480 05POKAGON 69.0 1 | AEP_P1-3_#12402_05NILES 69.0_1 | OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246422 TO BUS 246477 CKT 1 / 246422 05MAYFLWER 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246476 TO BUS 246477 CKT 1 / 246476 05NILES 34.5 246477 05NILES 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD405 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0226 | 0.899 | 12.36 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD406 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0224 | 0.8991 | 12.33 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD407 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246477 | 05NILES | 69 | 205 | 1.0072 | 0.8974 | 10.98 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD408 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246477 | 05NILES | 69 | 205 | 1.007 | 0.8974 | 10.96 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD409 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246430 | 05BUCHAN S | 69 | 205 | 1.0064 | 0.9161 | 9.03 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD410 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246430 | 05BUCHAN S | 69 | 205 | 1.0063 | 0.9162 | 9.01 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD411 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246476 | 05NILES | 34.5 | 205 | 1.0191 | 0.9297 | 8.94 | 8 | N-1-1 | AEP_P1-2_#11884_1789 | OPEN BRANCH FROM BUS 246464 TO BUS 247020 CKT 1 / 246464 05LAKE ST 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246466 TO BUS 247020 CKT 1 / 246466 05LAKEHEAD 69.0 247020 05MANDR SS 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 247020 CKT 1 / 246477 05NILES 69.0 247020 05MANDR SS 69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD412 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246434 | 05CLARKEQUIP | 34.5 | 205 | 1.0305 | 0.9429 | 8.76 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD413 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246434 | 05CLARKEQUIP | 34.5 | 205 | 1.0304 | 0.9429 | 8.75 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD414 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 69 | 205 | 1.0079 | 0.9227 | 8.52 | 8 | N-1-1 | AEP_P1-2_#11889_1793 | OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD415 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246432 | 05BUCHANAN | 69 | 205 | 1.0078 | 0.9228 | 8.5 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#11878_1790 | OPEN BRANCH FROM BUS 246464 TO BUS 246480 CKT 1 / 246464 05LAKE ST 69.0 246480 05POKAGON 69.0 1 | No | Part 4: Voltage Limits | Solved by existing baseline project | Solved by B3160
AEP-VD416 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247559 | 05JARRETT | 46 | 205 | 1.0219 | 0.8712 | 15.07 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1996, driven by S1996, additional scope of S1996 needed to address this | Submitted for inclusion in Local Plan
AEP-VD417 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247559 | 05JARRETT | 46 | 205 | 0.9881 | 0.8701 | 11.8 | 8 | N-1-1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1996, driven by S1996, additional scope of S1996 needed to address this | Submitted for inclusion in Local Plan
AEP-VD418 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244833 | 05HARTLAND | 46 | 205 | 0.9981 | 0.9101 | 8.8 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1996, driven by S1996, additional scope of S1996 needed to address this | Submitted for inclusion in Local Plan
AEP-VD419 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244832 | 05FRANKSBR | 46 | 205 | 0.9977 | 0.9114 | 8.63 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1996, driven by S1996, additional scope of S1996 needed to address this | Submitted for inclusion in Local Plan
AEP-VD420 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244835 | 05MAMMOTH | 46 | 205 | 1.008 | 0.926 | 8.2 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S1996, driven by S1996, additional scope of S1996 needed to address this | Submitted for inclusion in Local Plan
AEP-VD421 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245330 | 05KILBUCK | 34.5 | 205 | 1.0241 | 0.94337 | 8.073 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VD422 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245346 | 05STILLWL8 | 34.5 | 205 | 1.0185 | 0.93728 | 8.122 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VD423 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245378 | 05GLENMONT | 34.5 | 205 | 1.0184 | 0.93717 | 8.123 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2149 | Submitted for inclusion in Local Plan
AEP-VD424 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246984 | 05HEMLOCK | 69 | 205 | 1.0108 | 0.8958 | 11.5 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD425 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246984 | 05HEMLOCK | 69 | 205 | 1.0093 | 0.9261 | 8.32 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD426 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246984 | 05HEMLOCK | 69 | 205 | 0.9899 | 0.8956 | 9.43 | 8 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD427 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9894 | 0.8166 | 17.28 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD428 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9578 | 0.8163 | 14.15 | 8 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD429 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9901 | 0.8635 | 12.66 | 8 | N-1-1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD430 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246735 | 05COOLVL | 69 | 205 | 0.9641 | 0.8605 | 10.36 | 8 | N-1-1 | AEP_P1-2_#11465 | OPEN BRANCH FROM BUS 242703 TO BUS 243947 CKT 1 / 242703 05LEON A 138 243947 05RIPLEY 138 1 | AEP_P1-2_#11396_2874 | OPEN BRANCH FROM BUS 244762 TO BUS 247014 CKT 1 / 244762 05RAVENSWD 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244754 TO BUS 247014 CKT 1 / 244754 05COTAGEVI 69.0 247014 05SARAH LNSS69.0 1 OPEN BRANCH FROM BUS 244761 TO BUS 247014 CKT 1 / 244761 05RACINE 69.0 247014 05SARAH LNSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2178 | Submitted for inclusion in Local Plan
AEP-VD431 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.87854 | 11.026 | 8 | FB | AEP_P4_#13164_05FIELDALE 69.0_E | OPEN BRANCH FROM BUS 243799 TO BUS 243963 CKT 1 / 243799 05FIELDALE2 138 243963 05FIELD EQ 999 1 OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243963 TO BUS 243964 CKT 1 / 243963 05FIELD EQ 999 243964 05FIELDALE 34.5 1 OPEN BRANCH FROM BUS 243946 TO BUS 243965 CKT 1 / 243946 05BASSETT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243965 CKT 1 / 243959 05DUPONT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243996 CKT 1 / 243965 05FIELDALE 69.0 243996 05STNLY TW 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 REMOVE SWSHUNT FROM BUS 243965 / 243965 05FIELDALE 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD432 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.87856 | 11.024 | 8 | FB | AEP_P4_#13161_05FIELDALE 69.0_C | OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243946 TO BUS 243965 CKT 1 / 243946 05BASSETT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243965 CKT 1 / 243959 05DUPONT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243996 CKT 1 / 243965 05FIELDALE 69.0 243996 05STNLY TW 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 REMOVE SWSHUNT FROM BUS 243965 / 243965 05FIELDALE 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD433 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.87894 | 10.986 | 8 | FB | AEP_P4_#15363_05FIELDALE 69.0_F | OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243946 TO BUS 243965 CKT 1 / 243946 05BASSETT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243965 CKT 1 / 243959 05DUPONT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243985 CKT 1 / 243959 05DUPONT 69.0 243985 05RICH ACR 69.0 1 OPEN BRANCH FROM BUS 243985 TO BUS 243986 CKT 1 / 243985 05RICH ACR 69.0 243986 05RIDGEWAY 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243996 CKT 1 / 243965 05FIELDALE 69.0 243996 05STNLY TW 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 REMOVE SWSHUNT FROM BUS 243965 / 243965 05FIELDALE 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD434 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.87874 | 11.006 | 8 | FB | AEP_P4_#13163_05FIELDALE 69.0_D | OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243946 TO BUS 243965 CKT 1 / 243946 05BASSETT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243946 TO BUS 244000 CKT 1 / 243946 05BASSETT 69.0 244000 05W.BASSET 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243965 CKT 1 / 243959 05DUPONT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243996 CKT 1 / 243965 05FIELDALE 69.0 243996 05STNLY TW 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 REMOVE SWSHUNT FROM BUS 243965 / 243965 05FIELDALE 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD435 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.8804 | 10.84 | 8 | FB | AEP_P4_#13162_05FIELDALE 69.0_G | OPEN BRANCH FROM BUS 243963 TO BUS 243965 CKT 1 / 243963 05FIELD EQ 999 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243946 TO BUS 243965 CKT 1 / 243946 05BASSETT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243959 TO BUS 243965 CKT 1 / 243959 05DUPONT 69.0 243965 05FIELDALE 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243996 CKT 1 / 243965 05FIELDALE 69.0 243996 05STNLY TW 69.0 1 OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 OPEN BRANCH FROM BUS 243996 TO BUS 244000 CKT 1 / 243996 05STNLY TW 69.0 244000 05W.BASSET 69.0 1 REMOVE SWSHUNT FROM BUS 243965 / 243965 05FIELDALE 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD436 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244007 | 05WOOLWINE | 69 | 205 | 0.9976 | 0.83574 | 16.186 | 8 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD437 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.87975 | 10.905 | 8 | Single | AEP_P1-2_#11292_292 | OPEN BRANCH FROM BUS 243965 TO BUS 243997 CKT 1 / 243965 05FIELDALE 69.0 243997 05STUART A 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD438 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243997 | 05STUART A | 69 | 205 | 0.9888 | 0.88298 | 10.582 | 8 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD439 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 23.86 | 23.6214 | 23.86 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD440 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 1.0057 | 0.7836 | 22.21 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD441 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244166 | 05GALAX1 | 69 | 205 | 1.0124 | 0.8215 | 19.09 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD442 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244182 | 05GALAX2 | 69 | 205 | 1.0124 | 0.8216 | 19.08 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD443 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244168 | 05INDEPEND | 69 | 205 | 1.0011 | 0.8183 | 18.28 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD444 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244166 | 05GALAX1 | 69 | 205 | 1 | 0.8283 | 17.17 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD445 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244182 | 05GALAX2 | 69 | 205 | 1 | 0.8284 | 17.16 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD446 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244168 | 05INDEPEND | 69 | 205 | 0.9871 | 0.8254 | 16.17 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD447 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 1.0007 | 0.8274 | 17.33 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD448 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244166 | 05GALAX1 | 69 | 205 | 0.9918 | 0.8616 | 13.02 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD449 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244182 | 05GALAX2 | 69 | 205 | 0.9918 | 0.8617 | 13.01 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD450 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244168 | 05INDEPEND | 69 | 205 | 0.9849 | 0.8645 | 12.04 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD451 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 1.0125 | 0.8261 | 18.64 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD452 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244166 | 05GALAX1 | 69 | 205 | 1.0058 | 0.8606 | 14.52 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD453 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244182 | 05GALAX2 | 69 | 205 | 1.0058 | 0.8607 | 14.51 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD454 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244168 | 05INDEPEND | 69 | 205 | 1.0003 | 0.8636 | 13.67 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD455 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242848 | 05WILLGP | 138 | 205 | 1.0115 | 0.7301 | 28.14 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD456 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242675 | 05HUFFMN | 138 | 205 | 1.013 | 0.732 | 28.1 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD457 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242755 | 05PIPERS | 138 | 205 | 1.0109 | 0.7313 | 27.96 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD458 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245117 | 05W.CARROLL | 138 | 205 | 1.0104 | 0.7324 | 27.8 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD459 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244287 | 05WOLF GLADE | 138 | 205 | 1.0103 | 0.7348 | 27.55 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD460 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242848 | 05WILLGP | 138 | 205 | 1.0101 | 0.7362 | 27.39 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD461 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242675 | 05HUFFMN | 138 | 205 | 1.0116 | 0.7381 | 27.35 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD462 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242755 | 05PIPERS | 138 | 205 | 1.0092 | 0.7374 | 27.18 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD463 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245117 | 05W.CARROLL | 138 | 205 | 1.0088 | 0.7385 | 27.03 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD464 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244287 | 05WOLF GLADE | 138 | 205 | 1.0089 | 0.7409 | 26.8 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD465 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242543 | 05AUSTIN | 138 | 205 | 1.0258 | 0.9368 | 8.9 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD466 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242848 | 05WILLGP | 138 | 205 | 0.9994 | 0.7772 | 22.22 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD467 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242755 | 05PIPERS | 138 | 205 | 0.9993 | 0.7794 | 21.99 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD468 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242675 | 05HUFFMN | 138 | 205 | 1.0011 | 0.7794 | 22.17 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD469 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245117 | 05W.CARROLL | 138 | 205 | 0.9993 | 0.7809 | 21.84 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD470 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242848 | 05WILLGP | 138 | 205 | 1.0045 | 0.7758 | 22.87 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD471 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242755 | 05PIPERS | 138 | 205 | 1.0041 | 0.778 | 22.61 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD472 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242675 | 05HUFFMN | 138 | 205 | 1.0061 | 0.778 | 22.81 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD473 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245117 | 05W.CARROLL | 138 | 205 | 1.0037 | 0.7795 | 22.42 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD474 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0415 | 0.81181 | 22.969 | 8 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD475 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243966 | 05FLOYD | 34.5 | 205 | 1.0469 | 0.91158 | 13.532 | 8 | Line w/o Fault | AEP_P2-1_242640 05FLOYD 138 243969 05FLOYD EQ 999 1 | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD476 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 1.0083 | 0.8034 | 20.49 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD477 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 0.9962 | 0.8102 | 18.6 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD478 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 0.9912 | 0.8494 | 14.18 | 8 | N-1-1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD479 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 1.0049 | 0.8483 | 15.66 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#5448_128 | OPEN BRANCH FROM BUS 242675 TO BUS 242684 CKT 1 / 242675 05HUFFMN 138 242684 05J.FERR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2179 | Submitted for inclusion in Local Plan
AEP-VD480 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244616 | 05MCKINNEY | 46 | 205 | 0.9981 | 0.91771 | 8.039 | 8 | FB | AEP_P4_#9507_05BEAVER CR2 138_P | OPEN BRANCH FROM BUS 243656 TO BUS 243671 CKT 1 / 243656 05BEAVC1EQ 999 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243656 TO BUS 243708 CKT 1 / 243656 05BEAVC1EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243656 TO BUS 243808 CKT 1 / 243656 05BEAVC1EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 245913 CKT 1 / 243671 05BEAVER CR1 138 245913 05KEWANEE 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 243683 CKT 1 / 243671 05BEAVER CR1 138 243683 05CONSTP 138 1 OPEN BRANCH FROM BUS 242645 TO BUS 243671 CKT 1 / 242645 05FREMO2 138 243671 05BEAVER CR1 138 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 243671 / 243671 05BEAVER CR1 138 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VD481 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243691 | 05HAYSBR | 138 | 205 | 0.9757 | 0.8824 | 9.33 | 8 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VD482 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244008 | 05STANVILLE1 | 138 | 205 | 0.981 | 0.8884 | 9.26 | 8 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VD483 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242915 | 05STANVILLE2 | 138 | 205 | 0.981 | 0.8884 | 9.26 | 8 | N-1-1 | AEP_P1-2_#5995_13817 | OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 | AEP_P1-2_#5996_26117 | OPEN BRANCH FROM BUS 243684 TO BUS 244008 CKT 1 / 243684 05DEWEY 138 244008 05STANVILLE1 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243702 CKT 1 / 243684 05DEWEY 138 243702 05THELMA 138 1 OPEN BRANCH FROM BUS 243684 TO BUS 243804 CKT 1 / 243684 05DEWEY 138 243804 05DEWEY 69.0 1 OPEN BRANCH FROM BUS 243804 TO BUS 244575 CKT 1 / 243804 05DEWEY 69.0 244575 05PEVLER 69.0 1 REMOVE SWSHUNT FROM BUS 243804 / 243804 05DEWEY 69.0 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2188 | Submitted for inclusion in Local Plan
AEP-VD484 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245737 | 05WRUTHFRDSS | 34.5 | 205 | 1.0193 | 0.93345 | 8.585 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD485 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245738 | 05DOWCHEM2 | 34.5 | 205 | 1.018 | 0.92838 | 8.962 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD486 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245796 | 05WHIRLPOO | 34.5 | 205 | 1.0171 | 0.92721 | 8.989 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD487 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245726 | 05GRIFTHSS | 34.5 | 205 | 1.0186 | 0.92617 | 9.243 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD488 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245762 | 05N BALTMR | 34.5 | 205 | 1.0074 | 0.92553 | 8.187 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD489 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245779 | 05POE AVE TP | 34.5 | 205 | 1.0071 | 0.92472 | 8.238 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD490 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245752 | 05HENRY8 | 34.5 | 205 | 1.0042 | 0.92206 | 8.214 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD491 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245729 | 05CYGBUCK | 34.5 | 205 | 0.9976 | 0.91485 | 8.275 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD492 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245761 | 05MUNGEN | 34.5 | 205 | 0.9868 | 0.90305 | 8.375 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD493 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245781 | 05PORTAGE8 | 34.5 | 205 | 0.9842 | 0.90022 | 8.398 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD494 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245780 | 05PORTAGE | 34.5 | 205 | 0.9841 | 0.90011 | 8.399 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD495 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245791 | 05VANBURN8 | 34.5 | 205 | 1.0079 | 0.9243 | 8.36 | 8 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-2_#15286 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243067 TO BUS 245775 CKT 1 / 243067 05NWOODC 138 245775 05NWOODCEQ 999 1 OPEN BRANCH FROM BUS 242989 TO BUS 243067 CKT 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD496 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245791 | 05VANBURN8 | 34.5 | 205 | 1.0107 | 0.92355 | 8.715 | 8 | FB | AEP_P4_#7765_05NFINDL 138_B | Open branch from bus 242989 to bus 243067 ckt 1 / 242989 05E LIMA 138 243067 05NWOODC 138 1 Open branch from bus 245775 to bus 243067 ckt 1 / 245775 05NWOODCEQ 999 243067 05NWOODC 138 1 Open branch from bus 243059 to bus 243067 ckt 1 / 243059 05N.FINDLAY 138 243067 05NWOODC 138 1 Open branch from bus 245773 to bus 243059 ckt 1 / 245773 05NFINDLY2 34.5 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 243059 ckt 1 / 245771 05N.FINDL1EQ 999 243059 05N.FINDLAY 138 1 Open branch from bus 245771 to bus 245764 ckt Z1 / 245771 05N.FINDL1EQ 999 245764 05N.FINDLAY169.0 Z1 Open branch from bus 245771 to bus 245772 ckt 1 / 245771 05N.FINDL1EQ 999 245772 05NFINDLY1 34.5 1 Remove SWSHUNT from bus 243059 / 243059 05N.FINDLAY 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD497 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245791 | 05VANBURN8 | 34.5 | 205 | 1.0079 | 0.9267 | 8.12 | 8 | N-1-1 | AEP_P1-2_#13408 | OPEN BRANCH FROM BUS 245752 TO BUS 245762 CKT 1 / 245752 05HENRY8 34.5 245762 05N BALTMR 34.5 1 OPEN BRANCH FROM BUS 245762 TO BUS 245773 CKT 1 / 245762 05N BALTMR 34.5 245773 05NFINDLY2 34.5 1 | AEP_P1-3_#12526_05NFINDL 138_1 | OPEN BRANCH FROM BUS 243059 TO BUS 245771 CKT 1 / 243059 05NFINDL 138 245771 05NFIND EQ 999 1 OPEN BRANCH FROM BUS 245764 TO BUS 245771 CKT Z1 / 245764 05N FINDLA 69.0 245771 05NFIND EQ 999 Z1 OPEN BRANCH FROM BUS 245771 TO BUS 245772 CKT 1 / 245771 05NFIND EQ 999 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 243059 TO BUS 243067 CKT 1 / 243059 05NFINDL 138 243067 05NWOODC 138 1 OPEN BRANCH FROM BUS 245738 TO BUS 245772 CKT 1 / 245738 05DOWCHEM2 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245726 TO BUS 245772 CKT 1 / 245726 05GRIFTHSS 34.5 245772 05NFINDLY1 34.5 1 OPEN BRANCH FROM BUS 245772 TO BUS 247312 CKT 1 / 245772 05NFINDLY1 34.5 247312 05VANBURSS 34.5 1 REMOVE SWSHUNT FROM BUS 245772 / 245772 05NFINDLY1 34.5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2199 | Submitted for inclusion in Local Plan
AEP-VD498 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243758 | 05MIDDLECR | 46 | 205 | 0.9968 | 0.86341 | 13.339 | 8 | Bus | EKPC_P2-2_FALCON 69 | OPEN BUS 341461 /* 2FALCON EK |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VD499 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243758 | 05MIDDLECR | 46 | 205 | 0.9968 | 0.86389 | 13.291 | 8 | Line w/o Fault | AEP_P2-1_243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1 | OPEN BRANCH FROM BUS 243721 TO BUS 341461 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VD500 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 1.0078 | 0.69296 | 31.484 | 8 | Bus | EKPC_P2-2_FALCON 69 | OPEN BUS 341461 /* 2FALCON EK |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VD501 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243721 | 05FALCON | 69 | 205 | 1.0078 | 0.69333 | 31.447 | 8 | Line w/o Fault | AEP_P2-1_243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1 | OPEN BRANCH FROM BUS 243721 TO BUS 341461 CKT Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2200 | Submitted for inclusion in Local Plan
AEP-VD502 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245900 | 05ROSELMS8 | 69 | 205 | 0.979 | 0.8764 | 10.26 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD503 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245910 | 05W OAKWOO | 69 | 205 | 0.9798 | 0.8773 | 10.25 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD504 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245877 | 05FTBROWN8 | 69 | 205 | 0.9862 | 0.8845 | 10.17 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD505 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245868 | 05CONTINEN | 69 | 205 | 0.9885 | 0.8872 | 10.13 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD506 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245869 | 05CONTIN8 | 69 | 205 | 0.9873 | 0.8882 | 9.91 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD507 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245864 | 05AUGLAIZE | 69 | 205 | 8.56 | 8.4744 | 8.56 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD508 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245900 | 05ROSELMS8 | 69 | 205 | 0.9664 | 0.8761 | 9.03 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD509 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245910 | 05W OAKWOO | 69 | 205 | 0.9672 | 0.877 | 9.02 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD510 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245877 | 05FTBROWN8 | 69 | 205 | 0.9737 | 0.8842 | 8.95 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD511 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245868 | 05CONTINEN | 69 | 205 | 0.9761 | 0.8869 | 8.92 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD512 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245869 | 05CONTIN8 | 69 | 205 | 0.977 | 0.8879 | 8.91 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD513 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245864 | 05AUGLAIZE | 69 | 205 | 0.9828 | 0.8947 | 8.81 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD514 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245900 | 05ROSELMS8 | 69 | 205 | 0.9847 | 0.8343 | 15.04 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD515 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245910 | 05W OAKWOO | 69 | 205 | 0.9857 | 0.8355 | 15.02 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD516 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245877 | 05FTBROWN8 | 69 | 205 | 0.9917 | 0.8422 | 14.95 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD517 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245868 | 05CONTINEN | 69 | 205 | 0.9952 | 0.8462 | 14.9 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD518 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245869 | 05CONTIN8 | 69 | 205 | 0.9937 | 0.8476 | 14.61 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD519 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245864 | 05AUGLAIZE | 69 | 205 | 0.9876 | 0.8591 | 12.85 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD520 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245904 | 05SHERWOOD | 69 | 205 | 0.9851 | 0.8902 | 9.49 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD521 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245886 | 05MARK CEN | 69 | 205 | 0.9851 | 0.9013 | 8.38 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD522 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245904 | 05SHERWOOD | 69 | 205 | 1.0028 | 0.9172 | 8.56 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD523 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245886 | 05MARK CEN | 69 | 205 | 1.0099 | 0.9253 | 8.46 | 8 | N-1-1 | AEP_P1-2_#12217_917 | OPEN BRANCH FROM BUS 245868 TO BUS 247140 CKT 1 / 245868 05CONTINEN 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245882 TO BUS 247140 CKT 1 / 245882 05KALIDA 69.0 247140 05N.KALISS 69.0 1 OPEN BRANCH FROM BUS 245883 TO BUS 247140 CKT Z1 / 245883 05KALIDA8 69.0 247140 05N.KALISS 69.0 Z1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2215 | Submitted for inclusion in Local Plan
AEP-VD524 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9971 | 0.8035 | 19.36 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD525 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9971 | 0.8035 | 19.36 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD526 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9971 | 0.8035 | 19.36 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD527 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9971 | 0.8035 | 19.36 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD528 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9984 | 0.8012 | 19.72 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD529 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9984 | 0.8012 | 19.72 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD530 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9984 | 0.8013 | 19.71 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD531 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9984 | 0.8013 | 19.71 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD532 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 1.0022 | 0.8895 | 11.27 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD533 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 1.0022 | 0.8896 | 11.26 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD534 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 1.0022 | 0.8896 | 11.26 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD535 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 1.0022 | 0.8896 | 11.26 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD536 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9971 | 0.8942 | 10.29 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD537 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9971 | 0.8942 | 10.29 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD538 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243723 | 05GOLDENOK | 69 | 205 | 0.9971 | 0.8942 | 10.29 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD539 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243752 | 05WHITSBRG | 69 | 205 | 0.9971 | 0.8942 | 10.29 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD540 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0088 | 0.7784 | 23.04 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD541 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0088 | 0.7784 | 23.04 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD542 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 1.0039 | 0.7792 | 22.47 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD543 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 1.0039 | 0.7792 | 22.47 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD544 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0021 | 0.7762 | 22.59 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD545 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243751 | 05WEEKSBRY | 69 | 205 | 1.0021 | 0.7763 | 22.58 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD546 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 1.0027 | 0.7769 | 22.58 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD547 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243744 | 05REEDYCOL | 69 | 205 | 22.57 | 22.3443 | 22.57 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD548 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.7953 | 19.99 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD549 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.7953 | 19.99 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD550 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9969 | 0.7931 | 20.38 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD551 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9969 | 0.7931 | 20.38 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD552 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 0.9994 | 0.8153 | 18.41 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD553 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 0.9994 | 0.8153 | 18.41 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD554 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 1.0012 | 0.8129 | 18.83 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD555 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 1.0012 | 0.813 | 18.82 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD556 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 69 | 205 | 1.0132 | 0.9111 | 10.21 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD557 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 69 | 205 | 1.0132 | 0.9111 | 10.21 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD558 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 69 | 205 | 1.0144 | 0.9087 | 10.57 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD559 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243719 | 05DAISY | 69 | 205 | 1.0144 | 0.9088 | 10.56 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD560 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 1.0003 | 0.8841 | 11.62 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD561 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 1.0003 | 0.8841 | 11.62 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD562 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243747 | 05SLEMP | 69 | 205 | 1.0108 | 0.9264 | 8.44 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD563 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243747 | 05SLEMP | 69 | 205 | 1.0108 | 0.9264 | 8.44 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD564 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243747 | 05SLEMP | 69 | 205 | 1.0096 | 0.9242 | 8.54 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD565 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243747 | 05SLEMP | 69 | 205 | 1.0096 | 0.9242 | 8.54 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD566 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 1.005 | 0.8968 | 10.82 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD567 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 1.005 | 0.8968 | 10.82 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD568 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.8887 | 10.65 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD569 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243739 | 05MAYKING | 69 | 205 | 0.9952 | 0.8887 | 10.65 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD570 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 0.9994 | 0.9013 | 9.81 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD571 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243717 | 05COLLIER | 69 | 205 | 0.9994 | 0.9013 | 9.81 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD572 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 0.9988 | 0.7821 | 21.67 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD573 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 0.9988 | 0.7821 | 21.67 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD574 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 1.0051 | 0.7799 | 22.52 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD575 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 1.0051 | 0.7799 | 22.52 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD576 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 1.0065 | 0.8768 | 12.97 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD577 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 1.0065 | 0.8769 | 12.96 | 8 | N-1-1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD578 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 0.9988 | 0.8815 | 11.73 | 8 | N-1-1 | AEP_P1-2_#8331_21198 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243687 TO BUS 243722 CKT 1 / 243687 05FLEMIN 138 243722 05FLEMING 69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD579 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243722 | 05FLEMING | 69 | 205 | 0.9988 | 0.8815 | 11.73 | 8 | N-1-1 | AEP_P1-3_#12003_05BEEFHI 138_1 | OPEN BRANCH FROM BUS 243673 TO BUS 243685 CKT 1 / 243673 05BEEFHI 138 243685 05DORTON 138 1 OPEN BRANCH FROM BUS 243673 TO BUS 243687 CKT 1 / 243673 05BEEFHI 138 243687 05FLEMIN 138 1 OPEN BRANCH FROM BUS 243722 TO BUS 243736 CKT 1 / 243722 05FLEMING 69.0 243736 05JENKINS 69.0 1 | AEP_P1-2_#11452_258 | OPEN BRANCH FROM BUS 243708 TO BUS 247455 CKT 1 / 243708 05BEAVERCR 69.0 247455 05WEEKSBRYSS69.0 1 OPEN BRANCH FROM BUS 243722 TO BUS 247456 CKT 1 / 243722 05FLEMING 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243744 TO BUS 247456 CKT 1 / 243744 05REEDYCOL 69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 247455 TO BUS 247456 CKT 1 / 247455 05WEEKSBRYSS69.0 247456 05REEDYCO SS69.0 1 OPEN BRANCH FROM BUS 243751 TO BUS 247455 CKT 1 / 243751 05WEEKSBRY 69.0 247455 05WEEKSBRYSS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Associated with S2219 | Submitted for inclusion in Local Plan
AEP-VD580 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 1.0022 | 0.85707 | 14.513 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD581 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 69 | 205 | 1.0271 | 0.92022 | 10.688 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD582 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 69 | 205 | 1.0156 | 0.71111 | 30.449 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD583 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 1.0173 | 0.93575 | 8.155 | 8 | Tower | AEP_P7-1_#10939 | OPEN BRANCH FROM BUS 242951 TO BUS 244938 CKT Z1 / 242951 05ADDISONZ 138 244938 05ADDISON8 138 Z1 OPEN BRANCH FROM BUS 242951 TO BUS 243013 CKT 1 / 242951 05ADDISONZ 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242951 TO BUS 243126 CKT 1 / 242951 05ADDISONZ 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243046 TO BUS 243126 CKT 1 / 243046 05N CROW 138 243126 05THIVENER1Z 138 1 OPEN BRANCH FROM BUS 243073 TO BUS 246273 CKT 1 / 243073 05PATRT8 138 246273 05THIVENR SS 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 243126 TO BUS 246273 CKT Z1 / 243126 05THIVENER1Z 138 246273 05THIVENR SS 138 Z1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD584 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.91365 | 9.895 | 8 | FB | AEP_P4_#9849_05GAVIN1 138_AE1 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 243013 TO BUS 244949 CKT 1 / 243013 05GAVIN1 138 244949 05GAVIN1 69.0 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 REMOVE SWSHUNT FROM BUS 243013 / 243013 05GAVIN1 138 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD585 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.91662 | 9.598 | 8 | FB | AEP_P4_#9850_05GAVIN1 138_AE | OPEN BRANCH FROM BUS 243013 TO BUS 243069 CKT 1 / 243013 05GAVIN1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD586 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.9162 | 9.64 | 8 | FB | AEP_P4_#10511_05SPORN 138_N2 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 247040 CKT 1 / 242807 05SPORN 138 247040 05MOUNTN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD587 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.9162 | 9.64 | 8 | FB | AEP_P4_#11463_05LAKIN 69.0_G | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD588 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.91618 | 9.642 | 8 | FB | AEP_P4_#10517_05SPORN 138_N | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 243084 CKT 1 / 242807 05SPORN 138 243084 05RUTLAN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD589 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.9162 | 9.64 | 8 | Bus | AEP_P2-2_#11463_05LAKIN 69.0_1 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD590 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.91578 | 9.682 | 8 | Line w/o Fault | AEP_P2-1_244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 | OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD591 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244759 | 05LOCK LAN | 69 | 205 | 1.0126 | 0.9162 | 9.64 | 8 | Single | AEP_P1-2_#5878_187 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD592 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.085 | 0.92773 | 15.727 | 8 | Line w/o Fault | AEP_P2-1_242762 05REEDCR 138 244207 05REEDYCEQ 999 1 | OPEN BRANCH FROM BUS 242762 TO BUS 244207 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD593 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246883 | 05GROVES 3 | 13.8 | 205 | 0.9902 | 0.8644 | 12.58 | 8 | Line w/o Fault | AEP_P2-1_243518 05GROVES 138 246882 05GROVEQ3 999 8 | OPEN BRANCH FROM BUS 243518 TO BUS 246882 CKT 8 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD594 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246883 | 05GROVES 3 | 13.8 | 205 | 0.9902 | 0.86432 | 12.588 | 8 | Bus | AEP_P2-2_#11094_05GROVES 138_E | OPEN BRANCH FROM BUS 243518 TO BUS 246882 CKT 8 / 243518 05GROVES 138 246882 05GROVEQ3 999 8 OPEN BRANCH FROM BUS 243473 TO BUS 243518 CKT 2 / 243473 05BIXBY 138 243518 05GROVES 138 2 OPEN BRANCH FROM BUS 243518 TO BUS 246761 CKT 1 / 243518 05GROVES 138 246761 05THREEC 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246724 CKT 3 / 243518 05GROVES 138 246724 05GROVES2L 13.8 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD595 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246883 | 05GROVES 3 | 13.8 | 205 | 0.9902 | 0.86488 | 12.532 | 8 | FB | AEP_P4_#9664_05GROVES 138_4 | OPEN BRANCH FROM BUS 243518 TO BUS 246882 CKT 8 / 243518 05GROVES 138 246882 05GROVEQ3 999 8 OPEN BRANCH FROM BUS 243473 TO BUS 243518 CKT 2 / 243473 05BIXBY 138 243518 05GROVES 138 2 OPEN BRANCH FROM BUS 243518 TO BUS 246761 CKT 1 / 243518 05GROVES 138 246761 05THREEC 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246724 CKT 3 / 243518 05GROVES 138 246724 05GROVES2L 13.8 3 REMOVE LOAD D4 FROM BUS 243473 / 243473 05BIXBY 138 D4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD596 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246883 | 05GROVES 3 | 13.8 | 205 | 0.9902 | 0.86513 | 12.507 | 8 | FB | AEP_P4_#9666_05GROVES 138_2 | OPEN BRANCH FROM BUS 243518 TO BUS 246882 CKT 8 / 243518 05GROVES 138 246882 05GROVEQ3 999 8 OPEN BRANCH FROM BUS 243473 TO BUS 243518 CKT 2 / 243473 05BIXBY 138 243518 05GROVES 138 2 OPEN BRANCH FROM BUS 243473 TO BUS 246761 CKT 1 / 243473 05BIXBY 138 246761 05THREEC 138 1 OPEN BRANCH FROM BUS 246761 TO BUS 246762 CKT 1 / 246761 05THREEC 138 246762 05GRFN W 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246761 CKT 1 / 243518 05GROVES 138 246761 05THREEC 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246724 CKT 3 / 243518 05GROVES 138 246724 05GROVES2L 13.8 3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD597 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246723 | 05GROVES1L | 13.8 | 205 | 0.9994 | 0.88482 | 11.458 | 8 | Bus | AEP_P2-2_#9665_05GROVES 138_W | OPEN BRANCH FROM BUS 243518 TO BUS 246884 CKT 7 / 243518 05GROVES 138 246884 05GROVEQ2 999 7 OPEN BRANCH FROM BUS 243472 TO BUS 243518 CKT 1 / 243472 05BEXLEY 138 243518 05GROVES 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246760 CKT 1 / 243518 05GROVES 138 246760 05REFUGE 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246704 CKT 1 / 243518 05GROVES 138 246704 05GROVES 2 39.4 1 REMOVE SWSHUNT FROM BUS 243518 / 243518 05GROVES 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD598 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246723 | 05GROVES1L | 13.8 | 205 | 0.9994 | 0.88482 | 11.458 | 8 | FB | AEP_P4_#9665_05GROVES 138_9 | OPEN BRANCH FROM BUS 243518 TO BUS 246884 CKT 7 / 243518 05GROVES 138 246884 05GROVEQ2 999 7 OPEN BRANCH FROM BUS 243472 TO BUS 243518 CKT 1 / 243472 05BEXLEY 138 243518 05GROVES 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246760 CKT 1 / 243518 05GROVES 138 246760 05REFUGE 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246704 CKT 1 / 243518 05GROVES 138 246704 05GROVES 2 39.4 1 REMOVE SWSHUNT FROM BUS 243518 / 243518 05GROVES 138 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD599 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246723 | 05GROVES1L | 13.8 | 205 | 0.9994 | 0.88677 | 11.263 | 8 | FB | AEP_P4_#9667_05GROVES 138_7 | OPEN BRANCH FROM BUS 243518 TO BUS 246884 CKT 7 / 243518 05GROVES 138 246884 05GROVEQ2 999 7 OPEN BRANCH FROM BUS 244868 TO BUS 246760 CKT 1 / 244868 05BRICE 138 246760 05REFUGE 138 1 OPEN BRANCH FROM BUS 243472 TO BUS 243518 CKT 1 / 243472 05BEXLEY 138 243518 05GROVES 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246760 CKT 1 / 243518 05GROVES 138 246760 05REFUGE 138 1 OPEN BRANCH FROM BUS 243572 TO BUS 246760 CKT 1 / 243572 05SHANON 138 246760 05REFUGE 138 1 OPEN BRANCH FROM BUS 243518 TO BUS 246704 CKT 1 / 243518 05GROVES 138 246704 05GROVES 2 39.4 1 REMOVE SWSHUNT FROM BUS 243518 / 243518 05GROVES 138 REMOVE LOAD D3 FROM BUS 243518 / 243518 05GROVES 138 D3 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD600 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246723 | 05GROVES1L | 13.8 | 205 | 0.9994 | 0.90287 | 9.653 | 8 | Line w/o Fault | AEP_P2-1_243518 05GROVES 138 246884 05GROVEQ2 999 7 | OPEN BRANCH FROM BUS 243518 TO BUS 246884 CKT 7 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD601 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.0885 | 1.0035 | 8.499 | 8 | Line w/o Fault | AEP_P2-1_242762 05REEDCR 138 244207 05REEDYCEQ 999 1 | OPEN BRANCH FROM BUS 242762 TO BUS 244207 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD602 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0149 | 0.896 | 11.89 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD603 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 1.0042 | 0.9 | 10.42 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD604 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9992 | 0.9003 | 9.89 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD605 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0072 | 0.896 | 11.12 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD606 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9945 | 0.8394 | 15.51 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD607 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.993 | 0.8398 | 15.32 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD608 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9945 | 0.8459 | 14.86 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD609 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 14.57 | 14.4243 | 14.57 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD610 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0173 | 0.8897 | 12.76 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD611 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9942 | 0.8883 | 10.59 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD612 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245836 | 05ROCKHILL | 34.5 | 205 | 1.0118 | 0.8897 | 12.21 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD613 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244740 | 0523RD ST | 34.5 | 205 | 0.9891 | 0.8886 | 10.05 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD614 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9938 | 0.8339 | 15.99 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD615 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9911 | 0.8341 | 15.7 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD616 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9938 | 0.8585 | 13.53 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD617 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244751 | 05APPLEGRV | 69 | 205 | 0.9916 | 0.8579 | 13.37 | 8 | N-1-1 | AEP_P1-2_#5873_184 | OPEN BRANCH FROM BUS 242540 TO BUS 243095 CKT 1 / 242540 05APPLE1 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243003 TO BUS 243095 CKT 1 / 243003 05FAYETTE Z 138 243095 05SCOTTOWNSS 138 1 OPEN BRANCH FROM BUS 243095 TO BUS 244972 CKT Z1 / 243095 05SCOTTOWNSS 138 244972 05SCOTTWN8 12.0 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD618 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245614 | 05FREMNT C | 69 | 205 | 1.0088 | 0.64202 | 36.678 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD619 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244279 | 05DISMALSS | 69 | 205 | 1.0301 | 0.94035 | 8.975 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD620 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.0848 | 0.743 | 34.18 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD621 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.0848 | 0.743 | 34.18 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD622 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244212 | 05ROTHERWD | 34.5 | 205 | 1.0241 | 0.9215 | 10.26 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD623 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 34.5 | 205 | 1.0299 | 0.928 | 10.19 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD624 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.0824 | 0.7608 | 32.16 | 8 | N-1-1 | AEP_P1-3_#12033_05HOLST1 138_5 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244196 CKT 1 / 244194 05HLSTN5EQ 999 244196 05HOLSTN L 69.0 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242670 CKT ZB / 242669 05HOLST1 138 242670 05HOLST2 138 ZB OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD625 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244208 | 05REEDYCR | 12 | 205 | 1.0824 | 0.7608 | 32.16 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD626 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244212 | 05ROTHERWD | 34.5 | 205 | 1.0131 | 0.9245 | 8.86 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD627 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244219 | 05WKINGSP | 34.5 | 205 | 1.0189 | 0.931 | 8.79 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD628 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245064 | 05TITANIUM | 69 | 205 | 1.0213 | 0.9406 | 8.07 | 8 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD629 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245064 | 05TITANIUM | 69 | 205 | 1.0213 | 0.9406 | 8.07 | 8 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD630 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 1.0083 | 0.8846 | 12.37 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD631 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244165 | 05FRIES | 69 | 205 | 0.9854 | 0.8838 | 10.16 | 8 | N-1-1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD632 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 1.0038 | 0.6461 | 35.77 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD633 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 0.9883 | 0.6491 | 33.92 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD634 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 1.0015 | 0.8383 | 16.32 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD635 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 0.9976 | 0.8383 | 15.93 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD636 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 1.0017 | 0.643 | 35.87 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD637 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243156 | 05W.NEW PHIL | 138 | 205 | 0.9873 | 0.6487 | 33.86 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD638 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 17.24 | 17.0676 | 17.24 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD639 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243082 | 05ROCKHILL1 | 138 | 205 | 1.0033 | 0.8336 | 16.97 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Potential M-3 need identified, awaiting field and engineering analysis
AEP-VD640 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 1.0295 | 0.8896 | 13.99 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD641 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 1.0289 | 0.8897 | 13.92 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD642 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 1.0288 | 0.89011 | 13.869 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD643 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 1.0288 | 0.89031 | 13.849 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD644 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 1.0299 | 0.91847 | 11.143 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD645 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 1.0293 | 0.91876 | 11.054 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD646 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 1.0286 | 0.91919 | 10.941 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD647 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 1.0255 | 0.91488 | 11.062 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD648 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 1.0127 | 0.65135 | 36.135 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD649 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 1.0114 | 0.65139 | 36.001 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD650 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 1.011 | 0.6519 | 35.91 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD651 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 1.0109 | 0.65215 | 35.875 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD652 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 1.0165 | 0.70855 | 30.795 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD653 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 0.9977 | 0.68257 | 31.513 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD654 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 1.016 | 0.70871 | 30.729 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD655 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 1.0158 | 0.70937 | 30.643 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD656 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245623 | 05HOLRAN | 69 | 205 | 1.0064 | 0.84403 | 16.237 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD657 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245625 | 05MAPLE GR | 69 | 205 | 1.0064 | 0.86167 | 14.473 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD658 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 244869 | 05BOSSERMAN | 69 | 205 | 1.0219 | 0.93886 | 8.304 | 8 | FB | AEP_P4_#14347_05BOSSERMAN 138_B2 | OPEN BRANCH FROM BUS 244869 TO BUS 247489 CKT 1 / 244869 05BOSSERMAN 69.0 247489 05BOSSERMAN 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD659 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 244869 | 05BOSSERMAN | 69 | 205 | 1.0219 | 0.93886 | 8.304 | 8 | Single | AEP_P1-2_#14612 | OPEN BRANCH FROM BUS 244869 TO BUS 247489 CKT 1 / 244869 05BOSSERMAN 69.0 247489 05BOSSERMAN 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD660 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.9162 | 8.53 | 8 | FB | AEP_P4_#9849_05GAVIN1 138_AE1 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 243013 TO BUS 244949 CKT 1 / 243013 05GAVIN1 138 244949 05GAVIN1 69.0 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 REMOVE SWSHUNT FROM BUS 243013 / 243013 05GAVIN1 138 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD661 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91915 | 8.235 | 8 | FB | AEP_P4_#9850_05GAVIN1 138_AE | OPEN BRANCH FROM BUS 243013 TO BUS 243069 CKT 1 / 243013 05GAVIN1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD662 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91873 | 8.277 | 8 | FB | AEP_P4_#10511_05SPORN 138_N2 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 247040 CKT 1 / 242807 05SPORN 138 247040 05MOUNTN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD663 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91874 | 8.276 | 8 | FB | AEP_P4_#11463_05LAKIN 69.0_G | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD664 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91871 | 8.279 | 8 | FB | AEP_P4_#10517_05SPORN 138_N | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 243084 CKT 1 / 242807 05SPORN 138 243084 05RUTLAN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD665 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91874 | 8.276 | 8 | Bus | AEP_P2-2_#11463_05LAKIN 69.0_1 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD666 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91832 | 8.318 | 8 | Line w/o Fault | AEP_P2-1_244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 | OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD667 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244760 | 05PTPLEASN | 69 | 205 | 1.0015 | 0.91874 | 8.276 | 8 | Single | AEP_P1-2_#5878_187 | OPEN BRANCH FROM BUS 242698 TO BUS 243013 CKT 1 / 242698 05LAKIN 138 243013 05GAVIN1 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 242807 CKT 1 / 242698 05LAKIN 138 242807 05SPORN 138 1 OPEN BRANCH FROM BUS 242698 TO BUS 244756 CKT 1 / 242698 05LAKIN 138 244756 05LAKIN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244759 CKT 1 / 244756 05LAKIN 69.0 244759 05LOCK LAN 69.0 1 OPEN BRANCH FROM BUS 244756 TO BUS 244761 CKT 1 / 244756 05LAKIN 69.0 244761 05RACINE 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD668 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9807 | 0.85854 | 12.216 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD669 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9779 | 0.85668 | 12.122 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD670 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9795 | 0.85849 | 12.101 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD671 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9817 | 0.86159 | 12.011 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD672 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9912 | 0.87525 | 11.595 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD673 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9869 | 0.88517 | 10.173 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD674 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9858 | 0.90157 | 8.423 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD675 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9808 | 0.84474 | 13.606 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD676 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9776 | 0.84284 | 13.476 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD677 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9793 | 0.84478 | 13.452 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD678 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9816 | 0.84845 | 13.315 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD679 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.992 | 0.86431 | 12.769 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD680 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9877 | 0.8757 | 11.2 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD681 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0152 | 0.807 | 20.82 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD682 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0074 | 0.8073 | 20.01 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD683 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9865 | 0.89357 | 9.293 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD684 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9608 | 0.7797 | 18.11 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD685 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.007 | 0.92113 | 8.587 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD686 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.007 | 0.92113 | 8.587 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD687 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.007 | 0.92113 | 8.587 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD688 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0071 | 0.92123 | 8.587 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD689 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0071 | 0.92123 | 8.587 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD690 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0071 | 0.92123 | 8.587 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD691 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.007 | 0.92124 | 8.576 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD692 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0071 | 0.92135 | 8.575 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD693 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0082 | 0.92241 | 8.579 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD694 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0082 | 0.92241 | 8.579 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD695 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0082 | 0.92241 | 8.579 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD696 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0082 | 0.92255 | 8.565 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD697 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.007 | 0.92174 | 8.526 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD698 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0071 | 0.92185 | 8.525 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD699 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0082 | 0.92302 | 8.518 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD700 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.954 | 0.7844 | 16.96 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD701 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9557 | 0.7863 | 16.94 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD702 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244534 | 05DALTEX L | 23 | 205 | 0.9978 | 0.91566 | 8.214 | 8 | FB | AEP_P4_#14657_05CHAPSS 138_E | OPEN BRANCH FROM BUS 242671 TO BUS 247242 CKT 1 / 242671 05HOPKIN 138 247242 05CHAPSS 138 1 OPEN BRANCH FROM BUS 242705 TO BUS 242735 CKT 1 / 242705 05LOGAN2 138 242735 05NPOINT 138 1 OPEN BRANCH FROM BUS 242735 TO BUS 247242 CKT 1 / 242735 05NPOINT 138 247242 05CHAPSS 138 1 OPEN BRANCH FROM BUS 242735 TO BUS 244530 CKT 1 / 242735 05NPOINT 138 244530 05N.POINT 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD703 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0108 | 0.831 | 17.98 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD704 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244302 | 05BIGROCK | 34.5 | 205 | 0.9645 | 0.88314 | 8.136 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD705 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244314 | 05THOMAS | 34.5 | 205 | 0.9659 | 0.88464 | 8.126 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD706 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245352 | 05WARSAW | 34.5 | 205 | 1.0089 | 0.92781 | 8.109 | 8 | Non-redundant relay failure | AEP_P5_#11299_05OHIO_05OHIO | OPEN BRANCH FROM BUS 238745 TO BUS 242941 CKT 1 / 238745 02GALION 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243454 TO BUS 242941 CKT 1 / 243454 05BIXBY 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 243455 TO BUS 242941 CKT 1 / 243455 05CONES 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242940 TO BUS 242941 CKT 1 / 242940 05MUSKNG 345 242941 05OHIOCT 345 1 OPEN BRANCH FROM BUS 242941 TO BUS 244319 CKT Z1 / 242941 05OHIOCT 345 244319 05OHIOCT_REA 345 Z1 OPEN BRANCH FROM BUS 242941 TO BUS 243070 CKT 1 / 242941 05OHIOCT 345 243070 05OHIOCT 138 1 REMOVE SWSHUNT FROM BUS 242941 / 242941 05OHIOCT 345 OPEN BRANCH FROM BUS 242950 TO BUS 246941 CKT 1 / 242950 05ACADEM 138 246941 05MILL2Z 138 1 OPEN BRANCH FROM BUS 247302 TO BUS 242962 CKT Z1 / 247302 05BLDBG8 138 242962 05BLDBGZ 138 Z1 OPEN BRANCH FROM BUS 242962 TO BUS 247278 CKT 1 / 242962 05BLDBGZ 138 247278 05MILL1Z 138 1 OPEN BRANCH FROM BUS 242962 TO BUS 243070 CKT 1 / 242962 05BLDBGZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242973 TO BUS 247253 CKT 1 / 242973 05BUCKH8 138 247253 05BUCKSS 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243105 CKT 1 / 247253 05BUCKSS 138 243105 05SMILLB 138 1 OPEN BRANCH FROM BUS 247253 TO BUS 243145 CKT 1 / 247253 05BUCKSS 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 247725 TO BUS 243076 CKT 1 / 247725 05CONESPREP 138 243076 05CONESPREPZ 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243488 CKT 1 / 243076 05CONESPREPZ 138 243488 05CONESVILLE 138 1 OPEN BRANCH FROM BUS 243076 TO BUS 243070 CKT 1 / 243076 05CONESPREPZ 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 246770 TO BUS 243070 CKT 1 / 246770 05DRESDN 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243001 CKT 1 / 242998 05EPOINT 138 243001 05EZANEV 138 1 OPEN BRANCH FROM BUS 242998 TO BUS 243070 CKT 1 / 242998 05EPOINT 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243001 TO BUS 243074 CKT 1 / 243001 05EZANEV 138 243074 05PHILO1 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243070 CKT 1 / 243007 05FRAZEY 138 243070 05OHIOCT 138 1 OPEN BRANCH FROM BUS 243007 TO BUS 243079 CKT 1 / 243007 05FRAZEY 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 247278 TO BUS 243050 CKT 1 / 247278 05MILL1Z 138 243050 05NBELVL 138 1 OPEN BRANCH FROM BUS 246941 TO BUS 243160 CKT 1 / 246941 05MILL2Z 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243063 TO BUS 243079 CKT 1 / 243063 05N.NEWARK1 138 243079 05REFORM 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 246010 CKT 2 / 243070 05OHIOCT 138 246010 05PHILO2 138 2 OPEN BRANCH FROM BUS 243070 TO BUS 243075 CKT 1 / 243070 05OHIOCT 138 243075 05POWELS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243094 CKT 1 / 243070 05OHIOCT 138 243094 05SCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243145 CKT 1 / 243070 05OHIOCT 138 243145 05WCOSHC 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 243160 CKT 1 / 243070 05OHIOCT 138 243160 05WTRNWY 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243070 TO BUS 245338 CKT 2 / 243070 05OHIOCT 138 245338 05OHIO CTR 69.0 2 OPEN BRANCH FROM BUS 243145 TO BUS 245350 CKT 1 / 243145 05WCOSHC 138 245350 05W COSHTN 69.0 1 OPEN BRANCH FROM BUS 243105 TO BUS 245343 CKT 1 / 243105 05SMILLB 138 245343 05S MILLBR 34.5 1 OPEN BRANCH FROM BUS 243160 TO BUS 245425 CKT 1 / 243160 05WTRNWY 138 245425 05W TRINWY 12.0 1 REMOVE LOAD T1 FROM BUS 247302 / 247302 05BLDBG8 138 REMOVE LOAD C1 FROM BUS 243076 / 243076 05CONESPREPZ 138 REMOVE SWSHUNT FROM BUS 243488 / 243488 05CONESVILLE 138 REMOVE LOAD D1 FROM BUS 242998 / 242998 05EPOINT 138 REMOVE LOAD D1 FROM BUS 243007 / 243007 05FRAZEY 138 REMOVE SWSHUNT FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D4 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D5 FROM BUS 243063 / 243063 05N.NEWARK1 138 REMOVE LOAD D1 FROM BUS 243075 / 243075 05POWELS 138 REMOVE LOAD T1 FROM BUS 243079 / 243079 05REFORM 138 REMOVE LOAD D4 FROM BUS 243094 / 243094 05SCOSHC 138 OPEN BRANCH FROM BUS 245318 TO BUS 247628 CKT 1 / 245318 05CONESVIL 69.0 247628 05CHROME 69.0 1 OPEN BRANCH FROM BUS 245318 TO BUS 245322 CKT 1 / 245318 05CONESVIL 69.0 245322 05DRESDEN 69.0 1 OPEN BRANCH FROM BUS 245322 TO BUS 247404 CKT 1 / 245322 05DRESDEN 69.0 247404 05S.DRESDNSS69.0 1 OPEN BRANCH FROM BUS 245323 TO BUS 247404 CKT Z1 / 245323 05DRESDEN8 69.0 247404 05S.DRESDNSS69.0 Z1 OPEN BRANCH FROM BUS 245338 TO BUS 247404 CKT 1 / 245338 05OHIO CTR 69.0 247404 05S.DRESDNSS69.0 1 REMOVE LOAD D1 FROM BUS 245318 / 245318 05CONESVIL 69.0 REMOVE LOAD C1 FROM BUS 247628 / 247628 05CHROME 69.0 REMOVE LOAD D1 FROM BUS 245322 / 245322 05DRESDEN 69.0 REMOVE LOAD T1 FROM BUS 245323 / 245323 05DRESDEN8 69.0 REMOVE SWSHUNT FROM BUS 245343 / 245343 05S MILLBR 34.5 REMOVE LOAD D1 FROM BUS 245425 / 245425 05W TRINWY 12.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD707 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244301 | 05PATRICK | 34.5 | 205 | 0.9677 | 0.88658 | 8.112 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD708 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244293 | 05BULLCRK | 34.5 | 205 | 0.9763 | 0.89576 | 8.054 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD709 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245690 | 05DECLIFF | 34.5 | 205 | 1.0099 | 1.1021 | -9.225 | 8 | FB | AEP_P4_#10739_05LA RUE 138_B | OPEN BRANCH FROM BUS 242963 TO BUS 243153 CKT 1 / 242963 05HEDDSS 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 242963 TO BUS 245540 CKT Z1 / 242963 05HEDDSS 138 245540 05BLOOMFL8 12.0 Z1 OPEN BRANCH FROM BUS 242963 TO BUS 243011 CKT 1 / 242963 05HEDDSS 138 243011 05FULTON 138 1 OPEN BRANCH FROM BUS 243011 TO BUS 243148 CKT 1 / 243011 05FULTON 138 243148 05WINDFL 138 1 OPEN BRANCH FROM BUS 243048 TO BUS 243148 CKT 1 / 243048 05N WALD 138 243148 05WINDFL 138 1 OPEN BRANCH FROM BUS 243048 TO BUS 245708 CKT 1 / 243048 05N WALD 138 245708 05N WALDO 69.0 1 OPEN BRANCH FROM BUS 243048 TO BUS 244566 CKT 1 / 243048 05N WALD 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 243147 TO BUS 244566 CKT 1 / 243147 05WILDCRK SS 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243147 TO BUS 244645 CKT Z1 / 243147 05WILDCRK SS 138 244645 05WILDCRK 8 138 Z1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD710 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245690 | 05DECLIFF | 34.5 | 205 | 1.0099 | 1.1022 | -9.23 | 8 | FB | AEP_P4_#10738_05LA RUE 138_C | OPEN BRANCH FROM BUS 242963 TO BUS 243153 CKT 1 / 242963 05HEDDSS 138 243153 05WMTVER 138 1 OPEN BRANCH FROM BUS 242963 TO BUS 245540 CKT Z1 / 242963 05HEDDSS 138 245540 05BLOOMFL8 12.0 Z1 OPEN BRANCH FROM BUS 242963 TO BUS 243011 CKT 1 / 242963 05HEDDSS 138 243011 05FULTON 138 1 OPEN BRANCH FROM BUS 243011 TO BUS 243148 CKT 1 / 243011 05FULTON 138 243148 05WINDFL 138 1 OPEN BRANCH FROM BUS 243048 TO BUS 243148 CKT 1 / 243048 05N WALD 138 243148 05WINDFL 138 1 OPEN BRANCH FROM BUS 243048 TO BUS 245708 CKT 1 / 243048 05N WALD 138 245708 05N WALDO 69.0 1 OPEN BRANCH FROM BUS 243048 TO BUS 244566 CKT 1 / 243048 05N WALD 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 / 244566 05LA RUE 138 244567 05LA RUE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD711 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247890 | 05BROWNSTNSS | 34.5 | 205 | 1.0124 | 1.1124 | -10.001 | 8 | FB | AEP_P4_#10737_05LA RUE 138_A | OPEN BRANCH FROM BUS 243147 TO BUS 244566 CKT 1 / 243147 05WILDCRK SS 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243147 TO BUS 244645 CKT Z1 / 243147 05WILDCRK SS 138 244645 05WILDCRK 8 138 Z1 OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 / 244566 05LA RUE 138 244567 05LA RUE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD712 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245704 | 05MEEKER | 34.5 | 205 | 1.0121 | 1.1134 | -10.131 | 8 | FB | AEP_P4_#10737_05LA RUE 138_A | OPEN BRANCH FROM BUS 243147 TO BUS 244566 CKT 1 / 243147 05WILDCRK SS 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243147 TO BUS 244645 CKT Z1 / 243147 05WILDCRK SS 138 244645 05WILDCRK 8 138 Z1 OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 / 244566 05LA RUE 138 244567 05LA RUE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD713 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247890 | 05BROWNSTNSS | 34.5 | 205 | 1.0124 | 1.1142 | -10.177 | 8 | Line w/o Fault | AEP_P2-1_244566 05LA RUE 138 244567 05LA RUE 34.5 1 | OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD714 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245704 | 05MEEKER | 34.5 | 205 | 1.0121 | 1.1152 | -10.307 | 8 | Line w/o Fault | AEP_P2-1_244566 05LA RUE 138 244567 05LA RUE 34.5 1 | OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD715 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245690 | 05DECLIFF | 34.5 | 205 | 1.0099 | 1.1302 | -12.034 | 8 | FB | AEP_P4_#10737_05LA RUE 138_A | OPEN BRANCH FROM BUS 243147 TO BUS 244566 CKT 1 / 243147 05WILDCRK SS 138 244566 05LA RUE 138 1 OPEN BRANCH FROM BUS 243103 TO BUS 243147 CKT 1 / 243103 05SKENTO 138 243147 05WILDCRK SS 138 1 OPEN BRANCH FROM BUS 243147 TO BUS 244645 CKT Z1 / 243147 05WILDCRK SS 138 244645 05WILDCRK 8 138 Z1 OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 / 244566 05LA RUE 138 244567 05LA RUE 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD716 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245690 | 05DECLIFF | 34.5 | 205 | 1.0099 | 1.132 | -12.214 | 8 | Line w/o Fault | AEP_P2-1_244566 05LA RUE 138 244567 05LA RUE 34.5 1 | OPEN BRANCH FROM BUS 244566 TO BUS 244567 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD717 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 1.0023 | 0.91423 | 8.807 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD718 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 1.0005 | 0.9129 | 8.76 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD719 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 1.0017 | 0.91421 | 8.749 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD720 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 1.0038 | 0.91678 | 8.702 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD721 | 2020RTEP 2025LL_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 1.0125 | 0.92769 | 8.481 | 8 | Non-redundant relay failure | AEP_P5_#11282_05S BE_05S BE | OPEN BRANCH FROM BUS 246353 TO BUS 246066 CKT 5 / 246353 05S BENDEQ 999 246066 05S.BEND2 138 5 OPEN BRANCH FROM BUS 246371 TO BUS 243388 CKT 4 / 246371 05W SIDEEQ 999 243388 05W SIDE 138 4 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S BENDEQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246371 TO BUS 246372 CKT 1 / 246371 05W SIDEEQ 999 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246371 TO BUS 246369 CKT 4 / 246371 05W SIDEEQ 999 246369 05W SIDE 34.5 4 OPEN BRANCH FROM BUS 243273 TO BUS 243359 CKT 1 / 243273 05DARDEN 138 243359 05PINERD 138 1 OPEN BRANCH FROM BUS 243273 TO BUS 243370 CKT 1 / 243273 05DARDEN 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243285 TO BUS 246066 CKT 1 / 243285 05E.SIDE 138 246066 05S.BEND2 138 1 OPEN BRANCH FROM BUS 243352 TO BUS 243370 CKT 1 / 243352 05NTRDAM 138 243370 05S.BEND1 138 1 OPEN BRANCH FROM BUS 246066 TO BUS 243385 CKT 1 / 246066 05S.BEND2 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 REMOVE LOAD D1 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D2 FROM BUS 243273 / 243273 05DARDEN 138 REMOVE LOAD D1 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D2 FROM BUS 243285 / 243285 05E.SIDE 138 REMOVE LOAD D1 FROM BUS 243317 / 243317 05IRELAN 138 REMOVE LOAD C1 FROM BUS 243352 / 243352 05NTRDAM 138 REMOVE LOAD D1 FROM BUS 243359 / 243359 05PINERD 138 REMOVE LOAD D4 FROM BUS 246066 / 246066 05S.BEND2 138 REMOVE LOAD D1 FROM BUS 243385 / 243385 05TWIN B 138 OPEN BRANCH FROM BUS 245183 TO BUS 245217 CKT 1 / 245183 05COLFAX 69.0 245217 05MUESSEL 69.0 1 OPEN BRANCH FROM BUS 245183 TO BUS 246356 CKT 1 / 245183 05COLFAX 69.0 246356 05S.BEND 69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 245178 CKT 1 / 245217 05MUESSEL 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 245217 TO BUS 246372 CKT 1 / 245217 05MUESSEL 69.0 246372 05W.SIDE 69.0 1 OPEN BRANCH FROM BUS 246477 TO BUS 246361 CKT 1 / 246477 05NILES 69.0 246361 05SWANSON 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 245178 CKT 1 / 246356 05S.BEND 69.0 245178 05ST.MARY CO69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 REMOVE LOAD D4 FROM BUS 245183 / 245183 05COLFAX 69.0 REMOVE LOAD D1 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE LOAD D2 FROM BUS 245217 / 245217 05MUESSEL 69.0 REMOVE SWSHUNT FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D2 FROM BUS 246477 / 246477 05NILES 69.0 REMOVE LOAD D1 FROM BUS 245178 / 245178 05ST.MARY CO69.0 REMOVE SWSHUNT FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D1 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD D2 FROM BUS 246361 / 246361 05SWANSON 69.0 REMOVE LOAD C1 FROM BUS 246365 / 246365 05U PK MAL 69.0 REMOVE SWSHUNT FROM BUS 246314 / 246314 05DRAGOON 34.5 REMOVE LOAD C1 FROM BUS 246322 / 246322 05GRAPE RD 34.5 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD722 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0046 | 0.831 | 17.36 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD723 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0078 | 0.8365 | 17.13 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD724 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0147 | 0.8384 | 17.63 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD725 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9567 | 0.7923 | 16.44 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD726 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0077 | 0.8392 | 16.85 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD727 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0146 | 0.8412 | 17.34 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD728 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.935 | 0.7796 | 15.54 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD729 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9392 | 0.7843 | 15.49 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD730 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9409 | 0.7862 | 15.47 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD731 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9459 | 0.7922 | 15.37 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD732 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0092 | 0.8515 | 15.77 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD733 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.972 | 0.8231 | 14.89 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD734 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.004 | 0.8511 | 15.29 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD735 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9586 | 0.8232 | 13.54 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD736 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9701 | 0.8365 | 13.36 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD737 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9578 | 0.8367 | 12.11 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD738 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 1.0041 | 0.8946 | 10.95 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD739 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245468 | 05CASSELLJSS | 69 | 205 | 1.0169 | 0.6743 | 34.26 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD740 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245458 | 05FAIRDALE | 69 | 205 | 1.0128 | 0.6748 | 33.8 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD741 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245459 | 05SHIELDAL | 34.5 | 205 | 1.0098 | 0.676 | 33.38 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD742 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245470 | 05S CAMBRD | 69 | 205 | 1.0084 | 0.6758 | 33.26 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD743 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245459 | 05SHIELDAL | 34.5 | 205 | 0.9896 | 0.6876 | 30.2 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD744 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245468 | 05CASSELLJSS | 69 | 205 | 0.9869 | 0.6859 | 30.1 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD745 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245458 | 05FAIRDALE | 69 | 205 | 0.9873 | 0.6863 | 30.1 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD746 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245470 | 05S CAMBRD | 69 | 205 | 0.9883 | 0.6874 | 30.09 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD747 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 1.0044 | 0.8948 | 10.96 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD748 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0129 | 0.8936 | 11.93 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD749 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0132 | 0.894 | 11.92 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD750 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0136 | 0.8944 | 11.92 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD751 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0136 | 0.8944 | 11.92 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD752 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0149 | 0.8959 | 11.9 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD753 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.9991 | 0.8948 | 10.43 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD754 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9993 | 0.8951 | 10.42 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD755 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9722 | 0.8599 | 11.23 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD756 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0051 | 0.8936 | 11.15 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD757 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0054 | 0.894 | 11.14 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD758 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0058 | 0.8944 | 11.14 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD759 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0058 | 0.8944 | 11.14 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD760 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0072 | 0.8959 | 11.13 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD761 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 1.0039 | 0.9065 | 9.74 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD762 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0133 | 0.9046 | 10.87 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD763 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9992 | 0.9067 | 9.25 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD764 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245444 | 05CAMBRIDG | 34.5 | 205 | 24.44 | 24.1956 | 24.44 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD765 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 1.0041 | 0.9118 | 9.23 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD766 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.006 | 0.9046 | 10.14 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD767 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 1.0043 | 0.9147 | 8.96 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD768 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9992 | 0.912 | 8.72 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD769 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245444 | 05CAMBRIDG | 34.5 | 205 | 1.0023 | 0.7434 | 25.89 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD770 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9761 | 0.8827 | 9.34 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD771 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0117 | 0.9161 | 9.56 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD772 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9994 | 0.915 | 8.44 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD773 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245484 | 05WATER ST | 34.5 | 205 | 0.9978 | 0.7756 | 22.22 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD774 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0089 | 0.913 | 9.59 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD775 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245484 | 05WATER ST | 34.5 | 205 | 1.0004 | 0.7661 | 23.43 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD776 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9772 | 0.8897 | 8.75 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD777 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9774 | 0.89 | 8.74 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD778 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0081 | 0.917 | 9.11 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD779 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0034 | 0.913 | 9.04 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD780 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0049 | 0.9161 | 8.88 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD781 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9681 | 0.8829 | 8.52 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD782 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0078 | 0.9185 | 8.93 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD783 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0027 | 0.917 | 8.57 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD784 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0024 | 0.9185 | 8.39 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD785 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244972 | 05SCOTTWN8 | 12 | 205 | 1.0093 | 0.8203 | 18.9 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD786 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244625 | 05S.PIKEV1 | 69 | 205 | 0.9951 | 0.8426 | 15.25 | 8 | N-1-1 | AEP_P1-3_#13010_05BEAVER CR2 138_2 | OPEN BRANCH FROM BUS 243657 TO BUS 244688 CKT 1 / 243657 05BEAVC2EQ 999 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243657 TO BUS 243708 CKT 1 / 243657 05BEAVC2EQ 999 243708 05BEAVERCR 69.0 1 OPEN BRANCH FROM BUS 243657 TO BUS 243808 CKT 1 / 243657 05BEAVC2EQ 999 243808 05BEAVERCR 46.0 1 OPEN BRANCH FROM BUS 243671 TO BUS 244688 CKT ZP / 243671 05BEAVER CR1 138 244688 05BEAVER CR2 138 ZP OPEN BRANCH FROM BUS 243685 TO BUS 244688 CKT 1 / 243685 05DORTON 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243698 TO BUS 244688 CKT 1 / 243698 05MORGFK 138 244688 05BEAVER CR2 138 1 OPEN BRANCH FROM BUS 243703 TO BUS 244688 CKT 1 / 243703 05TOPMOS 138 244688 05BEAVER CR2 138 1 REMOVE SWSHUNT FROM BUS 244688 / 244688 05BEAVER CR2 138 | AEP_P1-3_#11473_05CEDARC 138_1 | DISCONNECT BUS 243661 / 243661 05CEDARCEQ 999 OPEN BRANCH FROM BUS 244594 TO BUS 244640 CKT 1 / 244594 05CEDARCRK 69.0 244640 05S.PIKEV2 69.0 1 OPEN BRANCH FROM BUS 244593 TO BUS 247368 CKT 1 / 244593 05CEDARCRK 46.0 247368 05SHELBY SS 46.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD787 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245847 | 05ST RITA | 34.5 | 205 | 1.0073 | 0.9256 | 8.17 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD788 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244972 | 05SCOTTWN8 | 12 | 205 | 0.997 | 0.8208 | 17.62 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD789 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242860 | 05ABERT | 69 | 205 | 1.0132 | 0.8422 | 17.1 | 8 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD790 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0137 | 0.8042 | 20.95 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD791 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245218 | 05COPPERHE | 34.5 | 205 | 1.0068 | 0.8076 | 19.92 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD792 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0088 | 0.8279 | 18.09 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD793 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.014 | 0.8365 | 17.75 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD794 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0139 | 0.8394 | 17.45 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD795 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9717 | 0.8137 | 15.8 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD796 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245250 | 05STONECK8 | 34.5 | 205 | 1.0033 | 0.8303 | 17.3 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD797 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245231 | 05E.MILLSTSS | 34.5 | 205 | 1.0091 | 0.8396 | 16.95 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD798 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245258 | 05GRADALL | 34.5 | 205 | 1.0091 | 0.8424 | 16.67 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD799 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0067 | 0.848 | 15.87 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD800 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246338 | 05LOGAN ST | 34.5 | 205 | 0.9557 | 0.8138 | 14.19 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD801 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.97 | 0.8283 | 14.17 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD802 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245249 | 05STONE CK | 34.5 | 205 | 1.0021 | 0.8496 | 15.25 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD803 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242886 | 05SKIMMR | 69 | 205 | 0.989 | 0.8603 | 12.87 | 8 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD804 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0412 | 0.8915 | 14.97 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD805 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.04 | 0.8905 | 14.95 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD806 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.041 | 0.8924 | 14.86 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD807 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0415 | 0.8932 | 14.83 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD808 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0413 | 0.8932 | 14.81 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD809 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0426 | 0.8951 | 14.75 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD810 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246366 | 05UNION | 34.5 | 205 | 0.9552 | 0.8284 | 12.68 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD811 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9721 | 0.8528 | 11.93 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD812 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.994 | 0.8826 | 11.14 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD813 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0354 | 0.8902 | 14.52 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD814 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9942 | 0.8829 | 11.13 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD815 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242860 | 05ABERT | 69 | 205 | 0.9887 | 0.8932 | 9.55 | 8 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD816 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0147 | 0.8867 | 12.8 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD817 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0155 | 0.8875 | 12.8 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD818 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0156 | 0.8877 | 12.79 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD819 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0159 | 0.888 | 12.79 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD820 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0173 | 0.8897 | 12.76 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD821 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242886 | 05SKIMMR | 69 | 205 | 0.9927 | 0.8999 | 9.28 | 8 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD822 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0421 | 0.9026 | 13.95 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD823 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.035 | 0.8979 | 13.71 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD824 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0412 | 0.9068 | 13.44 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD825 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.04 | 0.9058 | 13.42 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD826 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.041 | 0.9076 | 13.34 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD827 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0415 | 0.9083 | 13.32 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD828 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0413 | 0.9084 | 13.29 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD829 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244696 | 05CONNORST | 34.5 | 205 | 0.9889 | 0.8829 | 10.6 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD830 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244705 | 05E HUNTGT | 34.5 | 205 | 0.9891 | 0.8832 | 10.59 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD831 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.027 | 0.8933 | 13.37 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD832 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0426 | 0.9103 | 13.23 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD833 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245815 | 05BLUELICKSS | 34.5 | 205 | 1.0092 | 0.8868 | 12.24 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD834 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0257 | 0.8923 | 13.34 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD835 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245830 | 05MILCORSS | 34.5 | 205 | 1.0099 | 0.8876 | 12.23 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD836 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.0269 | 0.8941 | 13.28 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD837 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0272 | 0.8949 | 13.23 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD838 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245834 | 05ROBB AVE | 34.5 | 205 | 1.0101 | 0.8878 | 12.23 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD839 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0271 | 0.8949 | 13.22 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD840 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245820 | 05DANA COR | 34.5 | 205 | 1.0104 | 0.8881 | 12.23 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD841 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0354 | 0.9053 | 13.01 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD842 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0284 | 0.8968 | 13.16 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD843 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245858 | 05WRIGHT | 34.5 | 205 | 1.0118 | 0.8897 | 12.21 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD844 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 0.9951 | 0.8673 | 12.78 | 8 | N-1-1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD845 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0218 | 0.8919 | 12.99 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD846 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0398 | 0.9099 | 12.99 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD847 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0333 | 0.907 | 12.63 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD848 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0321 | 0.906 | 12.61 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD849 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.0332 | 0.9077 | 12.55 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD850 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0336 | 0.9085 | 12.51 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD851 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0421 | 0.9174 | 12.47 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD852 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0335 | 0.9085 | 12.5 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD853 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244162 | 05BYLLESBY | 69 | 205 | 1.0158 | 0.8682 | 14.76 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD854 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0349 | 0.9104 | 12.45 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD855 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.029 | 0.9043 | 12.47 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD856 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0284 | 0.9054 | 12.3 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD857 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.035 | 0.9126 | 12.24 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD858 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.0222 | 0.8996 | 12.26 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD859 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0163 | 0.8993 | 11.7 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD860 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9936 | 0.8944 | 9.92 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD861 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0398 | 0.9241 | 11.57 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD862 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0277 | 0.9115 | 11.62 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD863 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.976 | 0.8767 | 9.93 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD864 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245819 | 05DAYS INN | 34.5 | 205 | 1.0109 | 0.8994 | 11.15 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD865 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9944 | 0.9005 | 9.39 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD866 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244711 | 05FULKS | 34.5 | 205 | 0.9888 | 0.8947 | 9.41 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD867 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9947 | 0.9035 | 9.12 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD868 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.9772 | 0.8841 | 9.31 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD869 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9774 | 0.8844 | 9.3 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD870 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0119 | 0.9079 | 10.4 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD871 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244690 | 05BASF | 34.5 | 205 | 0.9894 | 0.9007 | 8.87 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD872 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246368 | 05VIRGIL S | 34.5 | 205 | 0.9664 | 0.8768 | 8.96 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD873 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.0144 | 0.913 | 10.14 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD874 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245468 | 05CASSELLJSS | 69 | 205 | 1.009 | 0.6312 | 37.78 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD875 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245458 | 05FAIRDALE | 69 | 205 | 1.004 | 0.632 | 37.2 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD876 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245459 | 05SHIELDAL | 34.5 | 205 | 0.9979 | 0.6319 | 36.6 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD877 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245470 | 05S CAMBRD | 69 | 205 | 0.9986 | 0.6337 | 36.49 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD878 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245459 | 05SHIELDAL | 34.5 | 205 | 1.0087 | 0.9099 | 9.88 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD879 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245468 | 05CASSELLJSS | 69 | 205 | 1.007 | 0.9085 | 9.85 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD880 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245458 | 05FAIRDALE | 69 | 205 | 1.0077 | 0.9092 | 9.85 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD881 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245470 | 05S CAMBRD | 69 | 205 | 1.0094 | 0.9109 | 9.85 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD882 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244741 | 0524TH ST | 34.5 | 205 | 0.9897 | 0.9038 | 8.59 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD883 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245824 | 05ELIZABET | 34.5 | 205 | 1.0081 | 0.908 | 10.01 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD884 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0115 | 0.9127 | 9.88 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD885 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0111 | 0.9142 | 9.69 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD886 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245444 | 05CAMBRIDG | 34.5 | 205 | 1.0232 | 0.9133 | 10.99 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD887 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245444 | 05CAMBRIDG | 34.5 | 205 | 0.9907 | 0.7178 | 27.29 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD888 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245484 | 05WATER ST | 34.5 | 205 | 1.0189 | 0.9162 | 10.27 | 8 | N-1-1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD889 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245484 | 05WATER ST | 34.5 | 205 | 0.9912 | 0.7454 | 24.58 | 8 | N-1-1 | AEP_P1-3_#12196_05E CAMBRD 69.0_1 | OPEN BRANCH FROM BUS 244066 TO BUS 245455 CKT 1 / 244066 05OLD WASHTN69.0 245455 05E CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245457 CKT 1 / 245455 05E CAMBRD 69.0 245457 05BYESVLLE 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245478 CKT 1 / 245455 05E CAMBRD 69.0 245478 05LEATHERW 69.0 1 OPEN BRANCH FROM BUS 245455 TO BUS 245470 CKT 1 / 245455 05E CAMBRD 69.0 245470 05S CAMBRD 69.0 1 OPEN BRANCH FROM BUS 245454 TO BUS 245455 CKT 1 / 245454 05E CAMBRD 34.5 245455 05E CAMBRD 69.0 1 REMOVE SWSHUNT FROM BUS 245455 / 245455 05E CAMBRD 69.0 OPEN BRANCH FROM BUS 245444 TO BUS 245465 CKT 1 / 245444 05CAMBRIDG 34.5 245465 05EDGETECH 34.5 1 OPEN BRANCH FROM BUS 245454 TO BUS 245465 CKT 1 / 245454 05E CAMBRD 34.5 245465 05EDGETECH 34.5 1 | AEP_P1-3_#11754_05WCAMBR 138_2 | OPEN BRANCH FROM BUS 242997 TO BUS 246490 CKT 1 / 242997 05E.NEWCONCZ 138 246490 05PHILO_BP 138 1 OPEN BRANCH FROM BUS 242997 TO BUS 243144 CKT 1 / 242997 05E.NEWCONCZ 138 243144 05WCAMBR 138 1 OPEN BRANCH FROM BUS 243144 TO BUS 245483 CKT 2 / 243144 05WCAMBR 138 245483 05W CAMBRD 69.0 2 OPEN BRANCH FROM BUS 245468 TO BUS 245483 CKT 1 / 245468 05CASSELLJSS69.0 245483 05W CAMBRD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD890 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244718 | 05JOHNSON LN | 34.5 | 205 | 0.9956 | 0.914 | 8.16 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD891 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246302 | 05MILES MISH | 34.5 | 205 | 0.968 | 0.8842 | 8.38 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD892 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245827 | 05JONES CT | 34.5 | 205 | 1.009 | 0.913 | 9.6 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD893 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246300 | 05BEIGER | 34.5 | 205 | 0.9683 | 0.8845 | 8.38 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD894 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244691 | 0526TH ST | 34.5 | 205 | 0.9958 | 0.9143 | 8.15 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD895 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245851 | 05SUP META | 34.5 | 205 | 1.0077 | 0.9127 | 9.5 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD896 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245817 | 05CEN AVE | 34.5 | 205 | 1.0074 | 0.9142 | 9.32 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD897 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244972 | 05SCOTTWN8 | 12 | 205 | 1.0062 | 0.8119 | 19.43 | 8 | N-1-1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD898 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244972 | 05SCOTTWN8 | 12 | 205 | 0.9946 | 0.8121 | 18.25 | 8 | N-1-1 | AEP_P1-3_#11615_05S.POINT2 138_4 | OPEN BRANCH FROM BUS 242918 TO BUS 245615 CKT 4 / 242918 05SPOIN4EQ 999 245615 05S.POINT2 138 4 OPEN BRANCH FROM BUS 242918 TO BUS 244965 CKT 4 / 242918 05SPOIN4EQ 999 244965 05S POINT 69.0 4 OPEN BRANCH FROM BUS 242918 TO BUS 243184 CKT 4 / 242918 05SPOIN4EQ 999 243184 05S POINT 34.5 4 OPEN BRANCH FROM BUS 243003 TO BUS 244971 CKT Z1 / 243003 05FAYETTE Z 138 244971 05FAYETTE8 138 Z1 OPEN BRANCH FROM BUS 243003 TO BUS 245615 CKT 1 / 243003 05FAYETTE Z 138 245615 05S.POINT2 138 1 OPEN BRANCH FROM BUS 243064 TO BUS 245615 CKT 1 / 243064 05NPROCT 138 245615 05S.POINT2 138 1 REMOVE SWSHUNT FROM BUS 245615 / 245615 05S.POINT2 138 OPEN BRANCH FROM BUS 244668 TO BUS 244965 CKT 1 / 244668 05HCOLLINS 69.0 244965 05S POINT 69.0 1 OPEN BRANCH FROM BUS 244965 TO BUS 247074 CKT 2 / 244965 05S POINT 69.0 247074 05LAWRENSS 69.0 2 OPEN BRANCH FROM BUS 243088 TO BUS 245615 CKT Z1 / 243088 05S.POINT1 138 245615 05S.POINT2 138 Z1 | AEP_P1-2_#5872_48 | OPEN BRANCH FROM BUS 242541 TO BUS 243040 CKT 1 / 242541 05APPLE2 138 243040 05MERCERVL Z 138 1 OPEN BRANCH FROM BUS 243040 TO BUS 244944 CKT Z1 / 243040 05MERCERVL Z 138 244944 05MERCERVL8 138 Z1 OPEN BRANCH FROM BUS 243040 TO BUS 246237 CKT 1 / 243040 05MERCERVL Z 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 242807 TO BUS 246237 CKT 1 / 242807 05SPORN 138 246237 05THIVENER2Z 138 1 OPEN BRANCH FROM BUS 246237 TO BUS 246273 CKT Z2 / 246237 05THIVENER2Z 138 246273 05THIVENR SS 138 Z2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD899 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245847 | 05ST RITA | 34.5 | 205 | 1.0112 | 0.9222 | 8.9 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD900 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9772 | 0.8897 | 8.75 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD901 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243746 | 05SILOAM | 69 | 205 | 0.977 | 0.8924 | 8.46 | 8 | N-1-1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD902 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245847 | 05ST RITA | 34.5 | 205 | 1.0074 | 0.9223 | 8.51 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD903 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245826 | 05HOVER PK | 34.5 | 205 | 1.0117 | 0.9285 | 8.32 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD904 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 1.003 | 0.908 | 9.5 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD905 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 1.0015 | 0.9069 | 9.46 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD906 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 1.0009 | 0.9065 | 9.44 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD907 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 1.0007 | 0.9065 | 9.42 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD908 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244679 | 05S.SHORE | 69 | 205 | 0.9696 | 0.8881 | 8.15 | 8 | N-1-1 | AEP_P1-2_#9856_21538 | OPEN BRANCH FROM BUS 243034 TO BUS 243140 CKT 1 / 243034 05MARQUI 138 243140 05WAKEFL 138 1 OPEN BRANCH FROM BUS 243087 TO BUS 243140 CKT 1 / 243087 05S LUCA 138 243140 05WAKEFL 138 1 | AEP_P1-3_#11612_05MILLBR PK1 138_5 | OPEN BRANCH FROM BUS 242988 TO BUS 243042 CKT 1 / 242988 05DOGWOO 138 243042 05MILLBR PK1 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243069 CKT 1 / 243042 05MILLBR PK1 138 243069 05FIREBR 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243047 CKT 1 / 243042 05MILLBR PK1 138 243047 05N PORT 138 1 OPEN BRANCH FROM BUS 243042 TO BUS 243173 CKT 5 / 243042 05MILLBR PK1 138 243173 05MILLBRK 69.0 5 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD909 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245833 | 05RANDALL | 34.5 | 205 | 1.0118 | 0.9305 | 8.13 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD910 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243174 | 05MOULTO | 69 | 205 | 1.012 | 0.9236 | 8.84 | 8 | N-1-1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | AEP_P1-2_#14698 | OPEN BRANCH FROM BUS 245983 TO BUS 245994 CKT 1 / 245983 05GRISTMILL 138 245994 05GEMINI 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD911 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243174 | 05MOULTO | 69 | 205 | 1.012 | 0.9243 | 8.77 | 8 | N-1-1 | AEP_P1-2_#7330_4842 | OPEN BRANCH FROM BUS 243122 TO BUS 243152 CKT 1 / 243122 05SW LIM 138 243152 05WMOULT 138 1 | AEP_P1-3_#14700_05GRISTMILL 138_1 | OPEN BRANCH FROM BUS 245977 TO BUS 245983 CKT 1 / 245977 05GRISTMILL 345 245983 05GRISTMILL 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD912 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242860 | 05ABERT | 69 | 205 | 15.17 | 15.0183 | 15.17 | 8 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD913 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0456 | 0.8815 | 16.41 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD914 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0446 | 0.8808 | 16.38 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD915 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.0457 | 0.8828 | 16.29 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD916 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245898 | 05PAULDING | 69 | 205 | 1.0317 | 0.9045 | 12.72 | 8 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD917 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0464 | 0.8839 | 16.25 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD918 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0463 | 0.884 | 16.23 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD919 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0486 | 0.8871 | 16.15 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD920 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245879 | 05GEN PORT | 69 | 205 | 1.0259 | 0.8997 | 12.62 | 8 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD921 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245867 | 05CECIL8 | 69 | 205 | 1.0223 | 0.8974 | 12.49 | 8 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD922 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0439 | 0.8856 | 15.83 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD923 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245886 | 05MARK CEN | 69 | 205 | 1.0192 | 0.8957 | 12.35 | 8 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD924 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0389 | 0.901 | 13.79 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD925 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0378 | 0.9003 | 13.75 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD926 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.039 | 0.902 | 13.7 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD927 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0394 | 0.903 | 13.64 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD928 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0393 | 0.9031 | 13.62 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD929 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0417 | 0.9062 | 13.55 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD930 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0485 | 0.8958 | 15.27 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD931 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0374 | 0.9043 | 13.31 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD932 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0456 | 0.909 | 13.66 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD933 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0446 | 0.9083 | 13.63 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD934 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243995 | 05SOUTHSID | 69 | 205 | 1.0445 | 0.9114 | 13.31 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD935 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.0457 | 0.91 | 13.57 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD936 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243993 | 05SCHOOLFI | 69 | 205 | 1.0434 | 0.9107 | 13.27 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD937 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.0439 | 0.8947 | 14.92 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD938 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0464 | 0.9109 | 13.55 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD939 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.0463 | 0.9111 | 13.52 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD940 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243949 | 05BRIDGE S | 69 | 205 | 1.0446 | 0.9123 | 13.23 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD941 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243989 | 05RIVERSD | 69 | 205 | 1.0451 | 0.9133 | 13.18 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD942 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0486 | 0.9142 | 13.44 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD943 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243982 | 05PINEYFOR | 69 | 205 | 1.045 | 0.9135 | 13.15 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD944 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244003 | 05WESTOVER | 69 | 205 | 1.0474 | 0.9166 | 13.08 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD945 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0421 | 0.9137 | 12.84 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD946 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0439 | 0.9122 | 13.17 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD947 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244002 | 05WEST FOR | 69 | 205 | 1.0431 | 0.9145 | 12.86 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD948 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245904 | 05SHERWOOD | 69 | 205 | 1.0156 | 0.9041 | 11.15 | 8 | N-1-1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD949 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.0379 | 0.9123 | 12.56 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD950 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0474 | 0.9057 | 14.17 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD951 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0485 | 0.9216 | 12.69 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD952 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243981 | 05NEW DESI | 69 | 205 | 1.0479 | 0.9238 | 12.41 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD953 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.0436 | 0.9223 | 12.13 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD954 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244005 | 05WHITMELL | 69 | 205 | 1.0439 | 0.9201 | 12.38 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD955 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0417 | 0.9222 | 11.95 | 8 | N-1-1 | AEP_P1-3_#11371_05DANVL1 138_1 | OPEN BRANCH FROM BUS 242619 TO BUS 243957 CKT 1 / 242619 05DANVL1 138 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243956 TO BUS 243957 CKT 1 / 243956 05DANVILLE 69.0 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 243955 TO BUS 243957 CKT 1 / 243955 05DANVILLE 34.5 243957 05DANVL1EQ 999 1 OPEN BRANCH FROM BUS 242544 TO BUS 242619 CKT 2 / 242544 05AXTON 138 242619 05DANVL1 138 2 OPEN BRANCH FROM BUS 242619 TO BUS 242620 CKT Z1 / 242619 05DANVL1 138 242620 05DANVL2 138 Z1 OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 REMOVE SWSHUNT FROM BUS 242619 / 242619 05DANVL1 138 OPEN BRANCH FROM BUS 243956 TO BUS 244018 CKT 1 / 243956 05DANVILLE 69.0 244018 05BALLOU2 69.0 1 OPEN BRANCH FROM BUS 243956 TO BUS 243984 CKT 1 / 243956 05DANVILLE 69.0 243984 05FALL CK SS69.0 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD956 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 10.25 | 10.1475 | 10.25 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD957 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0474 | 0.932 | 11.54 | 8 | N-1-1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD958 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244004 | 05WHITE OA | 69 | 205 | 1.0474 | 0.9299 | 11.75 | 8 | N-1-1 | AEP_P1-3_#12027_05E.MONU 138_3 | OPEN BRANCH FROM BUS 242629 TO BUS 243948 CKT 1 / 242629 05E.MONU 138 243948 05BRANTLY 69.0 1 OPEN BRANCH FROM BUS 243948 TO BUS 244013 CKT 1 / 243948 05BRANTLY 69.0 244013 05AIRSIDTP 69.0 1 | AEP_P1-2_#5424_107 | OPEN BRANCH FROM BUS 242619 TO BUS 242771 CKT 1 / 242619 05DANVL1 138 242771 05RIVERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD959 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242860 | 05ABERT | 69 | 205 | 1.0009 | 0.912 | 8.89 | 8 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD960 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242886 | 05SKIMMR | 69 | 205 | 1.0004 | 0.9134 | 8.7 | 8 | N-1-1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD961 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242886 | 05SKIMMR | 69 | 205 | 0.9863 | 0.8731 | 11.32 | 8 | N-1-1 | DVP_P1-2: LN 30 | OPEN BRANCH FROM BUS 313848 TO BUS 314689 CKT 1 /* 3BELLEVUE_DP115.00 - 3DOMINIO 115.00 OPEN BRANCH FROM BUS 313848 TO BUS 314861 CKT 1 /* 3BELLEVUE_DP115.00 - 3SKIMMER 115.00 OPEN BRANCH FROM BUS 314666 TO BUS 314689 CKT 1 /* 3ALTVSTA 115.00 - 3DOMINIO 115.00 OPEN BUS 313848 /* ISLAND: 3BELLEVUE_DP115.00 OPEN BUS 314689 /* ISLAND: 3DOMINIO 115.00 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD962 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9587 | 0.7686 | 19.01 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD963 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9511 | 0.7732 | 17.79 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD964 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9528 | 0.7751 | 17.77 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD965 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9538 | 0.7815 | 17.23 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD966 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246375 | 0512TH ST | 34.5 | 205 | 0.9604 | 0.8529 | 10.75 | 8 | N-1-1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD967 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246322 | 05GRAPE RD | 34.5 | 205 | 0.9323 | 0.7685 | 16.38 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD968 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246303 | 05BORLEY | 34.5 | 205 | 0.9365 | 0.7731 | 16.34 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD969 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246351 | 05RUSS ST | 34.5 | 205 | 0.9382 | 0.775 | 16.32 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD970 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246341 | 05RAILROAD | 34.5 | 205 | 0.9438 | 0.7814 | 16.24 | 8 | N-1-1 | AEP_P1-3_#14067_05S.BEND 5EQ 999_5 | OPEN BRANCH FROM BUS 246066 TO BUS 246353 CKT 5 / 246066 05S.BEND2 138 246353 05S.BEND 5EQ 999 5 OPEN BRANCH FROM BUS 246353 TO BUS 246356 CKT 5 / 246353 05S.BEND 5EQ 999 246356 05S.BEND 69.0 5 OPEN BRANCH FROM BUS 246353 TO BUS 246357 CKT 5 / 246353 05S.BEND 5EQ 999 246357 05SOUTHBEN 34.5 5 OPEN BRANCH FROM BUS 246361 TO BUS 246477 CKT 1 / 246361 05SWANSON 69.0 246477 05NILES 69.0 1 OPEN BRANCH FROM BUS 246356 TO BUS 247413 CKT 1 / 246356 05S.BEND 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246361 TO BUS 247413 CKT 1 / 246361 05SWANSON 69.0 247413 05UNIV PK SS69.0 1 OPEN BRANCH FROM BUS 246365 TO BUS 247413 CKT 1 / 246365 05U PK MAL 69.0 247413 05UNIV PK SS69.0 1 | AEP_P1-2_#5627_3107 | OPEN BRANCH FROM BUS 243280 TO BUS 243281 CKT 1 / 243280 05DRAGN 138 243281 05DRAGNZ 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243317 CKT 1 / 243281 05DRAGNZ 138 243317 05IRELAN 138 1 OPEN BRANCH FROM BUS 243281 TO BUS 243385 CKT 1 / 243281 05DRAGNZ 138 243385 05TWIN B 138 1 OPEN BRANCH FROM BUS 243317 TO BUS 243318 CKT 1 / 243317 05IRELAN 138 243318 05JACKSON RD 138 1 OPEN BRANCH FROM BUS 243280 TO BUS 246314 CKT 1 / 243280 05DRAGN 138 246314 05DRAGOON 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD971 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245886 | 05MARK CEN | 69 | 205 | 0.9851 | 0.8955 | 8.96 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD972 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245867 | 05CECIL8 | 69 | 205 | 0.9864 | 0.8973 | 8.91 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD973 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245879 | 05GEN PORT | 69 | 205 | 0.9881 | 0.8995 | 8.86 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD974 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245898 | 05PAULDING | 69 | 205 | 0.9922 | 0.9043 | 8.79 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD975 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245267 | 05BILLIAR | 69 | 205 | 0.9986 | 0.90527 | 9.333 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD976 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245289 | 05N FREDBR | 69 | 205 | 0.9993 | 0.88225 | 11.705 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD977 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245287 | 05MORELND8 | 69 | 205 | 0.9998 | 0.87932 | 12.048 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD978 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245298 | 05SHREVE | 69 | 205 | 1.0012 | 0.86741 | 13.379 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD979 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245266 | 05BIG PRAI | 69 | 205 | 0.9996 | 0.86559 | 13.401 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD980 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247028 | 05PAINTVSS | 69 | 205 | 1.0037 | 0.86327 | 14.043 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD981 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245274 | 05DRAKVAL8 | 69 | 205 | 0.9985 | 0.85926 | 13.924 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD982 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245286 | 05LOUDNVL8 | 69 | 205 | 0.9975 | 0.85809 | 13.941 | 8 | FB | AEP_P4_#9937_05WOOSTE 138_I | OPEN BRANCH FROM BUS 245306 TO BUS 243158 CKT 1 / 245306 05WOOSTREQ 999 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 245306 TO BUS 245305 CKT 1 / 245306 05WOOSTREQ 999 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 245306 TO BUS 245303 CKT 1 / 245306 05WOOSTREQ 999 245303 05WOOSTER 12.0 1 OPEN BRANCH FROM BUS 243000 TO BUS 243158 CKT 1 / 243000 05EWOOST 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243105 TO BUS 243151 CKT 1 / 243105 05SMILLB 138 243151 05WMILLS 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 243158 CKT 1 / 243151 05WMILLS 138 243158 05WOOSTE 138 1 OPEN BRANCH FROM BUS 243151 TO BUS 245374 CKT 1 / 243151 05WMILLS 138 245374 05WMILLRBG 69.0 1 OPEN BRANCH FROM BUS 243158 TO BUS 245304 CKT 1 / 243158 05WOOSTE 138 245304 05WOOSTER 23.0 1 OPEN BRANCH FROM BUS 243151 TO BUS 245366 CKT Z1 / 243151 05WMILLS 138 245366 05WMILLS 8 12.0 Z1 REMOVE SWSHUNT FROM BUS 243158 / 243158 05WOOSTE 138 OPEN BRANCH FROM BUS 245265 TO BUS 245305 CKT 1 / 245265 05BEALL AV 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247027 TO BUS 245305 CKT 1 / 247027 05MORELDSS 69.0 245305 05WOOSTER 69.0 1 OPEN BRANCH FROM BUS 247401 TO BUS 245305 CKT 1 / 247401 05PRAIRLN SS69.0 245305 05WOOSTER 69.0 1 open branch from bus 245374 to bus 247028 ckt 1 / 245374 05WMILLRBG 69.0 247028 05PAINTVSS 69.0 1 open branch from bus 245368 to bus 245374 ckt 1 / 245368 05SBENTNSS 69.0 245374 05WMILLRBG 69.0 1 remove swshunt from bus 245374 /* 245374 05WMILLRBG 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD983 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245904 | 05SHERWOOD | 69 | 205 | 0.9851 | 0.904 | 8.11 | 8 | N-1-1 | AEP_P1-2_#11787_926 | OPEN BRANCH FROM BUS 243179 TO BUS 245886 CKT 1 / 243179 05S HICKSV 69.0 245886 05MARK CEN 69.0 1 | AEP_P1-2_#11792_901 | OPEN BRANCH FROM BUS 243169 TO BUS 245898 CKT 1 / 243169 05HAVILND2 69.0 245898 05PAULDING 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD984 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245625 | 05MAPLE GR | 69 | 205 | 0.9945 | 0.81298 | 18.152 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD985 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245623 | 05HOLRAN | 69 | 205 | 0.9942 | 0.79198 | 20.222 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD986 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 1.0092 | 0.63963 | 36.957 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD987 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 1.0094 | 0.63858 | 37.082 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD988 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 1.0101 | 0.63832 | 37.178 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD989 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 1.005 | 0.56609 | 43.891 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD990 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 1.0035 | 0.56641 | 43.709 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD991 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 1.0028 | 0.56735 | 43.545 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD992 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 1.003 | 0.5671 | 43.59 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD993 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 0.9919 | 0.61585 | 37.605 | 8 | FB | AEP_P4_#7728_05FREMCT 138_C | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 1 / 243008 05FREMCT 138 243130 05TIFFIN 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243130 CKT 2 / 243008 05FREMCT 138 243130 05TIFFIN 138 2 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 3 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 3 OPEN BRANCH FROM BUS 247523 TO BUS 245617 CKT Z1 / 247523 05FE WFREMSS 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245631 TO BUS 245617 CKT 1 / 245631 05SBC CONT 69.0 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245645 TO BUS 245617 CKT 1 / 245645 005CLYDE 69.0 245617 05FREMONT 69.0 1 REMOVE SWSHUNT FROM BUS 243008 / 243008 05FREMCT 138 REMOVE SWSHUNT FROM BUS 245617 / 243017 05FREMONT 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD994 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244297 | 05JWLC$C2 | 69 | 205 | 1.03 | 0.94022 | 8.978 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD995 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244318 | 05VANSANT | 69 | 205 | 1.0274 | 0.93739 | 9.001 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD996 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244316 | 05TURKEYPN | 69 | 205 | 1.0243 | 0.93399 | 9.031 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD997 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244278 | 05DESKINS | 69 | 205 | 1.0244 | 0.93222 | 9.218 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD998 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244284 | 05GARDNCRK | 69 | 205 | 1.0244 | 0.9322 | 9.22 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD999 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247469 | 05VANCE FORK | 69 | 205 | 1.0214 | 0.92893 | 9.247 | 8 | FB | AEP_P4_#10238_05GARDEC 138_L | OPEN BRANCH FROM BUS 242661 TO BUS 244290 CKT 1 / 242661 05HALES1 138 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244289 TO BUS 244290 CKT 1 / 244289 05HALES BR 69.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 244288 TO BUS 244290 CKT 1 / 244288 05HALES BR 12.0 244290 05HALESBEQ 999 1 OPEN BRANCH FROM BUS 242605 TO BUS 242606 CKT 1 / 242605 05CLNCHR 138 242606 05CLNLFD 138 1 OPEN BRANCH FROM BUS 242606 TO BUS 242639 CKT 1 / 242606 05CLNLFD 138 242639 05FLETCH 138 1 OPEN BRANCH FROM BUS 242639 TO BUS 242801 CKT 1 / 242639 05FLETCH 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242661 CKT 1 / 242648 05GARDEC 138 242661 05HALES1 138 1 OPEN BRANCH FROM BUS 242648 TO BUS 242801 CKT 1 / 242648 05GARDEC 138 242801 05SKEGGS BRZ 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242661 TO BUS 242794 CKT 1 / 242661 05HALES1 138 242794 05SHACKM 138 1 OPEN BRANCH FROM BUS 242801 TO BUS 246828 CKT Z1 / 242801 05SKEGGS BRZ 138 246828 05SKEGGS BR 138 Z1 OPEN BRANCH FROM BUS 242606 TO BUS 242868 CKT 1 / 242606 05CLNLFD 138 242868 05CLNCHFLD 69.0 1 OPEN BRANCH FROM BUS 242648 TO BUS 244284 CKT 1 / 242648 05GARDEC 138 244284 05GARDNCRK 69.0 1 OPEN BRANCH FROM BUS 244308 TO BUS 246828 CKT 1 / 244308 05SKEGGSBR 69.0 246828 05SKEGGS BR 138 1 REMOVE SWSHUNT FROM BUS 242648 / 242648 05GARDEC 138 OPEN BRANCH FROM BUS 244272 TO BUS 244277 CKT 1 / 244272 05CLELL 69.0 244277 05CONSOLID 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244274 CKT 1 / 244272 05CLELL 69.0 244274 05HORNMTN 69.0 1 OPEN BRANCH FROM BUS 244272 TO BUS 244303 CKT 1 / 244272 05CLELL 69.0 244303 05PERMAC 69.0 1 OPEN BRANCH FROM BUS 244279 TO BUS 244289 CKT 1 / 244279 05DISMALSS 69.0 244289 05HALES BR 69.0 1 OPEN BRANCH FROM BUS 244289 TO BUS 244296 CKT 1 / 244289 05HALES BR 69.0 244296 05JWLC$C1 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244308 CKT 1 / 244274 05HORNMTN 69.0 244308 05SKEGGSBR 69.0 1 OPEN BRANCH FROM BUS 244274 TO BUS 244322 CKT 1 / 244274 05HORNMTN 69.0 244322 05VP#6 69.0 1 REMOVE SWSHUNT FROM BUS 244289 / 244289 05HALES BR 69.0 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1000 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244411 | 05JARROLD | 46 | 205 | 0.9919 | 0.89284 | 9.906 | 8 | Line w/o Fault | AEP_P2-1_244448 05SUNDIAL 46.0 244463 05PETTUSSS 46.0 1 | OPEN BRANCH FROM BUS 244448 TO BUS 244463 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1001 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244397 | 05DOROTHY | 46 | 205 | 0.988 | 0.89797 | 9.003 | 8 | Line w/o Fault | AEP_P2-1_244448 05SUNDIAL 46.0 244463 05PETTUSSS 46.0 1 | OPEN BRANCH FROM BUS 244448 TO BUS 244463 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1002 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244285 | 05GRUNDY | 34.5 | 205 | 0.9793 | 0.89908 | 8.022 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1003 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242860 | 05ABERT | 69 | 205 | 1.0143 | 0.9319 | 8.24 | 8 | N-1-1 | AEP_P1-2_#5467_168 | OPEN BRANCH FROM BUS 242737 TO BUS 242785 CKT 1 / 242737 05OPOSSUMCK 138 242785 05S.LYNC 138 1 | AEP_P1-3_#11298_05REUSENS1 138_4 | OPEN BRANCH FROM BUS 242561 TO BUS 242765 CKT 1 / 242561 05BOONSBORO 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242591 TO BUS 242765 CKT 1 / 242591 05CENTRR 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242719 TO BUS 242765 CKT 1 / 242719 05MONEL 138 242765 05REUSENS1 138 1 OPEN BRANCH FROM BUS 242765 TO BUS 242882 CKT 4 / 242765 05REUSENS1 138 242882 05REUSENS 69.0 4 OPEN BRANCH FROM BUS 242765 TO BUS 242889 CKT 1 / 242765 05REUSENS1 138 242889 05REUSENS 34.5 1 REMOVE SWSHUNT FROM BUS 242765 / 242765 05REUSENS1 138 OPEN BRANCH FROM BUS 242860 TO BUS 242882 CKT 1 / 242860 05ABERT 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242876 TO BUS 242882 CKT 1 / 242876 05MONROE A 69.0 242882 05REUSENS 69.0 1 OPEN BRANCH FROM BUS 242882 TO BUS 247360 CKT 1 / 242882 05REUSENS 69.0 247360 05PEAKLANDSS69.0 1 REMOVE SWSHUNT FROM BUS 242882 / 242882 05REUSENS 69.0 OPEN BRANCH FROM BUS 242889 TO BUS 247866 CKT 1 / 242889 05REUSENS 34.5 247866 05GLAMORGNSS34.5 1 REMOVE UNIT 1 FROM BUS 242889 / 242889 05REUSENS 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1004 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0205 | 0.8446 | 17.59 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1005 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 34.5 | 205 | 1.0169 | 0.8689 | 14.8 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1006 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 34.5 | 205 | 1.0226 | 0.8948 | 12.78 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1007 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244213 | 05SEWAGEPL | 34.5 | 205 | 1.0269 | 0.9145 | 11.24 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1008 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244185 | 05BORDENML | 34.5 | 205 | 1.0322 | 0.9204 | 11.18 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1009 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244184 | 05BLUERDGE | 34.5 | 205 | 1.0323 | 0.921 | 11.13 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1010 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244199 | 05KYLEHILL | 34.5 | 205 | 1.0195 | 0.9219 | 9.76 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1011 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244186 | 05CUMBRLND | 34.5 | 205 | 10.84 | 10.7316 | 10.84 | 8 | N-1-1 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1012 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244695 | 05CONNOR F | 34.5 | 205 | 0.9119 | 0.6378 | 27.41 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1013 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244695 | 05CONNOR F | 34.5 | 205 | 0.9209 | 0.6375 | 28.34 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1014 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247205 | 05WELLMONT | 34.5 | 205 | 1.0121 | 0.8508 | 16.13 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1015 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244191 | 05HIGHLAND | 34.5 | 205 | 1.0028 | 0.8737 | 12.91 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1016 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244200 | 05LOVEDALE | 34.5 | 205 | 1.0141 | 0.899 | 11.51 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1017 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244213 | 05SEWAGEPL | 34.5 | 205 | 1.0169 | 0.918 | 9.89 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1018 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244185 | 05BORDENML | 34.5 | 205 | 1.014 | 0.9236 | 9.04 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1019 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244184 | 05BLUERDGE | 34.5 | 205 | 1.0145 | 0.9242 | 9.03 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1020 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244199 | 05KYLEHILL | 34.5 | 205 | 1.0136 | 0.9248 | 8.88 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1021 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244186 | 05CUMBRLND | 34.5 | 205 | 1.0186 | 0.9288 | 8.98 | 8 | N-1-1 | AEP_P1-2_#5700_9206 | OPEN BRANCH FROM BUS 242669 TO BUS 244194 CKT 1 / 242669 05HOLST1 138 244194 05HLSTN5EQ 999 1 OPEN BRANCH FROM BUS 244194 TO BUS 244197 CKT 1 / 244194 05HLSTN5EQ 999 244197 05HOLSTON1 34.5 1 OPEN BRANCH FROM BUS 242669 TO BUS 242739 CKT 1 / 242669 05HOLST1 138 242739 05OREBANK 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 242829 CKT 1 / 242669 05HOLST1 138 242829 05TENNE1 138 1 OPEN BRANCH FROM BUS 242669 TO BUS 360476 CKT 1 / 242669 05HOLST1 138 360476 4BOONE HP 138 1 REMOVE LOAD D7 FROM BUS 242669 / 242669 05HOLST1 138 D7 | AEP_P1-2_#5685_170 | OPEN BRANCH FROM BUS 242729 TO BUS 242762 CKT 1 / 242729 05NAGEL 138 242762 05REEDCR 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1022 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244695 | 05CONNOR F | 34.5 | 205 | 0.9076 | 0.6289 | 27.87 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1023 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244695 | 05CONNOR F | 34.5 | 205 | 0.9177 | 0.6284 | 28.93 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1024 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244145 | 05RADFORD | 34.5 | 205 | 0.9917 | 0.8989 | 9.28 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1025 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244149 | 05DUBLIN | 34.5 | 205 | 0.9839 | 0.9027 | 8.12 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1026 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244146 | 05RADFRD A | 69 | 205 | 0.9887 | 0.9032 | 8.55 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1027 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244140 | 05HICKMAN | 69 | 205 | 0.9939 | 0.9089 | 8.5 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1028 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245065 | 05TORONTO | 69 | 205 | 1.0208 | 0.94 | 8.08 | 8 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1029 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244649 | 05VALLEYCONV | 69 | 205 | 1.0212 | 0.9404 | 8.08 | 8 | N-1-1 | AEP_P1-3_#11775_05E LIVR 138_1 | OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 REMOVE SWSHUNT FROM BUS 245037 / 245037 05E LIVRPO 69.0 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1030 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245065 | 05TORONTO | 69 | 205 | 1.0208 | 0.94 | 8.08 | 8 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1031 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 244649 | 05VALLEYCONV | 69 | 205 | 1.0212 | 0.9404 | 8.08 | 8 | N-1-1 | AEP_P1-2_#8991 | OPEN BRANCH FROM BUS 235293 TO BUS 235404 CKT 1 / 235293 01ARROYJ 138 235404 01S CHST 138 1 OPEN BRANCH FROM BUS 235404 TO BUS 242990 CKT 1 / 235404 01S CHST 138 242990 05E LIVR 138 1 OPEN BRANCH FROM BUS 242990 TO BUS 245037 CKT 1 / 242990 05E LIVR 138 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245035 TO BUS 245037 CKT 1 / 245035 05S.CALCSS 69.0 245037 05E LIVRPO 69.0 1 OPEN BRANCH FROM BUS 245037 TO BUS 245053 CKT 1 / 245037 05E LIVRPO 69.0 245053 05STATE LI 69.0 1 OPEN BRANCH FROM BUS 235292 TO BUS 235293 CKT ZL / 235292 01ARROYO 138 235293 01ARROYJ 138 ZL OPEN BRANCH FROM BUS 235293 TO BUS 235710 CKT 1 / 235293 01ARROYJ 138 235710 01WYLIE R 138 1 | FE-P1-2-MP-138-555T | DISCONNECT BRANCH FROM BUS 235406 TO BUS 235421 CKT 1 /* 01WEIRJT 138 01WEIRTN 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 235710 CKT 1 /* 01WEIRJT 138 01WYLIE R 138 DISCONNECT BRANCH FROM BUS 235406 TO BUS 243113 CKT 1 /* 01WEIRJT 138 05STORON 138 DISCONNECT BRANCH FROM BUS 243113 TO BUS 245049 CKT 1 /* 05STORON 138 05S TORONT 69 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1032 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0164 | 0.932 | 8.44 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1033 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0164 | 0.932 | 8.44 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1034 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0164 | 0.932 | 8.44 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1035 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0143 | 0.93236 | 8.194 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1036 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.0142 | 0.93225 | 8.195 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1037 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0164 | 0.93328 | 8.312 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1038 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0143 | 0.92971 | 8.459 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1039 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0143 | 0.92971 | 8.459 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1040 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0143 | 0.92971 | 8.459 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1041 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.0142 | 0.9296 | 8.46 | 8 | Single | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1042 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.0142 | 0.9296 | 8.46 | 8 | Bus | AEP_P2-2_#10186_05CLYTR2 138_2 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1043 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.0142 | 0.9296 | 8.46 | 8 | FB | AEP_P4_#10186_05CLYTR2 138_E | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1044 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0143 | 0.93099 | 8.331 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1045 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244141 | 05PULASFUR | 34.5 | 205 | 1.0142 | 0.93088 | 8.332 | 8 | FB | AEP_P4_#10188_05CLYTR2 138_Q | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 934750 TO BUS 242853 CKT 1 / 934750 AD1-102 TAP 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242745 TO BUS 242841 CKT 1 / 242745 05PEAKCK 138 242841 05W GLOW 138 1 OPEN BRANCH FROM BUS 242841 TO BUS 242853 CKT 1 / 242841 05W GLOW 138 242853 05WURNO 138 1 OPEN BRANCH FROM BUS 242853 TO BUS 244151 CKT Z1 / 242853 05WURNO 138 244151 05WURNO L 34.5 Z1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 REMOVE SWSHUNT FROM BUS 242853 / 242853 05WURNO 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1046 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245645 | 05CLYDE | 69 | 205 | 0.989 | 0.9048 | 8.42 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1047 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247726 | 05W.FREMONT | 69 | 205 | 1.0064 | 0.9228 | 8.36 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1048 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245611 | 05E FREMON | 69 | 205 | 0.9966 | 0.9081 | 8.85 | 8 | N-1-1 | AEP_P1-3_#12324_05FREMCT 138_1 | OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1049 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245649 | 05BLOOM RD | 69 | 205 | 0.9967 | 0.9081 | 8.86 | 8 | N-1-1 | AEP_P1-3_#12324_05FREMCT 138_1 | OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1050 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 247860 | 05BATTERY SS | 69 | 205 | 0.9974 | 0.9085 | 8.89 | 8 | N-1-1 | AEP_P1-3_#12324_05FREMCT 138_1 | OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1051 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245627 | 05N FREMON | 69 | 205 | 0.999 | 0.9096 | 8.94 | 8 | N-1-1 | AEP_P1-3_#12324_05FREMCT 138_1 | OPEN BRANCH FROM BUS 243008 TO BUS 245614 CKT 1 / 243008 05FREMCT 138 245614 05FREMNT C 69.0 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1052 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244145 | 05RADFORD | 34.5 | 205 | 1.0028 | 0.9123 | 9.05 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1053 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244146 | 05RADFRD A | 69 | 205 | 0.9997 | 0.9183 | 8.14 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1054 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244140 | 05HICKMAN | 69 | 205 | 1.0049 | 0.9239 | 8.1 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1055 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244133 | 05INGLES | 69 | 205 | 1.0099 | 0.9175 | 9.24 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1056 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244148 | 05RIVERBEN | 69 | 205 | 1.0093 | 0.918 | 9.13 | 8 | N-1-1 | AEP_P1-4_05MORGAN C 34.500 | REMOVE SWSHUNT FROM BUS 244135 /05MORGAN C 34.500 | AEP_P1-2_#10186 | OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1057 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245308 | 05GOLDENC8 | 69 | 205 | 0.9941 | 0.8817 | 11.24 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1058 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245272 | 05CLEARCK8 | 69 | 205 | 0.9962 | 0.8841 | 11.21 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1059 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243896 | 05MADSNBRG | 69 | 205 | 1 | 0.8882 | 11.18 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1060 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245311 | 05E UNION | 69 | 205 | 1.0001 | 0.8881 | 11.2 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1061 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245290 | 05N WAYNE8 | 69 | 205 | 1.0016 | 0.89 | 11.16 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1062 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245299 | 05SMITHVIL | 69 | 205 | 1.002 | 0.8904 | 11.16 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1063 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246811 | 05LUK USA | 69 | 205 | 1.0036 | 0.8923 | 11.13 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1064 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245291 | 05N WOOSTE | 69 | 205 | 1.0041 | 0.8929 | 11.12 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1065 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245276 | 05TEKFOR | 69 | 205 | 1.0039 | 0.8924 | 11.15 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1066 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245284 | 05HIGHLNDO | 69 | 205 | 1.0034 | 0.8928 | 11.06 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1067 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245282 | 05HEFFRLN8 | 69 | 205 | 1.0007 | 0.8916 | 10.91 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1068 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245268 | 05BOWMAN S | 23 | 205 | 1.004 | 0.8943 | 10.97 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1069 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245294 | 05GRSTNSL5 | 23 | 205 | 1.004 | 0.8943 | 10.97 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1070 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245285 | 05INTL PAP | 23 | 205 | 1.004 | 0.8943 | 10.97 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1071 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245302 | 05W WOOSTE | 69 | 205 | 1.0023 | 0.8932 | 10.91 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1072 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245281 | 05GRSTSLGR | 23 | 205 | 1.0042 | 0.8946 | 10.96 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1073 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245262 | 05AKRON BR | 23 | 205 | 1.0043 | 0.8947 | 10.96 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1074 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245265 | 05BEALL AV | 69 | 205 | 1.0024 | 0.8931 | 10.93 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1075 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245307 | 05WSTR IRO | 69 | 205 | 1.0028 | 0.8947 | 10.81 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1076 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245295 | 05RUBBRMD2 | 23 | 205 | 1.0095 | 0.8997 | 10.98 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1077 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245297 | 05S WOOSTE | 23 | 205 | 1.0062 | 0.8995 | 10.67 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1078 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245287 | 05MORELND8 | 69 | 205 | 0.9977 | 0.9101 | 8.76 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1079 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245289 | 05N FREDBR | 69 | 205 | 0.9972 | 0.9115 | 8.57 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1080 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245266 | 05BIG PRAI | 69 | 205 | 0.997 | 0.9122 | 8.48 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1081 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245298 | 05SHREVE | 69 | 205 | 0.9986 | 0.9139 | 8.47 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1082 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245286 | 05LOUDNVL8 | 69 | 205 | 0.9943 | 0.913 | 8.13 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1083 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245274 | 05DRAKVAL8 | 69 | 205 | 0.9954 | 0.9141 | 8.13 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1084 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244242 | 05KNOTTY P | 69 | 205 | 1.0183 | 0.92653 | 9.177 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1085 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244286 | 05GRUNDY | 69 | 205 | 1.023 | 0.9192 | 10.38 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1086 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244869 | 05BOSSERMAN | 69 | 205 | 1.0119 | 0.9305 | 8.14 | 8 | Single | AEP_P1-2_#14612 | OPEN BRANCH FROM BUS 244869 TO BUS 247489 CKT 1 / 244869 05BOSSERMAN 69.0 247489 05BOSSERMAN 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1087 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244869 | 05BOSSERMAN | 69 | 205 | 1.0119 | 0.9305 | 8.14 | 8 | FB | AEP_P4_#14347_05BOSSERMAN 138_B2 | OPEN BRANCH FROM BUS 244869 TO BUS 247489 CKT 1 / 244869 05BOSSERMAN 69.0 247489 05BOSSERMAN 138 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1088 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244285 | 05GRUNDY | 34.5 | 205 | 1.0208 | 0.90742 | 11.338 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1089 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244293 | 05BULLCRK | 34.5 | 205 | 1.0179 | 0.9041 | 11.38 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1090 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244534 | 05DALTEX L | 23 | 205 | 1.0006 | 0.918 | 8.26 | 8 | FB | AEP_P4_#14657_05CHAPSS 138_E | OPEN BRANCH FROM BUS 242671 TO BUS 247242 CKT 1 / 242671 05HOPKIN 138 247242 05CHAPSS 138 1 OPEN BRANCH FROM BUS 242705 TO BUS 242735 CKT 1 / 242705 05LOGAN2 138 242735 05NPOINT 138 1 OPEN BRANCH FROM BUS 242735 TO BUS 247242 CKT 1 / 242735 05NPOINT 138 247242 05CHAPSS 138 1 OPEN BRANCH FROM BUS 242735 TO BUS 244530 CKT 1 / 242735 05NPOINT 138 244530 05N.POINT 34.5 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1091 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244301 | 05PATRICK | 34.5 | 205 | 1.0083 | 0.89355 | 11.475 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1092 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244314 | 05THOMAS | 34.5 | 205 | 1.0062 | 0.89124 | 11.496 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1093 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244302 | 05BIGROCK | 34.5 | 205 | 1.0041 | 0.88892 | 11.518 | 8 | FB | AEP_P4_#13219_05LOONEYCR 69.0_C | OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244324 CKT 1 / 244286 05GRUNDY 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244291 TO BUS 244304 CKT 1 / 244291 05HURLEY 69.0 244304 05RAPOCA 69.0 1 OPEN BRANCH FROM BUS 244304 TO BUS 244324 CKT 1 / 244304 05RAPOCA 69.0 244324 05LOONEYCR 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1094 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9973 | 0.89723 | 10.007 | 8 | Bus | AEP_P2-2_#13751_05PAX BRANCH46.0_2 | OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 / 247208 05MOSSYCRK 46.0 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 244899 TO BUS 247334 CKT 1 / 244899 05SCARBRO 46.0 247334 05PAX BRANCH46.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1095 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9973 | 0.89723 | 10.007 | 8 | FB | AEP_P4_#13751_05PAX BRANCH46.0_B | OPEN BRANCH FROM BUS 242564 TO BUS 247333 CKT 1 / 242564 05BRADL1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 242689 TO BUS 247333 CKT 1 / 242689 05KANAWHA1 138 247333 05PAX BRANCH 138 1 OPEN BRANCH FROM BUS 247333 TO BUS 247334 CKT 1 / 247333 05PAX BRANCH 138 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 / 247208 05MOSSYCRK 46.0 247334 05PAX BRANCH46.0 1 OPEN BRANCH FROM BUS 244899 TO BUS 247334 CKT 1 / 244899 05SCARBRO 46.0 247334 05PAX BRANCH46.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1096 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9973 | 0.89462 | 10.268 | 8 | Line w/o Fault | AEP_P2-1_247208 05MOSSYCRK 46.0 247334 05PAX BRANCH 46.0 1 | OPEN BRANCH FROM BUS 247208 TO BUS 247334 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1097 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244887 | 05KINGSTON | 46 | 205 | 0.9973 | 0.89462 | 10.268 | 8 | Line w/o Fault | AEP_P2-1_247206 05EKINGS Z 46.0 247208 05MOSSYCRK 46.0 1 | OPEN BRANCH FROM BUS 247206 TO BUS 247208 CKT 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1098 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245631 | 05SBC CONT | 69 | 205 | 1.0077 | 0.9185 | 8.92 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1099 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245634 | 05STONE ST | 69 | 205 | 1.0069 | 0.9201 | 8.68 | 8 | N-1-1 | AEP_P1-3_#744_05FOSTOR 345_1 | OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 / 242936 05FOSTOR 345 243006 05FOSTOR 138 1 | AEP_P1-2_#5249_11579 | OPEN BRANCH FROM BUS 243009 TO BUS 245616 CKT 1 / 243009 05FRMNT 138 245616 05FREMNTEQ 999 1 OPEN BRANCH FROM BUS 245616 TO BUS 245617 CKT 1 / 245616 05FREMNTEQ 999 245617 05FREMONT 69.0 1 OPEN BRANCH FROM BUS 245616 TO BUS 245618 CKT 1 / 245616 05FREMNTEQ 999 245618 05FREMONT- 12.0 1 OPEN BRANCH FROM BUS 239154 TO BUS 243009 CKT 1 / 239154 02W.FREM 138 243009 05FRMNT 138 1 OPEN BRANCH FROM BUS 243008 TO BUS 243009 CKT 1 / 243008 05FREMCT 138 243009 05FRMNT 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. driven by S1996, additional scope of S1996 needed to address this
AEP-VD1100 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245278 | 05E WOOSTR | 12 | 205 | 0.9456 | 0.8334 | 11.22 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1101 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245292 | 05ORRVIL L | 12 | 205 | 0.9806 | 0.8743 | 10.63 | 8 | N-1-1 | AEP_P1-2_#5120_602 | OPEN BRANCH FROM BUS 239237 TO BUS 243000 CKT 1 / 239237 02CLVR-S 138 243000 05EWOOST 138 1 | AEP_P1-2_#5142_704 | OPEN BRANCH FROM BUS 242954 TO BUS 242978 CKT 1 / 242954 05APPLEC 138 242978 05CANALR 138 1 OPEN BRANCH FROM BUS 242954 TO BUS 243092 CKT 1 / 242954 05APPLEC 138 243092 05SCANTO 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 243000 CKT 1 / 242978 05CANALR 138 243000 05EWOOST 138 1 OPEN BRANCH FROM BUS 242978 TO BUS 245270 CKT 1 / 242978 05CANALR 138 245270 05CANAL RD 69.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1102 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244168 | 05INDEPEND | 69 | 205 | 1.0011 | 0.8928 | 10.83 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1103 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244166 | 05GALAX1 | 69 | 205 | 1.0124 | 0.8983 | 11.41 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1104 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244182 | 05GALAX2 | 69 | 205 | 1.0124 | 0.8984 | 11.4 | 8 | N-1-1 | AEP_P1-2_#14845 | OPEN BRANCH FROM BUS 242683 TO BUS 244287 CKT 1 / 242683 05J.EARL 138 244287 05WOLF GLADE 138 1 | AEP_P1-2_#14840 | OPEN BRANCH FROM BUS 242675 TO BUS 242755 CKT 1 / 242675 05HUFFMN 138 242755 05PIPERS 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1105 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244063 | 05MEADOW C | 34.5 | 205 | 0.9597 | 0.8748 | 8.49 | 8 | N-1-1 | DVP_P1-2: LN 566 | OPEN BRANCH FROM BUS 242519 TO BUS 314912 CKT 1 /* 05CLOVRD 500.00 - 8LEXNGTN 500.00 | AEP_P1-2_#311_5 | OPEN BRANCH FROM BUS 242512 TO BUS 242514 CKT 1 / 242512 05CLOVRD 765 242514 05J.FERR 765 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1106 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244069 | 05NEW CAST | 34.5 | 205 | 0.9616 | 0.8768 | 8.48 | 8 | N-1-1 | DVP_P1-2: LN 566 | OPEN BRANCH FROM BUS 242519 TO BUS 314912 CKT 1 /* 05CLOVRD 500.00 - 8LEXNGTN 500.00 | AEP_P1-2_#311_5 | OPEN BRANCH FROM BUS 242512 TO BUS 242514 CKT 1 / 242512 05CLOVRD 765 242514 05J.FERR 765 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1107 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244077 | 05STONECGA | 34.5 | 205 | 8.13 | 8.0487 | 8.13 | 8 | N-1-1 | DVP_P1-2: LN 566 | OPEN BRANCH FROM BUS 242519 TO BUS 314912 CKT 1 /* 05CLOVRD 500.00 - 8LEXNGTN 500.00 | AEP_P1-2_#311_5 | OPEN BRANCH FROM BUS 242512 TO BUS 242514 CKT 1 / 242512 05CLOVRD 765 242514 05J.FERR 765 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1108 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244150 | 05SMITH LA | 34.5 | 205 | 1.0164 | 0.93465 | 8.175 | 8 | FB | AEP_P4_#10189_05CLYTR2 138_P | OPEN BRANCH FROM BUS 242640 TO BUS 243969 CKT 1 / 242640 05FLOYD 138 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 247868 CKT 3 / 244132 05N.CLAYTREQ 999 247868 05N.CLAYTOR 138 3 OPEN BRANCH FROM BUS 243967 TO BUS 243969 CKT 1 / 243967 05FLOYD 69.0 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244131 TO BUS 244132 CKT 1 / 244131 05N.CLAYTOR 69.0 244132 05N.CLAYTREQ 999 1 OPEN BRANCH FROM BUS 243966 TO BUS 243969 CKT 1 / 243966 05FLOYD 34.5 243969 05FLOYD EQ 999 1 OPEN BRANCH FROM BUS 244132 TO BUS 244138 CKT 3 / 244132 05N.CLAYTREQ 999 244138 05N.CLAYTO 34.5 3 OPEN BRANCH FROM BUS 242535 TO BUS 242610 CKT 1 / 242535 05ALUMRG 138 242610 05CLYTR3 138 1 OPEN BRANCH FROM BUS 242535 TO BUS 242640 CKT 1 / 242535 05ALUMRG 138 242640 05FLOYD 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 247870 CKT 2 / 242609 05CLYTR2 138 247870 05CLAYTR HY2 138 2 OPEN BRANCH FROM BUS 247868 TO BUS 247870 CKT 1 / 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242610 CKT Z1 / 242609 05CLYTR2 138 242610 05CLYTR3 138 Z1 OPEN BRANCH FROM BUS 242609 TO BUS 242634 CKT 1 / 242609 05CLYTR2 138 242634 05EDGEMO 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 242721 CKT 1 / 242609 05CLYTR2 138 242721 05MORGAN 138 1 OPEN BRANCH FROM BUS 242609 TO BUS 934750 CKT 1 / 242609 05CLYTR2 138 934750 AD1-102 TAP 138 1 OPEN BRANCH FROM BUS 242640 TO BUS 242750 CKT 1 / 242640 05FLOYD 138 242750 05PHILPOTT Z 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 247723 CKT 1 / 242750 05PHILPOTT Z 138 247723 05PHILPOTT 138 1 OPEN BRANCH FROM BUS 242750 TO BUS 242844 CKT 1 / 242750 05PHILPOTT Z 138 242844 05W.BASS 138 1 OPEN BRANCH FROM BUS 242907 TO BUS 247870 CKT 1 / 242907 05CLAY-2 11.0 247870 05CLAYTR HY2 138 1 REMOVE SWSHUNT FROM BUS 242609 / 242609 05CLYTR2 138 OPEN BRANCH FROM BUS 243967 TO BUS 244007 CKT 1 / 243967 05FLOYD 69.0 244007 05WOOLWINE 69.0 1 OPEN BRANCH FROM BUS 244131 TO BUS 244133 CKT 1 / 244131 05N.CLAYTOR 69.0 244133 05INGLES 69.0 1 REMOVE UNIT 3 FROM BUS 242907 / 242907 05CLAY-2 11.0 3 REMOVE UNIT 4 FROM BUS 242907 / 242907 05CLAY-2 11.0 4 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1109 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244793 | 05GUTHRIE | 46 | 205 | 0.9997 | 0.9191 | 8.06 | 8 | FB | AEP_P4_#10489_05CHEM 2 138_W | OPEN BRANCH FROM BUS 242576 TO BUS 242593 CKT 1 / 242576 05CAPITOLH 138 242593 05CHEM 2 138 1 OPEN BRANCH FROM BUS 242578 TO BUS 242593 CKT 1 / 242578 05CARB Z 138 242593 05CHEM 2 138 1 OPEN BRANCH FROM BUS 242592 TO BUS 242593 CKT Z1 / 242592 05CHEM 1 138 242593 05CHEM 2 138 Z1 OPEN BRANCH FROM BUS 242592 TO BUS 242740 CKT 2 / 242592 05CHEM 1 138 242740 05ORTIN 138 2 OPEN BRANCH FROM BUS 242592 TO BUS 242836 CKT 1 / 242592 05CHEM 1 138 242836 05TURNE1 138 1 OPEN BRANCH FROM BUS 242593 TO BUS 242617 CKT 1 / 242593 05CHEM 2 138 242617 05DALEWD 138 1 OPEN BRANCH FROM BUS 242592 TO BUS 244781 CKT 1 / 242592 05CHEM 1 138 244781 05CHEM 1 46.0 1 OPEN BRANCH FROM BUS 242592 TO BUS 244783 CKT 1 / 242592 05CHEM 1 138 244783 05CHEM 3 46.0 1 OPEN BRANCH FROM BUS 242593 TO BUS 244781 CKT 1 / 242593 05CHEM 2 138 244781 05CHEM 1 46.0 1 OPEN BRANCH FROM BUS 242593 TO BUS 244782 CKT 1 / 242593 05CHEM 2 138 244782 05CHEM 2 46.0 1 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Solved by B3100 new scope presented in 7/17/2020 Western SRRTEP
AEP-VD1110 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.9997 | 0.86959 | 13.011 | 8 | FB | DVP_P4-5: L542-2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314794 CKT 1 /* 3DOOMS 115.00 - 6DOOMS 230.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1111 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.9997 | 0.86958 | 13.012 | 8 | FB | DVP_P4-5: L842-2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314794 CKT 3 /* 3DOOMS 115.00 - 6DOOMS 230.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1112 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.9997 | 0.86967 | 13.003 | 8 | FB | DVP_P4-2: 16042 | OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1113 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.9997 | 0.86983 | 12.987 | 8 | FB | DVP_P4-2: 10242 | OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314812 CKT 1 /* 3BRND DP 115.00 - 3STAUNTN 115.00 OPEN BUS 314791 /* ISLAND: 3BRND DP 115.00 OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1114 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247086 | 05REDHIL | 115 | 205 | 0.9997 | 0.86967 | 13.003 | 8 | Bus | DVP_P2-2: DOOMS B2 | OPEN BRANCH FROM BUS 314767 TO BUS 314793 CKT 1 /* 3MIDWAY 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314791 TO BUS 314793 CKT 1 /* 3BRND DP 115.00 - 3DOOMS 115.00 OPEN BRANCH FROM BUS 314793 TO BUS 314819 CKT 1 /* 3DOOMS 115.00 - 3WAYNSBO 115.00 |  |  | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1115 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 1.0049 | 0.6438 | 36.11 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1116 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 0.986 | 0.6468 | 33.92 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1117 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.0088 | 0.7217 | 28.71 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1118 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.0089 | 0.7217 | 28.72 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1119 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.0009 | 0.722 | 27.89 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1120 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.0009 | 0.722 | 27.89 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1121 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0022 | 0.8366 | 16.56 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1122 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0022 | 0.8366 | 16.56 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1123 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 0.9962 | 0.8366 | 15.96 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1124 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 0.9962 | 0.8366 | 15.96 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1125 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 1.0029 | 0.6408 | 36.21 | 8 | N-1-1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1126 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 1.006 | 0.7114 | 29.46 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1127 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 1.006 | 0.7115 | 29.45 | 8 | N-1-1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1128 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243060 | 05NINTIE | 138 | 205 | 0.985 | 0.6465 | 33.85 | 8 | N-1-1 | AEP_P1-2_#5222_2003 | OPEN BRANCH FROM BUS 242964 TO BUS 243060 CKT 1 / 242964 05BOLIVA 138 243060 05NINTIE 138 1 OPEN BRANCH FROM BUS 242964 TO BUS 243092 CKT 1 / 242964 05BOLIVA 138 243092 05SCANTO 138 1 | AEP_P1-3_#11756_05W.NEW PHIL 138_2 | OPEN BRANCH FROM BUS 243156 TO BUS 245257 CKT 2 / 243156 05W.NEW PHIL 138 245257 05W N PHIL 69.0 2 OPEN BRANCH FROM BUS 243020 TO BUS 243056 CKT 1 / 243020 05HILLVI 138 243056 05NEWCOM 138 1 OPEN BRANCH FROM BUS 243020 TO BUS 243156 CKT 1 / 243020 05HILLVI 138 243156 05W.NEW PHIL 138 1 REMOVE SWSHUNT FROM BUS 243156 / 243156 05W.NEW PHIL 138 REMOVE SWSHUNT FROM BUS 243020 / 243020 05HILLVI 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1129 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242626 | 05E.HUNTING2 | 138 | 205 | 0.9972 | 0.7119 | 28.53 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1130 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 245664 | 05E.HUNTING1 | 138 | 205 | 0.9972 | 0.7119 | 28.53 | 8 | N-1-1 | AEP_P1-2_#5877_186 | OPEN BRANCH FROM BUS 243064 TO BUS 245664 CKT 1 / 243064 05NPROCT 138 245664 05E.HUNTING1 138 1 | AEP_P1-2_#13746 | OPEN BRANCH FROM BUS 242621 TO BUS 242626 CKT 1 / 242621 05DARRH1 138 242626 05E.HUNTING2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1131 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0067 | 0.8318 | 17.49 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1132 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0067 | 0.8318 | 17.49 | 8 | N-1-1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1133 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 246155 | 05FORD LIMA2 | 138 | 205 | 1.0019 | 0.8319 | 17 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1134 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243765 | 05FORD LIMA1 | 138 | 205 | 1.0019 | 0.8319 | 17 | 8 | N-1-1 | AEP_P1-2_#5226_2061 | OPEN BRANCH FROM BUS 242989 TO BUS 246155 CKT 1 / 242989 05E LIMA 138 246155 05FORD LIMA2 138 1 | AEP_P1-3_#12222_05ROCKHILL2 138_1-2 | OPEN BRANCH FROM BUS 242989 TO BUS 245516 CKT 1 / 242989 05E LIMA 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 242995 TO BUS 245516 CKT 1 / 242995 05EASTOW 138 245516 05ROCKHILL2 138 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 1 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 1 OPEN BRANCH FROM BUS 245516 TO BUS 245836 CKT 2 / 245516 05ROCKHILL2 138 245836 05ROCKHILL 34.5 2 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1135 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242959 | 05BELDVL | 138 | 205 | 1.0033 | 0.9217 | 8.16 | 8 | N-1-1 | AEP_P1-3_#11759_05WAGENHALS2 138_2 | OPEN BRANCH FROM BUS 243139 TO BUS 245195 CKT 2 / 243139 05WAGENHALS2 138 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245192 TO BUS 245195 CKT 2 / 245192 05WAGNHAL2 69.0 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245193 TO BUS 245195 CKT 1 / 245193 05WAGNHAL2 23.0 245195 05WAGNL2EQ 999 1 OPEN BRANCH FROM BUS 243139 TO BUS 246267 CKT Z1 / 243139 05WAGENHALS2 138 246267 05WAGENHALS1 138 Z1 OPEN BRANCH FROM BUS 242980 TO BUS 243139 CKT 2 / 242980 05CANTNC 138 243139 05WAGENHALS2 138 2 OPEN BRANCH FROM BUS 243139 TO BUS 244070 CKT 1 / 243139 05WAGENHALS2 138 244070 05JUNE ROAD 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 243772 CKT 2 / 243139 05WAGENHALS2 138 243772 05LTV2 138 2 OPEN BRANCH FROM BUS 243052 TO BUS 243139 CKT 1 / 243052 05NECANT 138 243139 05WAGENHALS2 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 244943 CKT 1 / 243139 05WAGENHALS2 138 244943 05PACKARD BP 138 1 OPEN BRANCH FROM BUS 245127 TO BUS 245192 CKT 2 / 245127 05E CANTON 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245189 TO BUS 245192 CKT 2 / 245189 05W LOUISV 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245193 TO BUS 247301 CKT 1 / 245193 05WAGNHAL2 23.0 247301 05GEORGTW2 23.0 1 | AEP_P1-2_#6604_3700745 | OPEN BRANCH FROM BUS 243077 TO BUS 243134 CKT 1 / 243077 05PROMWY 138 243134 05W.CANTON1 138 1 OPEN BRANCH FROM BUS 243077 TO BUS 243142 CKT 1 / 243077 05PROMWY 138 243142 05WAYVIE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1136 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 243142 | 05WAYVIE | 138 | 205 | 1.0038 | 0.9223 | 8.15 | 8 | N-1-1 | AEP_P1-3_#11759_05WAGENHALS2 138_2 | OPEN BRANCH FROM BUS 243139 TO BUS 245195 CKT 2 / 243139 05WAGENHALS2 138 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245192 TO BUS 245195 CKT 2 / 245192 05WAGNHAL2 69.0 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245193 TO BUS 245195 CKT 1 / 245193 05WAGNHAL2 23.0 245195 05WAGNL2EQ 999 1 OPEN BRANCH FROM BUS 243139 TO BUS 246267 CKT Z1 / 243139 05WAGENHALS2 138 246267 05WAGENHALS1 138 Z1 OPEN BRANCH FROM BUS 242980 TO BUS 243139 CKT 2 / 242980 05CANTNC 138 243139 05WAGENHALS2 138 2 OPEN BRANCH FROM BUS 243139 TO BUS 244070 CKT 1 / 243139 05WAGENHALS2 138 244070 05JUNE ROAD 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 243772 CKT 2 / 243139 05WAGENHALS2 138 243772 05LTV2 138 2 OPEN BRANCH FROM BUS 243052 TO BUS 243139 CKT 1 / 243052 05NECANT 138 243139 05WAGENHALS2 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 244943 CKT 1 / 243139 05WAGENHALS2 138 244943 05PACKARD BP 138 1 OPEN BRANCH FROM BUS 245127 TO BUS 245192 CKT 2 / 245127 05E CANTON 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245189 TO BUS 245192 CKT 2 / 245189 05W LOUISV 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245193 TO BUS 247301 CKT 1 / 245193 05WAGNHAL2 23.0 247301 05GEORGTW2 23.0 1 | AEP_P1-2_#6604_3700745 | OPEN BRANCH FROM BUS 243077 TO BUS 243134 CKT 1 / 243077 05PROMWY 138 243134 05W.CANTON1 138 1 OPEN BRANCH FROM BUS 243077 TO BUS 243142 CKT 1 / 243077 05PROMWY 138 243142 05WAYVIE 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1137 | 2020RTEP 2025SUM_nonFSA_Final_07012020.raw | 242959 | 05BELDVL | 138 | 205 | 0.9982 | 0.917 | 8.12 | 8 | N-1-1 | AEP_P1-2_#6604_3700745 | OPEN BRANCH FROM BUS 243077 TO BUS 243134 CKT 1 / 243077 05PROMWY 138 243134 05W.CANTON1 138 1 OPEN BRANCH FROM BUS 243077 TO BUS 243142 CKT 1 / 243077 05PROMWY 138 243142 05WAYVIE 138 1 | AEP_P1-3_#11759_05WAGENHALS2 138_2 | OPEN BRANCH FROM BUS 243139 TO BUS 245195 CKT 2 / 243139 05WAGENHALS2 138 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245192 TO BUS 245195 CKT 2 / 245192 05WAGNHAL2 69.0 245195 05WAGNL2EQ 999 2 OPEN BRANCH FROM BUS 245193 TO BUS 245195 CKT 1 / 245193 05WAGNHAL2 23.0 245195 05WAGNL2EQ 999 1 OPEN BRANCH FROM BUS 243139 TO BUS 246267 CKT Z1 / 243139 05WAGENHALS2 138 246267 05WAGENHALS1 138 Z1 OPEN BRANCH FROM BUS 242980 TO BUS 243139 CKT 2 / 242980 05CANTNC 138 243139 05WAGENHALS2 138 2 OPEN BRANCH FROM BUS 243139 TO BUS 244070 CKT 1 / 243139 05WAGENHALS2 138 244070 05JUNE ROAD 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 243772 CKT 2 / 243139 05WAGENHALS2 138 243772 05LTV2 138 2 OPEN BRANCH FROM BUS 243052 TO BUS 243139 CKT 1 / 243052 05NECANT 138 243139 05WAGENHALS2 138 1 OPEN BRANCH FROM BUS 243139 TO BUS 244943 CKT 1 / 243139 05WAGENHALS2 138 244943 05PACKARD BP 138 1 OPEN BRANCH FROM BUS 245127 TO BUS 245192 CKT 2 / 245127 05E CANTON 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245189 TO BUS 245192 CKT 2 / 245189 05W LOUISV 69.0 245192 05WAGNHAL2 69.0 2 OPEN BRANCH FROM BUS 245193 TO BUS 247301 CKT 1 / 245193 05WAGNHAL2 23.0 247301 05GEORGTW2 23.0 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1138 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 0.9957 | 0.8771 | 11.86 | 8 | N-1-1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1139 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 0.9942 | 0.8889 | 10.53 | 8 | N-1-1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1140 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243933 | 05AMBLER RDG | 138 | 205 | 0.9921 | 0.8518 | 14.03 | 8 | N-1-1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. driven by S1996, additional scope of S1996 needed to address this
AEP-VD1141 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247714 | 05BROAD RUN | 138 | 205 | 0.9867 | 0.8519 | 13.48 | 8 | N-1-1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. driven by S1996, additional scope of S1996 needed to address this
AEP-VD1142 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 1.0085 | 0.9173 | 9.12 | 8 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 /* 3FORK UNION 115.00 - 3BREMO 115.00 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 /* 3BREMO 115.00 - 6BREMO 230.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1143 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 1.0066 | 0.8768 | 12.98 | 8 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1144 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 1.0037 | 0.8886 | 11.51 | 8 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1145 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 1.0073 | 0.902 | 10.53 | 8 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 /* 3BREMO 115.00 - 6BREMO 230.00 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 /* 3FORK UNION 115.00 - 3BREMO 115.00 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1146 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 243933 | 05AMBLER RDG | 138 | 205 | 1.0019 | 0.852 | 14.99 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. driven by S1996, additional scope of S1996 needed to address this
AEP-VD1147 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 247714 | 05BROAD RUN | 138 | 205 | 1.002 | 0.8522 | 14.98 | 8 | N-1-1 | AEP_P1-2_#13764_29760 | OPEN BRANCH FROM BUS 243933 TO BUS 247793 CKT 1 / 243933 05AMBLER RDG 138 247793 05LINDEN RD 138 1 | AEP_P1-2_#14960 | OPEN BRANCH FROM BUS 242637 TO BUS 247558 CKT 1 / 242637 05FLATWO 138 247558 05JARRETT 138 1 OPEN BRANCH FROM BUS 242637 TO BUS 247794 CKT 1 / 242637 05FLATWO 138 247794 05COCO 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. driven by S1996, additional scope of S1996 needed to address this
AEP-VD1148 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244302 | 05BIGROCK | 34.5 | 205 | 1.0012 | 0.8243 | 17.69 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1149 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244302 | 05BIGROCK | 34.5 | 205 | 1.0012 | 0.8294 | 17.18 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1150 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244293 | 05BULLCRK | 34.5 | 205 | 1.015 | 0.8411 | 17.39 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1151 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244293 | 05BULLCRK | 34.5 | 205 | 1.015 | 0.8461 | 16.89 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1152 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244285 | 05GRUNDY | 34.5 | 205 | 1.018 | 0.8447 | 17.33 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1153 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244285 | 05GRUNDY | 34.5 | 205 | 1.018 | 0.8496 | 16.84 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1154 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244286 | 05GRUNDY | 69 | 205 | 1.0204 | 0.8637 | 15.67 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1155 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244286 | 05GRUNDY | 69 | 205 | 1.0204 | 0.8681 | 15.23 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1156 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244301 | 05PATRICK | 34.5 | 205 | 1.0053 | 0.8293 | 17.6 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1157 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244301 | 05PATRICK | 34.5 | 205 | 1.0053 | 0.8344 | 17.09 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1158 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244314 | 05THOMAS | 34.5 | 205 | 1.0032 | 0.8268 | 17.64 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-2_#5325_160 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242661 / 242661 05HALES1 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1159 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244314 | 05THOMAS | 34.5 | 205 | 1.0032 | 0.8319 | 17.13 | 8 | N-1-1 | AEP_P1-2_#11358_238 | OPEN BRANCH FROM BUS 244279 TO BUS 244309 CKT 1 / 244279 05DISMALSS 69.0 244309 05SLATECRK 69.0 1 OPEN BRANCH FROM BUS 244286 TO BUS 244327 CKT 1 / 244286 05GRUNDY 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244324 TO BUS 244327 CKT 1 / 244324 05LOONEYCR 69.0 244327 05TWENTYMI 69.0 1 OPEN BRANCH FROM BUS 244309 TO BUS 244327 CKT 1 / 244309 05SLATECRK 69.0 244327 05TWENTYMI 69.0 1 | AEP_P1-3_#11385_05LOONEY 138_1 | OPEN BRANCH FROM BUS 242706 TO BUS 244326 CKT 1 / 242706 05LOONEY 138 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244324 TO BUS 244326 CKT 1 / 244324 05LOONEYCR 69.0 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 244325 TO BUS 244326 CKT 1 / 244325 05LOONEYCR 34.5 244326 05LOONEYEQ 999 1 OPEN BRANCH FROM BUS 242546 TO BUS 242742 CKT 1 / 242546 05BAILS1 138 242742 05PADFOR 138 1 OPEN BRANCH FROM BUS 242661 TO BUS 242662 CKT Z1 / 242661 05HALES1 138 242662 05HALES2 138 Z1 OPEN BRANCH FROM BUS 242662 TO BUS 242702 CKT 1 / 242662 05HALES2 138 242702 05LEFTFK 138 1 OPEN BRANCH FROM BUS 242662 TO BUS 242804 CKT 1 / 242662 05HALES2 138 242804 05SOURWO 138 1 OPEN BRANCH FROM BUS 242742 TO BUS 247290 CKT 1 / 242742 05PADFOR 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242804 TO BUS 247290 CKT 1 / 242804 05SOURWO 138 247290 05HARMON 138 1 OPEN BRANCH FROM BUS 242702 TO BUS 242706 CKT 1 / 242702 05LEFTFK 138 242706 05LOONEY 138 1 REMOVE SWSHUNT FROM BUS 242662 / 242662 05HALES2 138 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1160 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244579 | 05NEWCAMP | 69 | 205 | 1.0175 | 0.8594 | 15.81 | 8 | N-1-1 | AEP_P1-3_#13697_05JOHNSC 138_1 | OPEN BRANCH FROM BUS 243662 TO BUS 243695 CKT 1 / 243662 05JOHNCREQ 999 243695 05JOHNSC 138 1 OPEN BRANCH FROM BUS 243662 TO BUS 244606 CKT 1 / 243662 05JOHNCREQ 999 244606 05JOHNSCR 69.0 1 OPEN BRANCH FROM BUS 243662 TO BUS 244607 CKT 1 / 243662 05JOHNCREQ 999 244607 05JOHNSCRK 34.5 1 | AEP_P1-2_#5967_183 | OPEN BRANCH FROM BUS 243690 TO BUS 243807 CKT 1 / 243690 05HATFLD 138 243807 05HATFLDEQ 999 1 OPEN BRANCH FROM BUS 243807 TO BUS 244582 CKT 1 / 243807 05HATFLDEQ 999 244582 05HATFLD 69.0 1 OPEN BRANCH FROM BUS 243807 TO BUS 244583 CKT 1 / 243807 05HATFLDEQ 999 244583 05HATFLD 46.0 1 OPEN BRANCH FROM BUS 242562 TO BUS 242599 CKT 1 / 242562 05BORLND 138 242599 05CINDER 138 1 OPEN BRANCH FROM BUS 242562 TO BUS 243690 CKT 1 / 242562 05BORLND 138 243690 05HATFLD 138 1 OPEN BRANCH FROM BUS 242599 TO BUS 242810 CKT 1 / 242599 05CINDER 138 242810 05SPRIG2 138 1 OPEN BRANCH FROM BUS 243690 TO BUS 243694 CKT 1 / 243690 05HATFLD 138 243694 05INEZ 138 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1161 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244579 | 05NEWCAMP | 69 | 205 | 0.9881 | 0.8595 | 12.86 | 8 | N-1-1 | AEP_P1-2_#5967_183 | OPEN BRANCH FROM BUS 243690 TO BUS 243807 CKT 1 / 243690 05HATFLD 138 243807 05HATFLDEQ 999 1 OPEN BRANCH FROM BUS 243807 TO BUS 244582 CKT 1 / 243807 05HATFLDEQ 999 244582 05HATFLD 69.0 1 OPEN BRANCH FROM BUS 243807 TO BUS 244583 CKT 1 / 243807 05HATFLDEQ 999 244583 05HATFLD 46.0 1 OPEN BRANCH FROM BUS 242562 TO BUS 242599 CKT 1 / 242562 05BORLND 138 242599 05CINDER 138 1 OPEN BRANCH FROM BUS 242562 TO BUS 243690 CKT 1 / 242562 05BORLND 138 243690 05HATFLD 138 1 OPEN BRANCH FROM BUS 242599 TO BUS 242810 CKT 1 / 242599 05CINDER 138 242810 05SPRIG2 138 1 OPEN BRANCH FROM BUS 243690 TO BUS 243694 CKT 1 / 243690 05HATFLD 138 243694 05INEZ 138 1 | AEP_P1-3_#13697_05JOHNSC 138_1 | OPEN BRANCH FROM BUS 243662 TO BUS 243695 CKT 1 / 243662 05JOHNCREQ 999 243695 05JOHNSC 138 1 OPEN BRANCH FROM BUS 243662 TO BUS 244606 CKT 1 / 243662 05JOHNCREQ 999 244606 05JOHNSCR 69.0 1 OPEN BRANCH FROM BUS 243662 TO BUS 244607 CKT 1 / 243662 05JOHNCREQ 999 244607 05JOHNSCRK 34.5 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1162 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242594 | 05CHERCK | 138 | 205 | 1.0052 | 0.89079 | 11.441 | 8 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1163 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242604 | 05CLIFFT | 138 | 205 | 1.0082 | 0.87931 | 12.889 | 8 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1164 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242818 | 05STOTES | 138 | 205 | 1.0048 | 0.92234 | 8.246 | 8 | N-1-1 | AEP_P1-2_#7561_2602421 | OPEN BRANCH FROM BUS 242564 TO BUS 242653 CKT 1 / 242564 05BRADL1 138 242653 05GRANDV 138 1 | AEP_P1-2_#5349_2440 | OPEN BRANCH FROM BUS 242650 TO BUS 242668 CKT 1 / 242650 05GLENL1 138 242668 05HINTON 138 1 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1165 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244446 | 05SOAPSTONE | 138 | 205 | 0.9975 | 0.81395 | 18.355 | 8 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1166 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244423 | 05JAMES RIVR | 138 | 205 | 1.0007 | 0.86715 | 13.355 | 8 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1167 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 1.0015 | 0.87718 | 12.432 | 8 | N-1-1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1168 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244446 | 05SOAPSTONE | 138 | 205 | 0.9916 | 0.82167 | 16.993 | 8 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1169 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 244423 | 05JAMES RIVR | 138 | 205 | 0.9966 | 0.87317 | 12.343 | 8 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
AEP-VD1170 | 2020RTEP 2025WIN_nonFSA_Final_07012020.raw | 242613 | 05COLLEEN SS | 138 | 205 | 0.9977 | 0.88283 | 11.487 | 8 | N-1-1 | DVP_P1-3: 6BREMO-TX#9 | OPEN BRANCH FROM BUS 314744 TO BUS 314747 CKT 1 | DVP_P1-2: LN 1030 | OPEN BRANCH FROM BUS 313708 TO BUS 314744 CKT 1 | No | Part 4: Voltage Limits | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.

## FERC Form 715 Short Circuit
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | Bus KV | Area | Breaker | Rating Type | DUTY_P | DUTY_A | BKR_CAPA (A) | Pre-fault Voltage (KV) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## FERC Form 715 Stability
Reserved(FG# assigned by PJM) | Analysis dynamics case info | Stability issue category | Bus # | Bus Name | Area | Stability Contingency description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## FERC Form 715 Other
Reserved(FG# assigned by PJM) | Analysis Case | Areas | Facility Name | Violations details | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment