## Notes
Thermal analysis column headings
Column Heading | Title | Description
Reserved(FG# assinged by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Fr Bus | From Bus Number | PSSE model bus number corresponding to the FROM bus of a facility identified as a potential violation
Fr Name | From Bus Name | PSSE model bus name corresponding to the FROM bus of a facility identified as a potential violation
To Bus | To Bus Number | PSSE model bus number corresponding to the TO bus of a facility identified as a potential violation
To Name | To Bus Name | PSSE model bus name corresponding to the TO bus of a facility identified as a potential violation
Tert Bus | Tertiary Bus Number | PSSE model bus number corresponding to the tertiary bus of a facility identified as a potential violation
Tert Name | Tertiary Bus Name | PSSE model bus name corresponding to the tertiary bus of a facility identified as a potential violation
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Facility Rating | Applicable thermal rating (MVA) of facility
DC Ld(%) | Direct Current Loading percentage | Percentage above Line Rating determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above Line Rating determined from AC testing
Cont Type | Contingency Type | N-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Conductor Rating (MVA) | Conductor Rating | Normal/Long Term Emergency/Short Term Emergency/Load Dump ratings of conductor
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Magnitude analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Upper/Lower Limit | High/Low Voltage Limit (P.U.) | Threshold of Per Unit High/Low voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Type | Contingency 2 Type | N-1-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower)
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Drop analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Vdrop (%) | Voltage Drop | The percentage that the voltage has dropped as a result of the contingency
Delta Voltage Limit | Voltage Drop Limit | Threshold of percentage drop, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Short Circuit analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | Short Circuit model bus number where breaker is located
Bus Name | Bus Name | Aspen bus name and voltage where breaker is located
Bus KV | BUS Voltage | Nominal BUS voltage
Area | Area Number | Area number of bus identified as potential violation
Breaker | Breaker Name | Breaker name as given by Transmission Owner
Rating Type | Type of Breaker | Symmetrical (S) or Total (T) rated type of breaker
DUTY_P | Duty Percentage | The percentage of the asymmetrical fault current divided by breaker capacity
DUTY_A | Asymmetrical Fault Current | The combination of the symmetrical component and the direct current component of the current.
BKR_CAPA (A) | Breaker Capacity | Breaker’s derated interrupting capability, (A)
Pre-fault Voltage (KV) | Pre-fault KV | Voltage on the bus prior to fault event
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Stability analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis dynamics case info. | Analysis dynamics case info. | Dynamics case year, loading condition, MMWG Series. For example, MMWG 2018 Series 2023 SLL case.
Stability issue category | Stability issue category | Stability issue category: transient stability or damping or dynamic voltage recovery or voltage ride through
Bus # | Bus number | Bus number of the identified plant or station in the analysis power flow model.
Bus Name | Bus name | Bus name of the identified plant or station in the analysis power flow model.
Area | Area | Area number of the identified plant or station.
Stability Contingency description | Contingency description | Detailed contingency description that causes the identified potential stability issue including sequence and fault clearing times.
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Other analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Facility Name | Facility Name | Facilities such as line, substation, generator, etc.
Violations details | Violations details | TO to describe the details of the violation
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Purpose of FERC FORM 715 VIOLATION SUBMISSIONS:
PJM seeks Transmission Owner (TO) criteria violation submissions on facilities in accordance with Local TO criteria. This would also include violations which are not power flow violations of criteria.
Criteria applied by Transmission Owner:
FERC Form 715 Analysis (Thermal/Voltage Magnitude/Voltage Drop/Short Circuit/Stability/Other)
TERMINOLOGY USED IN TEMPLATE:
Descriptions of the column headings used in each Excel tab are provided below.
ANALYSIS PROCEDURE:
Transmission Owners are expected to identify FERC Form 715 violations. All violations are to be captured and recorded in the applicable Excel tab. Please use the corresponding tabs based on the type of violation below:
  * FERC Form 715 Thermal tab should be used to enter thermal violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Magnitude tab should be used to enter voltage magnitude violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Drop tab should be used to enter voltage drop/rise violations associated with FERC Form 715 criteria
  * FERC Form 715 Short Circuit tab should be used to enter short circuit violations associated with FERC Form 715 criteria
  * FERC Form 715 Stability tab should be used to enter stability violations associated with FERC Form 715 criteria
  * FERC Form 715 Other tab should be used to enter violations associated with FERC Form 715 criteria which can not be included in the other tabs
TRANSMISSION OWNER CRITERIA:
In addition to the NERC and PJM criteria included in RTEP studies, PJM also considers Transmission Owner specific criteria. Individual TO criteria can be found at the following link:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx

## FERC Form 715 Voltage Magnitude
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Contingency 1 description | Cont 2 Name | Contingency 2 description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
ATSI-LLVM1 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.057 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM2 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.0608 | 1.05/0.90 | Single | DAY_P1_6648_BELLEFONTAINE_BLUE JACKET_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM3 | LL | 240604 | 02PRSPCTSR | 69 | 202 | 1.0481 | 1.0547 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM4 | LL | 240604 | 02PRSPCTSR | 69 | 202 | 1.0481 | 1.0572 | 1.05/0.90 | Single | DAY_P1_6648_BELLEFONTAINE_BLUE JACKET_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM5 | LL | 240602 | 02RADNOR | 69 | 202 | 1.0466 | 1.0532 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM6 | LL | 240602 | 02RADNOR | 69 | 202 | 1.0466 | 1.055 | 1.05/0.90 | Single | DAY_P1_6648_BELLEFONTAINE_BLUE JACKET_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM7 | LL | 240605 | 02RICHWOOD | 69 | 202 | 1.0503 | 1.0569 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM8 | LL | 240605 | 02RICHWOOD | 69 | 202 | 1.0503 | 1.0608 | 1.05/0.90 | Single | DAY_P1_6648_BELLEFONTAINE_BLUE JACKET_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM9 | LL | 240601 | 02SCIOTO R | 69 | 202 | 1.0468 | 1.0528 | 1.05/0.90 | Single | DAY_P1_6648_BELLEFONTAINE_BLUE JACKET_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM10 | LL | 240601 | 02SCIOTO R | 69 | 202 | 1.0468 | 1.0533 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM11 | LL | 239135 | 02TANGY | 69 | 202 | 1.0493 | 1.0559 | 1.05/0.90 | Single | AEP_P2-1_242925 05KAMMER 765 270162 AB2-067 TAP 765 1 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM12 | LL | 239858 | 02ADM-RIDG | 69 | 202 | 1.0517 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM13 | LL | 239827 | 02CALLCHEM | 69 | 202 | 1.0498 | 1.0531 | 1.05/0.90 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM14 | LL | 239830 | 02MAN.RD.E | 69 | 202 | 1.0523 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM15 | LL | 239835 | 02MAN.RD.W | 69 | 202 | 1.0526 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM16 | LL | 239829 | 02MARS | 69 | 202 | 1.0507 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM17 | LL | 239904 | 02MCKNITE | 69 | 202 | 1.0507 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM18 | LL | 239044 | 02PINE P | 69 | 202 | 1.0528 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM19 | LL | 239836 | 02RICHARD | 69 | 202 | 1.0525 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM20 | LL | 239828 | 02ROES.BRN | 69 | 202 | 1.0502 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM21 | LL | 239834 | 02WARRENDA | 69 | 202 | 1.0526 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM22 | LL | 239931 | 02WEXFORD | 69 | 202 | 1.0523 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM23 | LL | 238747 | 02GALION | 69 | 202 | 1.0458 | 1.0513 | 1.05/0.90 | Single | AEP_P1-4_05OHIOCT 345.00 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM24 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.0557 | 1.05/0.90 | Single | ATSI-P1-2-OES-69-022 | * KIRBY-KIRBY TAP 69KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM25 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.0557 | 1.05/0.90 | Single | ATSI-P1-2-OES-69-016B | * KIRBY - TANGY 69KV LINE FAULT |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM26 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.056 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-006 | * CRISSINGER - ROBERTS 138.00KV LINE FAULT |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM27 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | 1.0645 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-008B | * CRISSINGER-KIRBY 138KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM28 | LL | 240604 | 02PRSPCTSR | 69 | 202 | 1.0481 | 1.0533 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-006 | * CRISSINGER - ROBERTS 138.00KV LINE FAULT |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM29 | LL | 240604 | 02PRSPCTSR | 69 | 202 | 1.0481 | 1.0597 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-008B | * CRISSINGER-KIRBY 138KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM30 | LL | 240602 | 02RADNOR | 69 | 202 | 1.0466 | 1.0569 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-008B | * CRISSINGER-KIRBY 138KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM31 | LL | 240605 | 02RICHWOOD | 69 | 202 | 1.0503 | 1.056 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-006 | * CRISSINGER - ROBERTS 138.00KV LINE FAULT |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM32 | LL | 240605 | 02RICHWOOD | 69 | 202 | 1.0503 | 1.0644 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-008B | * CRISSINGER-KIRBY 138KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM33 | LL | 240601 | 02SCIOTO R | 69 | 202 | 1.0468 | 1.0531 | 1.05/0.90 | Single | ATSI-P1-2-OES-138-008B | * CRISSINGER-KIRBY 138KV LINE OUTAGE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM34 | LL | 240629 | 02KIRBY | 69 | 202 | 1.0503 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM35 | LL | 240605 | 02RICHWOOD | 69 | 202 | 1.0503 | - | 1.05/0.90 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM36 | LL | 240597 | 02SCIO + | 69 | 202 | 1.0483 | 1.0531 | 1.05/0.90 | Single | AEP_P1-2_#706 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM37 | LL | 239135 | 02TANGY | 69 | 202 | 1.0493 | 1.054 | 1.05/0.90 | Single | AEP_P1-4_05OHIOCT 345.00 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Not Valid
ATSI-LLVM38 | LL | 239135 | 02TANGY | 69 | 202 | 1.0493 | 1.0542 | 1.05/0.90 | Single | AEP_P1-2_#706 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
ATSI-LLVM101 | LL | 238582 | 02BRDVIE | 69 | 202 | 1.0462 | 1.0511 | 1.05/0.90 | Single | DAY_P1_URBANA_138_URBANA_69_BK_7 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM102 | LL | 238582 | 02BRDVIE | 69 | 202 | 1.0462 | 1.0508 | 1.05/0.90 | Single | DAY_P1_6936_EDGEWOOD_URBANA_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM103 | LL | 240700 | 02TECH + | 69 | 202 | 1.0458 | 1.0505 | 1.05/0.90 | Single | DAY_P1_URBANA_138_URBANA_69_BK_7 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM104 | LL | 240700 | 02TECH + | 69 | 202 | 1.0458 | 1.0503 | 1.05/0.90 | Single | DAY_P1_6936_EDGEWOOD_URBANA_69KV |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM105 | LL | 240699 | 02TECH II | 69 | 202 | 1.0454 | 1.0501 | 1.05/0.90 | Single | DAY_P1_URBANA_138_URBANA_69_BK_7 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM106 | LL | 240669 | 02MOREFIEL | 69 | 202 | 1.0454 | 1.0501 | 1.05/0.90 | Single | DAY_P1_URBANA_138_URBANA_69_BK_7 |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM107 | LL | 239838 | 02INGMAR-2 | 69 | 202 | 1.05 |  | 1.05/0.91 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM108 | LL | 239831 | 02INGMAR-1 | 69 | 202 | 1.05 |  | 1.05/0.92 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM109 | LL | 239826 | 02EVANSCIT | 69 | 202 | 1.0502 |  | 1.05/0.93 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM110 | LL | 239827 | 02CALLCHEM | 69 | 202 | 1.0505 |  | 1.05/0.94 | Single | Base Case |  |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM111 | LL | 239828 | 02ROES.BRN | 69 | 202 | 1.0508 | 1.0538 | 1.05/0.95 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM112 | LL | 239826 | 02EVANSCIT | 69 | 202 | 1.0502 | 1.0535 | 1.05/0.96 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM113 | LL | 239179 | 02ZELI69 | 69 | 202 | 1.049 | 1.0531 | 1.05/0.97 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM114 | LL | 238943 | 02MAPLE | 69 | 202 | 1.0488 | 1.0529 | 1.05/0.98 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM115 | LL | 239131 | 02ZELI_NO | 69 | 202 | 1.0483 | 1.0523 | 1.05/0.99 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020
ATSI-LLVM116 | LL | 239900 | 02FOMBELL | 69 | 202 | 1.0475 | 1.0513 | 1.05/0.100 | Single | AP-P1-2-WP-138-337T | * KRENSDALE - MAPLE (PP) 138KV APS-ATSI TIE |  |  | No | FirstEnergy Transmission Planning Criteria | Reliability Violations on Transmission Facilities Below 200 kV exclusion | New 715 violation added 8/27/2020