## Thermal
2025 RTEP PJM N-1 Thermal Result (Light Load)
No violations identified

## Voltage High
2025 RTEP PJM N-1 Voltage Magnitude Result (Light Load)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper Limit | Cont Type | Contingency | PJM Accepting Proposals | Comment
N1-LLVH1 | 200881 | 26BIGBY | 115 | 226 | 1.0557 | 1.0401 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH2 | 200881 | 26BIGBY | 115 | 226 | 1.0557 | 1.0401 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH3 | 200881 | 26BIGBY | 115 | 226 | 1.0558 | 1.0401 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH4 | 200881 | 26BIGBY | 115 | 226 | 1.0573 | 1.0401 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH5 | 200856 | 26LICK RUN | 115 | 226 | 1.055 | 1.0394 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH6 | 200856 | 26LICK RUN | 115 | 226 | 1.055 | 1.0394 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH7 | 200856 | 26LICK RUN | 115 | 226 | 1.0551 | 1.0394 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH9 | 200856 | 26LICK RUN | 115 | 226 | 1.0566 | 1.0394 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH10 | 200854 | 26BERKLY H | 115 | 226 | 1.0561 | 1.0405 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH11 | 200854 | 26BERKLY H | 115 | 226 | 1.0561 | 1.0405 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH12 | 200854 | 26BERKLY H | 115 | 226 | 1.0562 | 1.0405 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH13 | 200854 | 26BERKLY H | 115 | 226 | 1.0578 | 1.0405 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH14 | 200803 | 26MEY.NORT | 115 | 226 | 1.0561 | 1.0404 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH15 | 200803 | 26MEY.NORT | 115 | 226 | 1.0561 | 1.0404 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH16 | 200803 | 26MEY.NORT | 115 | 226 | 1.0561 | 1.0404 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH17 | 200803 | 26MEY.NORT | 115 | 226 | 1.0577 | 1.0404 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH18 | 200761 | 26ARNOLD R | 115 | 226 | 1.0557 | 1.0401 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH19 | 200761 | 26ARNOLD R | 115 | 226 | 1.0557 | 1.0401 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH20 | 200761 | 26ARNOLD R | 115 | 226 | 1.0558 | 1.0401 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH21 | 200761 | 26ARNOLD R | 115 | 226 | 1.0573 | 1.0401 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH22 | 200746 | 26ROCKWOOD | 115 | 226 | 1.052 | 1.0364 | 1.05 | Single | PN-P1-3-PN-115-025 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH23 | 200746 | 26ROCKWOOD | 115 | 226 | 1.052 | 1.0364 | 1.05 | Bus | PN-P2-2-PN-115-002 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH24 | 200746 | 26ROCKWOOD | 115 | 226 | 1.0521 | 1.0364 | 1.05 | Single | PN-P1-2-PN-115-068 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH25 | 200746 | 26ROCKWOOD | 115 | 226 | 1.0536 | 1.0364 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
N1-LLVH26 | 200744 | 26SOMERST | 115 | 226 | 1.0538 | 1.0322 | 1.05 | Line_FB | PN-P2-3-PN-115-62D | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area
Note on K3: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K4: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K5: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K6: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K7: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K8: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K9: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K10: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K11: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K12: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K13: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K14: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K15: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K16: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K17: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K18: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K19: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K20: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K21: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K22: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K23: CONTINGENCY 'PN-P1-3-PN-115-025' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200745 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 END
Note on K24: CONTINGENCY 'PN-P2-2-PN-115-002' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200743 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 202637 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 END
Note on K25: CONTINGENCY 'PN-P1-2-PN-115-068' DISCONNECT BRANCH FROM BUS 200744 TO BUS 200746 CKT 1 DISCONNECT BRANCH FROM BUS 200746 TO BUS 200773 CKT 1 END
Note on K26: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END
Note on K27: CONTINGENCY 'PN-P2-3-PN-115-62D' DISCONNECT BRANCH FROM BUS 200743 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 202637 TO BUS 200744 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200774 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200802 CKT 1 DISCONNECT BRANCH FROM BUS 200744 TO BUS 200788 CKT 2 END