## Summary
2025 RTEP PJM Generation Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Comment
GD-LL33 | 272365 | ESS H440 ;RT | 272363 | ESS H440 ; R | 1 | 138/138 | 222/222 | 196.7 | 207.17 | 203.53 | 105.32 | 103.47 | 'COMED_P2-1_186-L16914__' | single | 196.7/196.7 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area. Cancellation of S1533 on 7/17/2020 remove this violation
Note on N4: CONTINGENCY 'COMED_P2-1_186-L16914__' / CONTINGENCY # 256 TRIP BRANCH FROM BUS 272365 TO BUS 272516 CKT 1 / ESS H440 ;RT 138 STEWARD ; B 138 END