## N-1 Thermal
PJM N-1 Thermal Result (Summer 2025 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Comments
N1-ST31 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69/69 | 363/320 | 105 | 101.8095 | 103.34 | Line_FB | 'EKPC_P2-3_COOP S42-1014' | N/A | No | Tie Line to Non PJM facility. EKPC summer emergency rating is 152 MVA. LGEE summer emergency rating is 105 MVA.
N1-ST32 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 984.18 | 104.4321 | 102.617 | Single | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N1-ST33 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 984.18 | 104.2391 | 102.4362 | Single | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N1-ST41 | 246067 | 05NATRIUM34 | 243049 | 05NATRIUM12 | Z1 | 138/138 | 205/205 | 240 | 97.3333 | 101.13 | Line_FB | 'AEP_P4_#8897_05NATRIUM12 138_H' | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
N1-ST42 | 246067 | 05NATRIUM34 | 243049 | 05NATRIUM12 | Z1 | 138/138 | 205/205 | 240 | 97.3333 | 101.13 | Bus | 'AEP_P2-2_#8897_05NATRIUM12 138_2' | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
Note on I5: New Rating is used. Original rating is 1047.0
Note on I6: New Rating is used. Original rating is 1047.0

## N-1 Volt Low
PJM N-1 Voltage Magnitude Result (Summer 2025 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Low Limit | Cont Type | Contingency | PJM Accepting Proposals | Comment
N1-SVM1 | 934930 | AD1-125 POI | 138 | 201 | 0.8776 | 0.9795 | 0.92 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM2 | 934930 | AD1-125 POI | 138 | 201 | 0.8776 | 0.9795 | 0.92 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM3 | 235537 | 01BAKER | 138 | 201 | 0.8776 | 0.9795 | 0.92 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM4 | 235537 | 01BAKER | 138 | 201 | 0.8776 | 0.9795 | 0.92 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM5 | 235495 | 01NPETER | 138 | 201 | 0.8819 | 0.9818 | 0.92 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM6 | 235495 | 01NPETER | 138 | 201 | 0.8819 | 0.9818 | 0.92 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM7 | 235476 | 01HARDY | 138 | 201 | 0.88 | 0.9813 | 0.92 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM8 | 235476 | 01HARDY | 138 | 201 | 0.88 | 0.9813 | 0.92 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM9 | 228146 | PEERMONT | 69 | 234 | 0.9258 | 1.0037 | 0.94 | Single | AE_P1-2 CORS-SWAIN | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVM10 | 228129 | SWAINTON | 69 | 234 | 0.9157 | 1.0081 | 0.94 | Single | AE_P1-2 CORS-SWAIN | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Summer 2025)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Comment
N1-SVD1 | 934930 | AD1-125 POI | 138 | 201 | 0.8508 | 0.9795 | 12.87 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD2 | 934930 | AD1-125 POI | 138 | 201 | 0.8508 | 0.9795 | 12.87 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD3 | 235539 | 01NFRANK | 138 | 201 | 0.8822 | 0.9903 | 10.81 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD4 | 235539 | 01NFRANK | 138 | 201 | 0.8822 | 0.9903 | 10.81 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD5 | 235537 | 01BAKER | 138 | 201 | 0.8508 | 0.9795 | 12.87 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD6 | 235537 | 01BAKER | 138 | 201 | 0.8508 | 0.9795 | 12.87 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD7 | 235495 | 01NPETER | 138 | 201 | 0.8573 | 0.9818 | 12.45 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD8 | 235495 | 01NPETER | 138 | 201 | 0.8573 | 0.9818 | 12.45 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD9 | 235476 | 01HARDY | 138 | 201 | 0.8539 | 0.9813 | 12.74 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD10 | 235476 | 01HARDY | 138 | 201 | 0.8539 | 0.9813 | 12.74 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD11 | 235400 | 01SENECA | 138 | 201 | 0.8912 | 0.9934 | 10.22 | Line_FB | AP-P2-3-PE-138-002 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD12 | 235400 | 01SENECA | 138 | 201 | 0.8912 | 0.9934 | 10.22 | Bus | AP-P2-2-PE-138-013 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD13 | 232208 | STEVNSVL | 69 | 235 | 0.8884 | 0.9749 | 8.65 | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-SVD14 | 232207 | GRASONVL | 69 | 235 | 0.8758 | 0.9767 | 10.09 | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-SVD15 | 228146 | PEERMONT | 69 | 234 | 0.9204 | 1.0037 | 8.33 | Single | AE_P1-2 CORS-SWAIN | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-SVD16 | 228129 | SWAINTON | 69 | 234 | 0.9103 | 1.008 | 9.77 | Single | AE_P1-2 CORS-SWAIN | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## N-1 Load Drop
N-1 Analysis Load Drop Summary (Summer 2025 Case)
FG# | Contingency Name | Cont. Type | Cont. Areas | MW Drop | PJM Accepting Proposals | Comment
N1-SLD1 | DVP_P7-1: LN 2064-2073 | Tower | 345 | 305.6 | Yes | Generation available on Oregon Inlet to serve its loads and can operate under islanded conditions if there’s a disconnection from the transmission source. Load loss drops below 300 MW
Note on B4: CONTINGENCY 'DVP_P7-1: LN 2064-2073' OPEN BRANCH FROM BUS 314640 TO BUS 314641 CKT 2 OPEN BRANCH FROM BUS 314640 TO BUS 314647 CKT 1 OPEN BRANCH FROM BUS 313801 TO BUS 314632 CKT Z1 OPEN BRANCH FROM BUS 313801 TO BUS 314633 CKT 1 OPEN BRANCH FROM BUS 313801 TO BUS 314647 CKT 2 OPEN BRANCH FROM BUS 314633 TO BUS 314640 CKT 1 OPEN BRANCH FROM BUS 314640 TO BUS 314641 CKT 1 OPEN BUS 313801 OPEN BUS 314633 END