## Summary
2025 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Comment
GD-S1 | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 934.9 | 1390.3 | 1389.1 | 148.7 | 148.58 | DVP_P1-2: LN 557 | Single | Transformer rating is the same as basecase model | No | Not a violation, Loading should be <100% without AC1-107 (1600 MW) suspended queue generator
GD-S479 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 223 | 219.8 | 136 | 134.01 | DVP_P7-1: LN 2058-2181 | Tower | N/A | No | Tie Line to Non PJM facility. Dominion summer emergency rating is 218 MVA and load dump rating is 228 MVA. DEP summer emergency rating is 164 MVA.
GD-S2 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1025 | 1215.6 | 1211 | 118.6 | 118.15 | Base Case | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
GD-S480 | 221855 | CONSTITUTION | 221214 | CONCRD64 | 1 | 115 | 232 | 169 | 191.8 | 191 | 113.49 | 113.04 | BG_P7_BS_RIV_44&45 | Tower | Conductor Rating is the same as basecase model | Yes | No exclusion (multiple facility overloads in the same vicinity)
GD-S3 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1451.3 | 1449.9 | 110.12 | 110.01 | AEP_P1-2_#37_12 | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
GD-S4 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1449.6 | 1448.3 | 109.99 | 109.89 | AEP_P2-1_242516 05MOUNTN 765 242920 05BELMON 765 1 | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
GD-S481 | 270855 | POWERTON ; R | 349662 | 7TAZEWELL | 1 | 345 | 222/357 | 1489 | 1691 | 1630.8 | 113.57 | 109.52 | COMED_P7-1_345-L9806__R-S_+_345-L19601_B-S | Tower | N/A | No | Tie Line to Non PJM facility. ComEd applicable rating is 1837.7 MVA. Ameren summer emergency rating is 1507 MVA.
GD-S482 | 221125 | WESTPORT | 221155 | CENTER | 1 | 115 | 232 | 278 | 298.3 | 303.3 | 107.32 | 109.09 | BG_P7_BS_RIV_44&45 | Tower | SN/SE = 296/329 | No | Substation Equipment exclusion
GD-S5 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1435.4 | 1434.9 | 108.91 | 108.87 | AEP_P1-2_#6140_12 | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
GD-S483 | 221855 | CONSTITUTION | 221215 | CONCRD62 | 1 | 115 | 232 | 183 | 198.9 | 198.2 | 108.7 | 108.33 | BG_P7_BS_RIV_44&45 | Tower | Conductor Rating is the same as basecase model | Yes | No exclusion (multiple facility overloads in the same vicinity)
GD-S6 | 200043 | STEELCTY | 208101 | STCI | 1 | 500/230 | 229 | 879 | 936.5 | 940 | 106.54 | 106.94 | PL:20:P12:000096 | Single | SN/SE = 884/1200 | No | Substation Equipment exclusion
GD-S290 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363/320 | 105 | 109.1 | 110.7 | 103.94 | 105.48 | EKPC_P2-3_COOP S42-1014 | Breaker | N/A | No | Tie Line to Non PJM facility. EKPC summer emergency rating is 152 MVA. LGEE summer emergency rating is 105 MVA.
GD-S8 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1390.8 | 1386.8 | 105.52 | 105.22 | AEP_P1-2_#8401 | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
GD-S293 | 243039 | 05MELMOR | 242984 | 05CHATFL | 1 | 138 | 205 | 167 | 176.8 | 174.2 | 105.88 | 104.34 | AEP_P4_#7110_05MELMOR 138_B | Breaker | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-S11 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230 | 345 | 984.2 | 1044.2 | 1026.3 | 106.1 | 104.28 | DVP_P1-2: LN 2172 | Single | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
GD-S12 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230 | 345 | 984.2 | 1042.2 | 1024.5 | 105.9 | 104.09 | DVP_P1-2: LN 2210 | Single | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
GD-S298 | 246067 | 05NATRIUM34 | 243049 | 05NATRIUM12 | Z1 | 138 | 205 | 240 | 237.9 | 247 | 99.14 | 102.92 | AEP_P4_#8897_05NATRIUM12 138_H | Breaker | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-S446 | 246067 | 05NATRIUM34 | 243049 | 05NATRIUM12 | Z1 | 138 | 205 | 240 | 237.9 | 247 | 99.14 | 102.92 | AEP_P2-2_#8897_05NATRIUM12 138_2 | Bus | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-S13 | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 934.9 | 972.7 | 961.3 | 104.05 | 102.82 | DVP_P1-2: LN 567 | Single | Transformer rating is the same as basecase model | No | Not a violation, Loading should be <100% without AC1-107 (1600 MW) suspended queue generator
GD-S301 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | Z1 | 345 | 205/206 | 1868 | 1931.3 | 1914.9 | 103.39 | 102.51 | AEP_P4_#1760_05JEFRSO 765_A | Breaker | SN/SE = 2354/2354 | No | Substation Equipment exclusion
GD-S315 | 246067 | 05NATRIUM34 | 243049 | 05NATRIUM12 | Z1 | 138 | 205 | 240 | 233.5 | 241.9 | 97.27 | 100.8 | AEP_P4_#10033_05NATRIUM12 138_S | Breaker | N/A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-S14 | 242947 | 05WATERFORD | 242940 | 05MUSKNG | 1 | 345 | 205 | 1318 | 1326.4 | 1323.6 | 100.64 | 100.42 | AEP_P1-2_#707_8315 | Single | SN/SE = 2684/2684 | No | Substation Equipment exclusion
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
The final AC loading is due to contribution from Suspended, Deactivated, or Withdrawn generators and the loading on the circuit should be <100% without those generators.