## Summer N-1-1 Thermal Results
PJM N-1-1 Thermal Result (2025 Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | Initial AC (%) | SCD AC (%) | Contingency 1 | Contingency 2 | Conductor Rating (MVA) | PJM Accepting Proposals | Comments
N2-ST1 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 103.31 | 101.48 | 'DVP_P1-2: LN 9173' | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST2 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 103.17 | 101.34 | 'DVP_P1-2: LN 9173' | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST3 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 113.28 | 113.33 | 'DVP_P1-2: LN 274' | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST4 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 113.09 | 113.14 | 'DVP_P1-2: LN 274' | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST5 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 113.10 | 109.53 | 'DVP_P1-2: LN 2210' | 'DVP_P1-2: LN 274' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST6 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 109.27 | 104.44 | 'DVP_P1-2: LN 2210' | 'DVP_P1-2: LN 227' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST7 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 104.17 | 100.01 | 'DVP_P1-2: LN 2210' | 'DVP_P1-2: LN 2152' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST8 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 104.31 | 102.87 | 'DVP_P1-2: LN 2152' | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST9 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 104.17 | 102.73 | 'DVP_P1-2: LN 2152' | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST10 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 109.45 | 105.93 | 'DVP_P1-2: LN 227' | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST11 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1047.0 | 109.27 | 105.76 | 'DVP_P1-2: LN 227' | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST12 | 313863 | 6YARDLEY | 313730 | 6CABIN_RUN | 1 | 230/230 | 345/345 | 1047.0 | 101.86 | 101.65 | 'DVP_P1-2: LN 227' | 'DVP_P1-2: LN 274' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST13 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 113.28 | 109.6 | 'DVP_P1-2: LN 2172' | 'DVP_P1-2: LN 274' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST14 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 109.45 | 104.47 | 'DVP_P1-2: LN 2172' | 'DVP_P1-2: LN 227' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST15 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1047.0 | 104.31 | 100.02 | 'DVP_P1-2: LN 2172' | 'DVP_P1-2: LN 2152' | Conductor Rating is the same as basecase model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-ST16 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 285 | 113.61 | 113.61 | 'AEP_P1-3_#57_05E LIMA 345_1' | 'BASE CASE' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST17 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 107.42 | 107.42 | 'AEP_P1-3_#57_05E LIMA 345_1' | 'AEP_P1-2_#726_582' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST18 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 102.33 | 102.33 | 'AEP_P1-3_#57_05E LIMA 345_1' | 'AEP_P1-2_#5186_752' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST19 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 102.33 | 102.33 | 'AEP_P1-3_#57_05E LIMA 345_1' | 'AEP_P1-2_#5186' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST20 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 101.69 | 101.69 | 'AEP_P1-3_#57_05E LIMA 345_1' | 'AEP_P1-3_#744_05FOSTOR 345_1' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST21 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 102.33 | 102.33 | 'AEP_P1-2_#5186_752' | 'AEP_P1-3_#57_05E LIMA 345_1' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST22 | 242935 | 05E LIMA | 242989 | 05E LIMA | 2 | 345/138 | 205/205 | 368 | 102.33 | 102.33 | 'AEP_P1-2_#5186_752' | 'AEP_P1-3_#57_05E LIMA 345' | SN/SE = 501/564 | No | Substation Equipment exclusion
N2-ST23 | 228406 | GLASBORO | 228479 | ROWAN | 1 | 69/69 | 234/234 | 77 | 111.17 | 109.42 | 'AE_P1-2 MON-WASH' | 'AE_P1-2 MANTUA-MICK' | Conductor Rating is the same as basecase model | Yes | Removed due to model correction
N2-ST24 | 228479 | ROWAN | 228411 | PITMAN#1 | 1 | 69/69 | 234/234 | 77 | 104.95 | 103.25 | 'AE_P1-2 MON-WASH' | 'AE_P1-2 MANTUA-MICK' | Conductor Rating is the same as basecase model | Yes | Removed due to model correction
N2-ST25 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.92 | 123.15 | 'AE_P1-3 MID 3 XFR' | 'AE_P1-2 ENG-CORSON' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST26 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.91 | 123.12 | 'AE_P1-3 MID 3 XFR' | 'AE_P1-2 MID TP-MID' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST27 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.09 | 123.09 | 'AE_P1-3 MID 3 XFR' | 'AE_P1-3 MID 4 XFR' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST28 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.92 | 123.18 | 'AE_P1-2 CORSON-MID' | 'AE_P1-2 ENG-CORSON' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST29 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.92 | 123.15 | 'AE_P1-2 CORSON-MID' | 'AE_P1-2 MID TP-MID' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST30 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.1 | 123.12 | 'AE_P1-2 CORSON-MID' | 'AE_P1-3 MID 4 XFR' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST31 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.76 | 123.15 | 'AE_P1-2 MID TP-MID' | 'AE_P1-2 CORSON-MID' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST32 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 119.95 | 123.12 | 'AE_P1-2 MID TP-MID' | 'AE_P1-3 MID 3 XFR' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST33 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.77 | 123.18 | 'AE_P1-2 ENG-CORSON' | 'AE_P1-2 CORSON-MID' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST34 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 119.96 | 123.15 | 'AE_P1-2 ENG-CORSON' | 'AE_P1-3 MID 3 XFR' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST35 | 228406 | GLASBORO | 228479 | ROWAN | 1 | 69/69 | 234/234 | 77 | 111.6 | 109.41 | 'AE_P1-2 MANTUA-MICK' | 'AE_P1-2 MON-WASH' | Conductor Rating is the same as basecase model | Yes | Removed due to model correction
N2-ST36 | 228479 | ROWAN | 228411 | PITMAN#1 | 1 | 69/69 | 234/234 | 77 | 105.38 | 103.25 | 'AE_P1-2 MANTUA-MICK' | 'AE_P1-2 MON-WASH' | Conductor Rating is the same as basecase model | Yes | Removed due to model correction
N2-ST37 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 120.76 | 123.12 | 'AE_P1-3 MID 4 XFR' | 'AE_P1-2 CORSON-MID' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-ST38 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 119.95 | 123.09 | 'AE_P1-3 MID 4 XFR' | 'AE_P1-3 MID 3 XFR' | Conductor Rating is the same as basecase model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Note:
70% load diversified case (2020RTEP 2025SUM-70%_nonFSA_05062020.raw) was used to evaluate the result
Note on L18: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on L19: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on M19: CONTINGENCY 'AEP_P1-2_#726_582' OPEN BRANCH FROM BUS 242935 TO BUS 242945 CKT 1 END
Note on L20: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on M20: CONTINGENCY 'AEP_P1-2_#5186_752' OPEN BRANCH FROM BUS 243122 TO BUS 243136 CKT 1 END
Note on L21: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on L22: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on M22: CONTINGENCY 'AEP_P1-3_#744_05FOSTOR 345_1' OPEN BRANCH FROM BUS 242936 TO BUS 243006 CKT 1 END
Note on L23: CONTINGENCY 'AEP_P1-2_#5186_752' OPEN BRANCH FROM BUS 243122 TO BUS 243136 CKT 1 END
Note on M23: CONTINGENCY 'AEP_P1-3_#57_05E LIMA 345_1' OPEN BRANCH FROM BUS 242935 TO BUS 242989 CKT 1 END
Note on L24: CONTINGENCY 'AEP_P1-2_#5186_752' OPEN BRANCH FROM BUS 243122 TO BUS 243136 CKT 1 END
Note on L25: CONTINGENCY 'AE_P1-2 MON-WASH' OPEN LINE FROM BUS 228465 TO BUS 228474 CIRCUIT 1 END
Note on M25: CONTINGENCY 'AE_P1-2 MANTUA-MICK' OPEN LINE FROM BUS 228418 TO BUS 228470 CIRCUIT 1 END
Note on L26: CONTINGENCY 'AE_P1-2 MON-WASH' OPEN LINE FROM BUS 228465 TO BUS 228474 CIRCUIT 1 END
Note on M26: CONTINGENCY 'AE_P1-2 MANTUA-MICK' OPEN LINE FROM BUS 228418 TO BUS 228470 CIRCUIT 1 END
Note on L27: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END
Note on M27: CONTINGENCY 'AE_P1-2 ENG-CORSON' DISCONNECT BUS 228111 END
Note on L28: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END
Note on M28: CONTINGENCY 'AE_P1-2 MID TP-MID' OPEN LINE FROM BUS 228111 TO BUS 228112 CIRCUIT 1 END
Note on L29: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END
Note on M29: CONTINGENCY 'AE_P1-3 MID 4 XFR' OPEN LINE FROM BUS 228112 TO BUS 228186 CIRCUIT 1 END
Note on L30: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on M30: CONTINGENCY 'AE_P1-2 ENG-CORSON' DISCONNECT BUS 228111 END
Note on L31: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on M31: CONTINGENCY 'AE_P1-2 MID TP-MID' OPEN LINE FROM BUS 228111 TO BUS 228112 CIRCUIT 1 END
Note on L32: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on M32: CONTINGENCY 'AE_P1-3 MID 4 XFR' OPEN LINE FROM BUS 228112 TO BUS 228186 CIRCUIT 1 END
Note on L33: CONTINGENCY 'AE_P1-2 MID TP-MID' OPEN LINE FROM BUS 228111 TO BUS 228112 CIRCUIT 1 END
Note on M33: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on L34: CONTINGENCY 'AE_P1-2 MID TP-MID' OPEN LINE FROM BUS 228111 TO BUS 228112 CIRCUIT 1 END
Note on M34: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END
Note on L35: CONTINGENCY 'AE_P1-2 ENG-CORSON' DISCONNECT BUS 228111 END
Note on M35: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on L36: CONTINGENCY 'AE_P1-2 ENG-CORSON' DISCONNECT BUS 228111 END
Note on M36: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END
Note on L37: CONTINGENCY 'AE_P1-2 MANTUA-MICK' OPEN LINE FROM BUS 228418 TO BUS 228470 CIRCUIT 1 END
Note on M37: CONTINGENCY 'AE_P1-2 MON-WASH' OPEN LINE FROM BUS 228465 TO BUS 228474 CIRCUIT 1 END
Note on L38: CONTINGENCY 'AE_P1-2 MANTUA-MICK' OPEN LINE FROM BUS 228418 TO BUS 228470 CIRCUIT 1 END
Note on M38: CONTINGENCY 'AE_P1-2 MON-WASH' OPEN LINE FROM BUS 228465 TO BUS 228474 CIRCUIT 1 END
Note on L39: CONTINGENCY 'AE_P1-3 MID 4 XFR' OPEN LINE FROM BUS 228112 TO BUS 228186 CIRCUIT 1 END
Note on M39: CONTINGENCY 'AE_P1-2 CORSON-MID' OPEN LINE FROM BUS 228108 TO BUS 228113 CIRCUIT 1 END
Note on L40: CONTINGENCY 'AE_P1-3 MID 4 XFR' OPEN LINE FROM BUS 228112 TO BUS 228186 CIRCUIT 1 END
Note on M40: CONTINGENCY 'AE_P1-3 MID 3 XFR' OPEN LINE FROM BUS 228113 TO BUS 228122 CIRCUIT 1 END

## Load Drop
N-1-1 Analysis Load Drop Summary (Summer 2025 Case)
FG# | First Cont Name | Second Cont Name | TotalLoadLoss | PJM Accepting Proposals | Comment
N2-SLD1 | AEP_P1-2_#14022 | AEP_P1-2_#9701_27897 | 304.39 | No | Violation identified due to including the customer load associated with S2139 but not including the required reinforcement associated with S2139. If the load for S2139 was not included in the 2025 RTEP then there would be no valid violation
N2-SLD5 | DVP_P1-2: LN 2195 | DVP_P1-2: LN 2196 | 325.55 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0005
N2-SLD6 | DVP_P1-2: LN 2195 | DVP_P1-2: LN 2148 | 300.45 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0006
N2-SLD7 | DVP_P1-2: LN 2195 | DVP_P1-2: LN 2187 | 418.65 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0007
N2-SLD8 | DVP_P1-2: LN 2149 | DVP_P1-2: LN 9167 | 361.77 | Yes | Waxpool area. Supplemental projects in the area: DOM-2020-0012, DOM-2020-0021, DOM-2020-0022, DOM-2020-0024
N2-SLD9 | DVP_P1-2: LN 2073 | DVP_P1-2: LN 2064 | 305.61 | Yes | Generation available on Oregon Inlet to serve its loads and can operate under islanded conditions if there’s a disconnection from the transmission source. Load loss drops below 300 MW
N2-SLD10 | DVP_P1-2: LN 2011 | DVP_P1-2: LN 2187 | 492.19 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Includes impact of reverse power relaying at Lomar & Micron. Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0007