## Summer N-1-1 Voltage Mag
PJM N-1-1 Voltage Magnitude Results (2025 Summer)
FG# | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Comment
N2-SVM1 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9525 | 0.904 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM2 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9525 | 0.9091 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM3 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-042 | 0.9525 | 0.9119 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM4 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9556 | 0.9133 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM5 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9556 | 0.9176 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM6 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.953 | 0.9067 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM7 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-042 | 0.953 | 0.9124 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM8 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9542 | 0.8929 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM9 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9542 | 0.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM10 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-042 | 0.9542 | 0.9018 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM11 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-019 | AP-P1-2-PE-138-041 | 0.9645 | 0.9127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM12 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9543 | 0.9091 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM13 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9581 | 0.9177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM14 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9538 | 0.9 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM15 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-041 | 0.9538 | 0.9149 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM16 | 235467 | 01FRNCHM | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-2-PE-138-046 | 0.9483 | 0.8847 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM17 | 235467 | 01FRNCHM | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-157 | 0.9483 | 0.9189 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM18 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-2-PE-138-046 | 0.9508 | 0.903 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM19 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-4-PE-138-046 | 0.9508 | 0.9159 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM20 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-157 | 0.9508 | 0.9167 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM21 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-2-PE-138-046 | 0.9471 | 0.8962 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM22 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-157 | 0.9471 | 0.912 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM23 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-156 | 0.9471 | 0.9129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM24 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-059 | 0.9471 | 0.9129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM25 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-060 | 0.9471 | 0.9131 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM26 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-2-PE-138-046 | 0.9519 | 0.9063 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM27 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | FE-P1-2-MP-138-157 | 0.9519 | 0.9181 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM28 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-4-PE-138-046 | 0.9519 | 0.9197 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM29 | 235501 | 01PARRN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-024 | AP-P1-2-PE-138-046 | 0.9482 | 0.9129 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM30 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.9561 | 0.9039 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM31 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.96 | 0.9132 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM32 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.9552 | 0.9066 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM33 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.955 | 0.8928 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM34 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-019 | 0.955 | 0.9127 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM35 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-020 | 0.955 | 0.9149 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM36 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-042 | AP-P1-2-PE-138-018 | 0.9596 | 0.9169 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM37 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-042 | AP-P1-2-PE-138-018 | 0.9585 | 0.9196 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM38 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-042 | AP-P1-2-PE-138-018 | 0.9594 | 0.9085 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM39 | 235467 | 01FRNCHM | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.9689 | 0.8861 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM40 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.98 | 0.9045 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM41 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.9782 | 0.8976 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM42 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.9808 | 0.9077 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM43 | 235501 | 01PARRN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.975 | 0.9144 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM44 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | AP-P1-4-PE-138-046 | AP-P1-2-PE-138-024 | 0.9551 | 0.9162 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM45 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | AP-P1-4-PE-138-046 | AP-P1-2-PE-138-024 | 0.9577 | 0.9199 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM46 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-060 | AP-P1-2-PE-138-024 | 0.9747 | 0.9158 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM47 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-156 | AP-P1-2-PE-138-024 | 0.9709 | 0.9186 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM48 | 235467 | 01FRNCHM | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-157 | AP-P1-2-PE-138-024 | 0.9674 | 0.9188 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM49 | 235476 | 01HARDY | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-157 | AP-P1-2-PE-138-024 | 0.9748 | 0.9165 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM50 | 235479 | 01JUNCTN | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-157 | AP-P1-2-PE-138-024 | 0.972 | 0.9119 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM51 | 235495 | 01NPETER | 138 | 201 | 0.92 | 1.05 | FE-P1-2-MP-138-157 | AP-P1-2-PE-138-024 | 0.9757 | 0.918 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM52 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1_4-PN-345-017-DRT | PN-P1-2-PN-345-103T | 1.0282 | 1.051 | Yes | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM53 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-2-PN-345-103T | PN-P1-4-PN-345-002 | 1.0125 | 1.051 | Yes | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM54 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-2-PN-345-103T | PN-P1_4-PN-345-017-DRT | 1.0125 | 1.051 | Yes | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVM55 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-4-PN-345-002 | PN-P1-2-PN-345-103T | 1.0282 | 1.051 | Yes | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Summer N-1-1 Voltage Drop
PJM N-1-1 Voltage Drop Results (2025 Summer)
FG# | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Comment
N2-SVD1 | 235512 | 01STONEW | 138 | 201 | 10 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.955 | 0.8547 | 10.021 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVD2 | 235467 | 01FRNCHM | 138 | 201 | 10 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.9689 | 0.8612 | 10.767 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-SVD3 | 235479 | 01JUNCTN | 138 | 201 | 10 | AP-P1-2-PE-138-046 | AP-P1-2-PE-138-024 | 0.9782 | 0.8737 | 10.445 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion