## Winter N-1-1 Voltage Mag
PJM N-1-1 Voltage Magnitude Results (2025 Winter)
FG# | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Comment
N2-WVM1 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9556 | 0.9066 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM2 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9556 | 0.9114 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM3 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9584 | 0.9157 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM4 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9584 | 0.9193 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM5 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9577 | 0.9088 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM6 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9595 | 0.8982 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM7 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9595 | 0.9063 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM8 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-042 | 0.9595 | 0.9147 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM9 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9568 | 0.9095 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM10 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.961 | 0.9177 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM11 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.956 | 0.9037 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM12 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.962 | 0.9151 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM13 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.9603 | 0.9094 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM14 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-042 | AP-P1-2-PE-138-018 | 0.9645 | 0.9147 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVM15 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1_4-PN-345-017-DRT | PN-P1-2-PN-345-103T | 1.0412 | 1.0507 | Yes
N2-WVM16 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-2-PN-345-103T | PN-P1-2-PN-230-028 | 1.0122 | 1.0504 | Yes
N2-WVM17 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-2-PN-345-103T | PN-P1-4-PN-345-002 | 1.0122 | 1.0507 | Yes
N2-WVM18 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-2-PN-345-103T | PN-P1_4-PN-345-017-DRT | 1.0122 | 1.0507 | Yes
N2-WVM19 | 200942 | 26PIERCEBRK | 345 | 226 | 0.92 | 1.05 | PN-P1-4-PN-345-002 | PN-P1-2-PN-345-103T | 1.0412 | 1.0507 | Yes
N2-WVM20 | 234605 | ALLENDAL | 138 | 237 | 0.95 | 1.05 | 234604 SMAH138 146769 RAMP138 1 138/138 | PS_P1-2_J-3410 | 0.9739 | 0.9169 | TBD | Removed due to model correction
N2-WVM21 | 234601 | DRLNGTON | 138 | 237 | 0.95 | 1.05 | 234604 SMAH138 146769 RAMP138 1 138/138 | PS_P1-2_J-3410 | 0.974 | 0.9171 | TBD | Removed due to model correction
N2-WVM22 | 234613 | MCARTHR BLVD | 138 | 237 | 0.95 | 1.05 | 234604 SMAH138 146769 RAMP138 1 138/138 | PS_P1-2_J-3410 | 0.974 | 0.9171 | TBD | Removed due to model correction
N2-WVM23 | 234604 | SMAH138 | 138 | 237 | 0.95 | 1.05 | 234604 SMAH138 146769 RAMP138 1 138/138 | PS_P1-2_J-3410 | 0.9741 | 0.9172 | TBD | Removed due to model correction
N2-WVM24 | 234605 | ALLENDAL | 138 | 237 | 0.95 | 1.05 | PS_P1-2_J-3410 | 234604 SMAH138 146769 RAMP138 1 138/138 | 1.0307 | 0.9169 | TBD | Removed due to model correction
N2-WVM25 | 234601 | DRLNGTON | 138 | 237 | 0.95 | 1.05 | PS_P1-2_J-3410 | 234604 SMAH138 146769 RAMP138 1 138/138 | 1.0308 | 0.917 | TBD | Removed due to model correction
N2-WVM26 | 234613 | MCARTHR BLVD | 138 | 237 | 0.95 | 1.05 | PS_P1-2_J-3410 | 234604 SMAH138 146769 RAMP138 1 138/138 | 1.0309 | 0.9171 | TBD | Removed due to model correction
N2-WVM27 | 234604 | SMAH138 | 138 | 237 | 0.95 | 1.05 | PS_P1-2_J-3410 | 234604 SMAH138 146769 RAMP138 1 138/138 | 1.031 | 0.9172 | TBD | Removed due to model correction
N2-WVM28 | 314173 | 3GARNER | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9958 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM29 | 314400 | 3LANCA_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9909 | 0.8922 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM30 | 314178 | 3LANCAST | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9909 | 0.8922 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM31 | 314181 | 3NORNECK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0014 | 0.8292 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM32 | 313810 | 6DAHLGREN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0007 | 0.7521 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM33 | 314182 | 6NORNECK | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0001 | 0.7525 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM34 | 314139 | 6OAKGROV | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0021 | 0.7542 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM35 | 314183 | 6SANDERS | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9999 | 0.752 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM36 | 314190 | 6WESTMOR | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0006 | 0.7525 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM37 | 926472 | AC1-118 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0006 | 0.7526 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM38 | 316077 | AC2-138 C | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0015 | 0.8293 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM39 | 316078 | AC2-138 E | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0015 | 0.8293 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM40 | 316148 | AD1-046 C | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0024 | 0.7546 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM41 | 316149 | AD1-046 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0026 | 0.7548 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM42 | 938961 | AE1-124 C | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0022 | 0.7544 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM43 | 938962 | AE1-124 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0023 | 0.7544 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM44 | 939241 | AE1-155 MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9959 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM45 | 939240 | AE1-155 TAP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9959 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM46 | 314173 | 3GARNER | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM47 | 314400 | 3LANCA_1 | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9933 | 0.8922 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM48 | 314178 | 3LANCAST | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9933 | 0.8922 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM49 | 314181 | 3NORNECK | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0039 | 0.8292 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM50 | 313810 | 6DAHLGREN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9999 | 0.7521 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM51 | 314182 | 6NORNECK | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0033 | 0.7525 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM52 | 314139 | 6OAKGROV | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0031 | 0.7542 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM53 | 314183 | 6SANDERS | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.752 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM54 | 314190 | 6WESTMOR | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.7525 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM55 | 926472 | AC1-118 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.7526 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM56 | 316077 | AC2-138 C | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0039 | 0.8293 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM57 | 316078 | AC2-138 E | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.004 | 0.8293 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM58 | 316148 | AD1-046 C | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0034 | 0.7546 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM59 | 316149 | AD1-046 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0036 | 0.7548 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM60 | 938961 | AE1-124 C | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0032 | 0.7544 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM61 | 938962 | AE1-124 E | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0033 | 0.7544 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM62 | 939241 | AE1-155 MAIN | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVM63 | 939240 | AE1-155 TAP | 115 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.8332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"

## Winter N-1-1 Voltage Drop
PJM N-1-1 Voltage Drop Results (2025 Winter)
FG# | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Comment
N2-WVD1 | 314173 | 3GARNER | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9958 | 0.754 | 24.183 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD2 | 313886 | 3GREYSPT | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9952 | 0.8569 | 13.827 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD3 | 314385 | 3HARMO_1 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.004 | 0.8998 | 10.414 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD4 | 314395 | 3HARMO_2 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.004 | 0.8998 | 10.414 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD5 | 314174 | 3HARMONY | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.004 | 0.8998 | 10.414 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD6 | 314400 | 3LANCA_1 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9909 | 0.8208 | 17.015 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD7 | 314178 | 3LANCAST | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9909 | 0.8208 | 17.015 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD8 | 314181 | 3NORNECK | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0014 | 0.7498 | 25.161 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD9 | 313813 | 3OCRAN | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9919 | 0.8367 | 15.528 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD10 | 313870 | 3RAPPAHNCK | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9943 | 0.8534 | 14.092 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD11 | 313842 | 3RAPPAHNCK_1 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9938 | 0.853 | 14.084 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD12 | 313843 | 3RAPPAHNCK_2 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9943 | 0.8534 | 14.092 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD13 | 314187 | 3WAN 176 | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9874 | 0.8808 | 10.66 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD14 | 314191 | 3WHIT STONE | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.993 | 0.8455 | 14.754 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD15 | 313810 | 6DAHLGREN | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0007 | 0.7566 | 24.404 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD16 | 314182 | 6NORNECK | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0001 | 0.757 | 24.307 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD17 | 314139 | 6OAKGROV | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0021 | 0.7587 | 24.339 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD18 | 314183 | 6SANDERS | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9999 | 0.7565 | 24.335 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD19 | 314190 | 6WESTMOR | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0006 | 0.7571 | 24.349 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD20 | 926472 | AC1-118 E | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0006 | 0.7571 | 24.348 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD21 | 316077 | AC2-138 C | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0015 | 0.7499 | 25.158 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD22 | 316078 | AC2-138 E | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0015 | 0.75 | 25.157 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD23 | 316148 | AD1-046 C | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0024 | 0.7592 | 24.328 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD24 | 316149 | AD1-046 E | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0026 | 0.7593 | 24.323 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD25 | 316156 | AD2-030 C | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9875 | 0.8809 | 10.659 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD26 | 316157 | AD2-030 E | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9876 | 0.881 | 10.658 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD27 | 938961 | AE1-124 C | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0022 | 0.7589 | 24.334 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD28 | 938962 | AE1-124 E | 230 | 345 | 8 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 1.0023 | 0.7589 | 24.333 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD29 | 939241 | AE1-155 MAIN | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9959 | 0.7539 | 24.195 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD30 | 939240 | AE1-155 TAP | 115 | 345 | 10 | DVP_P1-2: LN 2145 | DVP_P1-2: LN 224 | 0.9959 | 0.7539 | 24.195 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD31 | 314173 | 3GARNER | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.7535 | 24.481 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD32 | 313886 | 3GREYSPT | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9971 | 0.8563 | 14.074 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD33 | 314385 | 3HARMO_1 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0058 | 0.8992 | 10.658 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD34 | 314395 | 3HARMO_2 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0058 | 0.8992 | 10.658 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD35 | 314174 | 3HARMONY | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0058 | 0.8992 | 10.658 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD36 | 314400 | 3LANCA_1 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9933 | 0.8202 | 17.312 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD37 | 314178 | 3LANCAST | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9933 | 0.8202 | 17.312 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD38 | 314181 | 3NORNECK | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0039 | 0.7493 | 25.457 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD39 | 313813 | 3OCRAN | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.994 | 0.8361 | 15.791 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD40 | 313870 | 3RAPPAHNCK | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9962 | 0.8528 | 14.339 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD41 | 313842 | 3RAPPAHNCK_1 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9957 | 0.8524 | 14.332 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD42 | 313843 | 3RAPPAHNCK_2 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9962 | 0.8528 | 14.339 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD43 | 314187 | 3WAN 176 | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9893 | 0.8802 | 10.909 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD44 | 314191 | 3WHIT STONE | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.995 | 0.8449 | 15.003 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD45 | 313810 | 6DAHLGREN | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9999 | 0.7561 | 24.372 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD46 | 314182 | 6NORNECK | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0033 | 0.7565 | 24.681 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD47 | 314139 | 6OAKGROV | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0031 | 0.7582 | 24.49 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD48 | 314183 | 6SANDERS | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.756 | 24.668 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD49 | 314190 | 6WESTMOR | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.7566 | 24.611 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD50 | 926472 | AC1-118 E | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0027 | 0.7566 | 24.609 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD51 | 316077 | AC2-138 C | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0039 | 0.7494 | 25.454 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD52 | 316078 | AC2-138 E | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.004 | 0.7495 | 25.453 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD53 | 316148 | AD1-046 C | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0034 | 0.7586 | 24.479 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD54 | 316149 | AD1-046 E | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0036 | 0.7588 | 24.475 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD55 | 316156 | AD2-030 C | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9894 | 0.8803 | 10.907 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD56 | 316157 | AD2-030 E | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9894 | 0.8804 | 10.907 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD57 | 938961 | AE1-124 C | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0032 | 0.7584 | 24.486 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD58 | 938962 | AE1-124 E | 230 | 345 | 8 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 1.0033 | 0.7584 | 24.484 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD59 | 939241 | AE1-155 MAIN | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.7534 | 24.493 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD60 | 939240 | AE1-155 TAP | 115 | 345 | 10 | DVP_P1-2: LN 224 | DVP_P1-2: LN 2145 | 0.9983 | 0.7534 | 24.493 | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WVD61 | 314763 | 3KIDDSTO | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9882 | 0.8682 | 11.999 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD62 | 313708 | 3FORK UNION | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9937 | 0.8677 | 12.602 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD63 | 313872 | 3FORK UNIO_1 | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9944 | 0.8683 | 12.611 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD64 | 314746 | 4BREMO | 138 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9889 | 0.8624 | 12.648 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD65 | 314744 | 3BREMO | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9915 | 0.8649 | 12.653 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD66 | 314868 | 3BREMO_1 | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9921 | 0.8655 | 12.662 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD67 | 314754 | 3CUNNING | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9835 | 0.8557 | 12.786 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD68 | 313874 | 3JAMES RI TP | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.981 | 0.8525 | 12.851 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD69 | 313875 | 3TRICESLK | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9807 | 0.8521 | 12.855 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD70 | 313871 | 3COBBS CREEK | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9701 | 0.8398 | 13.034 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N2-WVD71 | 314762 | 3JAMES R | 115 | 345 | 10 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-3: 6FORK UNION-TX#1 | 0.9602 | 0.8284 | 13.189 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion