## Thermal
2025 RTEP PJM N-1 Thermal Result (Winter)
FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | AC Ld(%) | Cont Type | Contingency | Transformer/Conductor Rating (MVA) | PJM Accepting Proposals | Comments
N1-W-T1 | 232206 | WYE MILL | 232207 | GRASONVL | 1 | 69/69 | 235/235 | 121 | 114.47 | Single | 'DPL_P1_2_CKT 6755' | 121/153 (WN/WE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-W-T2 | 232104 | MT PLSNT | 232106 | MIDLTNTP | 1 | 138/138 | 235/235 | 392 | 110.35 | Tower | 'DPL_P7_1_DBL_1NCB_FSA' | Conductor Rating is the same as base case model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-W-T13 | 221125 | WESTPORT | 221155 | CENTER | 1 | 115/115 | 232/232 | 278 | 102.81 | Tower | 'BG_P7_BS_RIV_44&45' | 334/360 (WN/WE) | No | Substation Equipment exclusion
N1-W-T14 | 242522 | 05AMOS | 242537 | 05AMOS | 7 | 345/138 | 205/205 | 696 | 102.82 | Line_FB | 'AEP_P4_#2827_05AMOS 345_J2' | 758/940 (WN/WE) | No | Substation Equipment exclusion
N1-W-T17 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | Z1 | 345/345 | 205/206 | 2148 | 100.91 | Line_FB | 'AEP_P4_#1760_05JEFRSO 765_A' | 2991/2991 (WN/WE) | No | Substation Equipment exclusion
N1-W-T19 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69/69 | 363/320 | 141 | 100.4 | Line_FB | 'EKPC_P2-3_COOP S42-1014' | N/A | No | limited by non PJM facility, EKPC side ratings WN/WE = 172/178
| Note: |  | The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
Note on L3: CONTINGENCY 'DPL_P1_2_CKT 6755' OPEN LINE FROM BUS 232206 TO BUS 232208 CIRCUIT 1 END
Note on L4: CONTINGENCY 'DPL_P7_1_DBL_1NCB_FSA' OPEN LINE FROM BUS 231003 TO BUS 232000 CKT 1 OPEN LINE FROM BUS 231003 TO BUS 923960 CKT 2 OPEN LINE FROM BUS 232000 TO BUS 923960 CKT 2 DISCONNECT BUS 923961 DISCONNECT BUS 923962 END
Note on L5: CONTINGENCY 'BG_P7_BS_RIV_44&45' DISCONNECT BUS 220989 DISCONNECT BUS 220990 DISCONNECT BUS 220977 DISCONNECT BUS 221230 DISCONNECT BUS 220987 DISCONNECT BUS 220988 END
Note on L6: CONTINGENCY 'AEP_P4_#2827_05AMOS 345_J2' OPEN BRANCH FROM BUS 242522 TO BUS 242525 CKT 1 OPEN BRANCH FROM BUS 242522 TO BUS 242537 CKT 8 END
Note on L7: CONTINGENCY 'AEP_P4_#1760_05JEFRSO 765_A' OPEN BRANCH FROM BUS 243207 TO BUS 243208 CKT 1 OPEN BRANCH FROM BUS 242924 TO BUS 243208 CKT 1 END
Note on L8: CONTINGENCY 'EKPC_P2-3_COOP S42-1014' OPEN BUS 342715 OPEN BUS 342900 OPEN BRANCH FROM BUS 342793 TO BUS 342796 CKT 1 OPEN BRANCH FROM BUS 342796 TO BUS 360448 CKT 1 OPEN BRANCH FROM BUS 342751 TO BUS 342796 CKT 1 OPEN BRANCH FROM BUS 342748 TO BUS 342751 CKT 1 OPEN BRANCH FROM BUS 342745 TO BUS 342751 CKT 1 OPEN BRANCH FROM BUS 342742 TO BUS 342745 CKT 1 OPEN BRANCH FROM BUS 342745 TO BUS 342799 CKT 1 END

## Votlage Low
2025 RTEP PJM N-1 Load Magnitude Result (Winter)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Low Limit | Cont Type | Contingency | PJM Accepting Proposals | Comments
N1-WVL1 | 232208 | STEVNSVL | 69 | 235 | 0.704 | 0.9561 | 0.94 | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL2 | 232208 | STEVNSVL | 69 | 235 | 0.8604 | 0.9561 | 0.94 | Single | DPL_P1_2_CKT 6755 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL3 | 232208 | STEVNSVL | 69 | 235 | 0.901 | 0.9561 | 0.94 | Single | DPL_P1_2_CKT 6767 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL4 | 232208 | STEVNSVL | 69 | 235 | 0.9304 | 0.9561 | 0.94 | Tower | DPL_P7_1_DBL_1NCB_FSA | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL5 | 232208 | STEVNSVL | 69 | 235 | 0.9346 | 0.9561 | 0.94 | Single | DPL_P2_1_CKT 13808-2 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL6 | 232208 | STEVNSVL | 69 | 235 | 0.9348 | 0.9561 | 0.94 | Single | DPL_P2_1_CKT 13761 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL7 | 232207 | GRASONVL | 69 | 235 | 0.6805 | 0.9662 | 0.94 | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVL8 | 232207 | GRASONVL | 69 | 235 | 0.886 | 0.9662 | 0.94 | Single | DPL_P1_2_CKT 6755 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
Note on J3: CONTINGENCY 'DPL_P1_2_CKT 6789' OPEN LINE FROM BUS 232206 TO BUS 232207 CIRCUIT 1 END
Note on J4: CONTINGENCY 'DPL_P1_2_CKT 6755' OPEN LINE FROM BUS 232206 TO BUS 232208 CIRCUIT 1 END
Note on J5: CONTINGENCY 'DPL_P1_2_CKT 6767' OPEN LINE FROM BUS 232207 TO BUS 232208 CIRCUIT 1 END
Note on J6: CONTINGENCY 'DPL_P7_1_DBL_1NCB_FSA' OPEN LINE FROM BUS 231003 TO BUS 232000 CKT 1 OPEN LINE FROM BUS 231003 TO BUS 923960 CKT 2 OPEN LINE FROM BUS 232000 TO BUS 923960 CKT 2 DISCONNECT BUS 923961 DISCONNECT BUS 923962 END
Note on J7: CONTINGENCY 'DPL_P2_1_CKT 13808-2' OPEN LINE FROM BUS 232104 TO BUS 232106 CIRCUIT 1 END
Note on J8: CONTINGENCY 'DPL_P2_1_CKT 13761' OPEN LINE FROM BUS 232102 TO BUS 232103 CIRCUIT 1 END
Note on J9: CONTINGENCY 'DPL_P1_2_CKT 6789' OPEN LINE FROM BUS 232206 TO BUS 232207 CIRCUIT 1 END
Note on J10: CONTINGENCY 'DPL_P1_2_CKT 6755' OPEN LINE FROM BUS 232206 TO BUS 232208 CIRCUIT 1 END

## Voltage Drop
2025 RTEP PJM N-1 Voltage Drop Results (Winter)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Violation | Cont Type | Contingency | PJM Accepting Proposals | PJM Comments
N1-WVD1 | 200936 | 26WILLMS | 115 | 226 | 0.9169 | 1.0184 | 10.15 | LD | Line_FB | PN-P2-3-PN-115-SB-66A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N1-WVD2 | 232208 | STEVNSVL | 69 | 235 | 0.7103 | 0.956 | 24.57 | LD | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVD3 | 232208 | STEVNSVL | 69 | 235 | 0.8666 | 0.956 | 8.94 | LD | Single | DPL_P1_2_CKT 6755 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
N1-WVD4 | 232207 | GRASONVL | 69 | 235 | 0.687 | 0.9661 | 27.91 | LD | Single | DPL_P1_2_CKT 6789 | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
Note on K3: CONTINGENCY 'PN-P2-3-PN-115-SB-66A' DISCONNECT BRANCH FROM BUS 200936 TO BUS 200679 CKT 1 DISCONNECT BRANCH FROM BUS 200679 TO BUS 200683 CKT 1 OPEN BRANCH FROM BUS 203353 TO BUS 200679 CKT 1 DISCONNECT BRANCH FROM BUS 200679 TO BUS 200680 CKT 1 DISCONNECT BRANCH FROM BUS 200679 TO BUS 200683 CKT 2 DISCONNECT BRANCH FROM BUS 130807 TO BUS 200680 CKT 1 DISCONNECT BRANCH FROM BUS 200680 TO BUS 200681 CKT 1 END
Note on K4: CONTINGENCY 'DPL_P1_2_CKT 6789' OPEN LINE FROM BUS 232206 TO BUS 232207 CIRCUIT 1 END
Note on K5: CONTINGENCY 'DPL_P1_2_CKT 6755' OPEN LINE FROM BUS 232206 TO BUS 232208 CIRCUIT 1 END
Note on K6: CONTINGENCY 'DPL_P1_2_CKT 6789' OPEN LINE FROM BUS 232206 TO BUS 232207 CIRCUIT 1 END

## >300MW load loss
2025 RTEP PJM N-1 Load Drop Results (Winter)
FG# | Contingency Name | Cont. Type | Cont. Areas | MW Drop | PJM Accepting Proposals | PJM Comments
N1-WLD-1 | DVP_P7-1: LN 219-2066 | Tower | 345 | 333.1 | Yes | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
N1-WLD-2 | DVP_P4-2: 219T2066 | Line_FB | 345 | 333.1 | Yes | No overlapping baseline upgrades, M-3 needs, or supplemental projects in the area.
Note on B3: CONTINGENCY 'DVP_P7-1: LN 219-2066' OPEN BRANCH FROM BUS 314306 TO BUS 314338 CKT 1 OPEN BRANCH FROM BUS 314306 TO BUS 314352 CKT 1 OPEN BUS 314306 OPEN BRANCH FROM BUS 313740 TO BUS 314343 CKT 1 OPEN BRANCH FROM BUS 313740 TO BUS 314352 CKT 1 OPEN BRANCH FROM BUS 314322 TO BUS 314343 CKT 1 OPEN BUS 313740 OPEN BUS 314343 END
Note on B4: CONTINGENCY 'DVP_P4-2: 219T2066' OPEN BRANCH FROM BUS 314306 TO BUS 314338 CKT 1 OPEN BRANCH FROM BUS 314306 TO BUS 314352 CKT 1 OPEN BUS 314306 OPEN BRANCH FROM BUS 313740 TO BUS 314343 CKT 1 OPEN BRANCH FROM BUS 313740 TO BUS 314352 CKT 1 OPEN BRANCH FROM BUS 314322 TO BUS 314343 CKT 1 OPEN BUS 313740 OPEN BUS 314343 END