## Summary
2025 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Transformer/Conductor Rating (MVA) | PJM Accepting Proposals | Comments
GD-W1 | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 1177.1 | 1455 | 1457.6 | 123.61 | 123.83 | DVP_P1-2: LN 557 | Single | Transformer Rating is the same as basecase model | No | Not a violation, Loading should be <100% without AC1-107 (1600 MW) suspended queue generator
GD-W2 | 232206 | WYE MILL | 232207 | GRASONVL | 1 | 69 | 235 | 121 | 125.1 | 138.1 | 103.43 | 114.12 | DPL_P1_2_CKT 6755 | Single | 121/153 (WN/WE) | No | • Reliability Violations on Transmission Facilities Below 200 kV exclusion • Related M-3 Need (DPL-2019-0002 and DPL-2019-0003)
GD-W307 | 221125 | WESTPORT | 221155 | CENTER | 1 | 115 | 232 | 278 | 314.5 | 316.1 | 113.14 | 113.71 | BG_P7_BS_RIV_44&45 | Tower | 334/360 (WN/WE) | No | Substation Equipment exclusion
GD-W3 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1711.5 | 1760.1 | 109.92 | 113.05 | AEP_P1-2_#695_1681 | Single | WSTE=1658 for PJM side | Yes | No exclusion (tie line, limited by ComEd conductor)
GD-W4 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1711.5 | 1759.1 | 109.92 | 112.98 | COMED_P1-2_765-L11215__-S | Single | WSTE=1658 for PJM side | Yes | No exclusion (tie line, limited by ComEd conductor)
GD-W181 | 242508 | 05AMOS | 242513 | 05CULLOD | 1 | 765 | 205 | 2312 | 2571.3 | 2610.5 | 111.21 | 112.91 | AEP_P4_#3149_05HANG R 765_B | Breaker | 5960/5960 (WN/WE) | No | Substation Equipment exclusion
GD-W308 | 232104 | MT PLSNT | 232106 | MIDLTNTP | 1 | 138 | 235 | 392 | 418.6 | 436.5 | 106.78 | 111.35 | DPL_P7_1_DBL_1NCB_FSA | Tower | Conductor Rating is the same as base case model | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W183 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | Z1 | 345 | 205/206 | 2148 | 2333.1 | 2385.2 | 108.62 | 111.04 | AEP_P4_#6189_05HANG R 765_D1 | Breaker | 2991/2991 (WN/WE) | No | Substation Equipment exclusion
GD-W6 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | Z1 | 345 | 205/206 | 2148 | 2284.9 | 2338.2 | 106.37 | 108.86 | AEP_P1-2_#709_546 | Single | 2991/2991 (WN/WE) | No | Substation Equipment exclusion
GD-W192 | 242522 | 05AMOS | 242537 | 05AMOS | 7 | 345/138 | 205 | 696 | 720.9 | 726.6 | 103.58 | 104.39 | AEP_P4_#2827_05AMOS 345_J2 | Breaker | 758/940 (WN/WE) | No | Substation Equipment exclusion
GD-W11 | 242701 | 05LEESVI | 314667 | 4ALTVSTA | 1 | 138 | 205/345 | 277 | 281.6 | 288.1 | 101.65 | 104.02 | AEP_P2-1_242688 05JOSHUA 138 247670 05JOSHUA_XFL 138 1 | Single | 258/320 (WN/WE) AEP side | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W10 | 242701 | 05LEESVI | 314667 | 4ALTVSTA | 1 | 138 | 205/345 | 277 | 281.6 | 288.1 | 101.65 | 104.02 | AEP_P2-1_247670 05JOSHUA_XFL 138 247669 05JOSHUA 1EQ 999 1 | Single | 258/320 (WN/WE) AEP side | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W9 | 242701 | 05LEESVI | 314667 | 4ALTVSTA | 1 | 138 | 205/345 | 277 | 281.6 | 288.1 | 101.64 | 104.02 | AEP_P1-3_#1372_05JOSHUA 765_1 | Single | 258/320 (WN/WE) AEP side | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W12 | 242701 | 05LEESVI | 314667 | 4ALTVSTA | 1 | 138 | 205/345 | 277 | 281.7 | 288.1 | 101.68 | 104.02 | AEP_P2-1_242515 05JOSHUA 765 247669 05JOSHUA 1EQ 999 1 | Single | 258/320 (WN/WE) AEP side | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W13 | 242701 | 05LEESVI | 314667 | 4ALTVSTA | 1 | 138 | 205/345 | 277 | 281.7 | 288.1 | 101.71 | 104.01 | AEP_P1-2_#3174_6 | Single | 258/320 (WN/WE) AEP side | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
GD-W197 | 235490 | 01MORGAN | 235453 | 01CHERYR | 1 | 138 | 201 | 229 | 233.2 | 236.9 | 101.84 | 103.43 | AP-P2-3-PE-500-018D | Breaker | 250/317 (WN/WE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-W198 | 235490 | 01MORGAN | 235453 | 01CHERYR | 1 | 138 | 201 | 229 | 233.1 | 236.7 | 101.79 | 103.38 | AP-P2-3-PE-500-018C | Breaker | 250/317 (WN/WE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-W14 | 324474 | 2CLAY VILG T | 341317 | 2CLAY VILLAG | 1 | 69 | 363/320 | 47 | 48.1 | 48.4 | 102.25 | 102.92 | EXT_324253 4GHENT 138 324290 4OWEN CO TAP 138 1 | Single | 70/73 (WN/WE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion, Substation Equipment exclusion
GD-W210 | 324531 | 2FERGUSON SO | 342287 | 2SOMERSET KU | 1 | 69 | 363/320 | 141 | 138.3 | 143.8 | 98.1 | 102.01 | EKPC_P2-3_COOP S42-1014 | Breaker | N/A | No | limited by non PJM facility, EKPC rating is 172/178 for WN/WE
| NOTE: |  | The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
The final AC loading is due to contribution from Suspended, Deactivated, or Withdrawn generators and the loading on the circuit should be <100% without those generators.