## Thermal
2025 RTEP PJM N-1-1 Thermal Result (Winter)
FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | Initial AC (%) | SCD AC (%) | Contingency 1 | Contingency 2 | Conductor Rating | PJM Accepting Proposals | PJM Comments
N2-WT1 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1160.0 | 106.09 | 105.26 | 'DVP_P1-2: LN 274' | 'DVP_P1-2: LN 2172' | Conductor Rating is the same as base case model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-WT2 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1160.0 | 105.92 | 105.08 | 'DVP_P1-2: LN 274' | 'DVP_P1-2: LN 2210' | Conductor Rating is the same as base case model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-WT3 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 1 | 230/230 | 345/345 | 1160.0 | 105.93 | 102.97 | 'DVP_P1-2: LN 2210' | 'DVP_P1-2: LN 274' | Conductor Rating is the same as base case model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-WT8 | 314171 | 6BRAMBL | 313827 | 6EVERGR MILL | 2 | 230/230 | 345/345 | 1160.0 | 106.10 | 103.02 | 'DVP_P1-2: LN 2172' | 'DVP_P1-2: LN 274' | Conductor Rating is the same as base case model | Yes | Supplmental projects in the area: DOM-2019-022, DOM-2020-0003
N2-WT9 | 313870 | 3RAPPAHNCK | 314191 | 3WHIT STONE | 1 | 115/115 | 345/345 | 185.0 | 181.91 | 103.13 | 'DVP_P1-2: LN 2145' | 'DVP_P1-2: LN 224' | Conductor Rating is the same as base case model | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WT10 | 313870 | 3RAPPAHNCK | 314191 | 3WHIT STONE | 1 | 115/115 | 345/345 | 185.0 | 181.91 | 103.13 | 'DVP_P1-2: LN 224' | 'DVP_P1-2: LN 2145' | Conductor Rating is the same as base case model | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WT11 | 314174 | 3HARMONY | 313886 | 3GREYSPT | 1 | 115/115 | 345/345 | 185.0 | 180.47 | 103.11 | 'DVP_P1-2: LN 2145' | 'DVP_P1-2: LN 224' | Conductor Rating is the same as base case model | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
N2-WT12 | 314174 | 3HARMONY | 313886 | 3GREYSPT | 1 | 115/115 | 345/345 | 185.0 | 180.47 | 103.11 | 'DVP_P1-2: LN 224' | 'DVP_P1-2: LN 2145' | Conductor Rating is the same as base case model | No | Immediate Need, Refer to Northern Neck addendum document "Dominion Northern Neck Area Violations Immediate Need 20200715"
Note on L4: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 SET PRECONTRATING 1470 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1564 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END
Note on M4: CONTINGENCY 'DVP_P1-2: LN 2172' OPEN BRANCH FROM BUS 313827 TO BUS 314171 CKT 1 /* 6EVERGR MILL230.00 - 6BRAMBL 230.00 END
Note on L5: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 SET PRECONTRATING 1470 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1564 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END
Note on M5: CONTINGENCY 'DVP_P1-2: LN 2210' OPEN BRANCH FROM BUS 313827 TO BUS 314171 CKT 2 /* 6EVERGR MILL230.00 - 6BRAMBL 230.00 END
Note on L6: CONTINGENCY 'DVP_P1-2: LN 2210' OPEN BRANCH FROM BUS 313827 TO BUS 314171 CKT 2 /* 6EVERGR MILL230.00 - 6BRAMBL 230.00 END
Note on M6: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 SET PRECONTRATING 1470 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1564 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END
Note on L7: CONTINGENCY 'DVP_P1-2: LN 2172' OPEN BRANCH FROM BUS 313827 TO BUS 314171 CKT 1 /* 6EVERGR MILL230.00 - 6BRAMBL 230.00 END
Note on M7: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 SET PRECONTRATING 1470 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1564 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END
Note on L8: CONTINGENCY 'DVP_P1-2: LN 2145' OPEN BRANCH FROM BUS 313810 TO BUS 314131 CKT 1 /* 6DAHLGREN 230.00 - 6ARNOLDS 230.00 OPEN BRANCH FROM BUS 314131 TO BUS 314175 CKT 1 /* 6ARNOLDS 230.00 - 6COMORN 230.00 OPEN BRANCH FROM BUS 314132 TO BUS 314175 CKT 1 /* 6BIRCHWD 230.00 - 6COMORN 230.00 OPEN BUS 314131 /* ISLAND: 6ARNOLDS 230.00 OPEN BUS 314175 /* ISLAND: 6COMORN 230.00 END
Note on M8: CONTINGENCY 'DVP_P1-2: LN 224' OPEN BRANCH FROM BUS 314172 TO BUS 314182 CKT 1 /* 6DUNNSVL 230.00 - 6NORNECK 230.00 OPEN BRANCH FROM BUS 314172 TO BUS 314388 CKT 1 /* 6DUNNSVL 230.00 - 6LANEXA 230.00 OPEN BUS 314172 /* ISLAND: 6DUNNSVL 230.00 END
Note on L9: CONTINGENCY 'DVP_P1-2: LN 224' OPEN BRANCH FROM BUS 314172 TO BUS 314182 CKT 1 /* 6DUNNSVL 230.00 - 6NORNECK 230.00 OPEN BRANCH FROM BUS 314172 TO BUS 314388 CKT 1 /* 6DUNNSVL 230.00 - 6LANEXA 230.00 OPEN BUS 314172 /* ISLAND: 6DUNNSVL 230.00 END
Note on M9: CONTINGENCY 'DVP_P1-2: LN 2145' OPEN BRANCH FROM BUS 313810 TO BUS 314131 CKT 1 /* 6DAHLGREN 230.00 - 6ARNOLDS 230.00 OPEN BRANCH FROM BUS 314131 TO BUS 314175 CKT 1 /* 6ARNOLDS 230.00 - 6COMORN 230.00 OPEN BRANCH FROM BUS 314132 TO BUS 314175 CKT 1 /* 6BIRCHWD 230.00 - 6COMORN 230.00 OPEN BUS 314131 /* ISLAND: 6ARNOLDS 230.00 OPEN BUS 314175 /* ISLAND: 6COMORN 230.00 END
Note on L10: CONTINGENCY 'DVP_P1-2: LN 2145' OPEN BRANCH FROM BUS 313810 TO BUS 314131 CKT 1 /* 6DAHLGREN 230.00 - 6ARNOLDS 230.00 OPEN BRANCH FROM BUS 314131 TO BUS 314175 CKT 1 /* 6ARNOLDS 230.00 - 6COMORN 230.00 OPEN BRANCH FROM BUS 314132 TO BUS 314175 CKT 1 /* 6BIRCHWD 230.00 - 6COMORN 230.00 OPEN BUS 314131 /* ISLAND: 6ARNOLDS 230.00 OPEN BUS 314175 /* ISLAND: 6COMORN 230.00 END
Note on M10: CONTINGENCY 'DVP_P1-2: LN 224' OPEN BRANCH FROM BUS 314172 TO BUS 314182 CKT 1 /* 6DUNNSVL 230.00 - 6NORNECK 230.00 OPEN BRANCH FROM BUS 314172 TO BUS 314388 CKT 1 /* 6DUNNSVL 230.00 - 6LANEXA 230.00 OPEN BUS 314172 /* ISLAND: 6DUNNSVL 230.00 END
Note on L11: CONTINGENCY 'DVP_P1-2: LN 224' OPEN BRANCH FROM BUS 314172 TO BUS 314182 CKT 1 /* 6DUNNSVL 230.00 - 6NORNECK 230.00 OPEN BRANCH FROM BUS 314172 TO BUS 314388 CKT 1 /* 6DUNNSVL 230.00 - 6LANEXA 230.00 OPEN BUS 314172 /* ISLAND: 6DUNNSVL 230.00 END
Note on M11: CONTINGENCY 'DVP_P1-2: LN 2145' OPEN BRANCH FROM BUS 313810 TO BUS 314131 CKT 1 /* 6DAHLGREN 230.00 - 6ARNOLDS 230.00 OPEN BRANCH FROM BUS 314131 TO BUS 314175 CKT 1 /* 6ARNOLDS 230.00 - 6COMORN 230.00 OPEN BRANCH FROM BUS 314132 TO BUS 314175 CKT 1 /* 6BIRCHWD 230.00 - 6COMORN 230.00 OPEN BUS 314131 /* ISLAND: 6ARNOLDS 230.00 OPEN BUS 314175 /* ISLAND: 6COMORN 230.00 END

## >300MW load loss
2025 RTEP PJM N-1-1 Load Drop Results (Winter)
FG# | First Cont Name | Second Cont Name | Cont. Areas | TotalLoadLoss | PJM Accepting Proposals | PJM Comments
N2-WLD1 | DVP_P1-2: LN 2187 | DVP_P1-2: LN 2195 | 345 | 470.15 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0005
N2-WLD2 | DVP_P1-2: LN 2196 | DVP_P1-2: LN 2195 | 345 | 356.05 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0006
N2-WLD3 | DVP_P1-2: LN 2195 | DVP_P1-2: LN 2148 | 345 | 330.95 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0007
N2-WLD4 | DVP_P1-2: LN 2149 | DVP_P1-2: LN 9167 | 345 | 374.33 | Yes | Waxpool area. Supplemental projects in the area: DOM-2020-0012, DOM-2020-0021, DOM-2020-0022, DOM-2020-0024
N2-WLD5 | DVP_P1-2: LN 219 | DVP_P1-2: LN 2066 | 345 | 333.07 | Yes | Winterpock area
N2-WLD6 | DVP_P1-2: LN 2011 | DVP_P1-2: LN 2187 | 345 | 517.51 | No | Immediate Need, Refer to Manassas addendum document "Dominion Manassas Immediate Need 20200723". Includes impact of reverse power relaying at Lomar & Micron. Supplemental projects in the area: DOM-2019-023, DOM-2020-001,DOM-2020-0004, DOM-2020-0005