## Summary
2026 Window 2 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Transformer/Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusion | Comments
GD-W2-W5 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1779.6 | 1838.4 | 114.3 | 118.08 | 765-L11215_-S_SRT-A | Single | WSTE=1658 for PJM side; WN/WE = 1310/1772 for MISO side | Yes |  | There is potential interation with M-3 supplemetnal projects associated with Need IDs NEET-2021-001 and NEET-2021-002.
GD-W2-W6 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1779.6 | 1838.4 | 114.3 | 118.08 | AEP_P1-2_#695_1681_SRT-A | Single | WSTE=1658 for PJM side; WN/WE = 1310/1772 for MISO side | Yes |  | There is potential interation with M-3 supplemetnal projects associated with Need IDs NEET-2021-001 and NEET-2021-002.
GD-W2-W211 | 270716 | DRESDEN ; B | 275179 | DRESDEN ;1M | 1 | 345/138 | 222 | 480 | 549.8 | 563 | 114.54 | 117.3 | COMED_P4_012-45-BT5-6_SRT-A | Breaker | WSTE=520 | Yes
GD-W2-W214 | 275179 | DRESDEN ;1M | 271337 | DRESDEN ; R | 1 | 138 | 222 | 480 | 549.7 | 552.6 | 114.51 | 115.13 | COMED_P4_012-45-BT5-6_SRT-A | Breaker | WSTE=520 | Yes
GD-W2-51 | 270716 | DRESDEN ; B | 274702 | KENDALL ;BU | 1 | 345 | 222 | 1284 | 1509 | 1499.5 | 117.53 | 116.78 | COMED_P7-1_345-L11620_B-S_+_345-L11622_R-S_SRT-A | Tower | Correct winter ratings WN/WE/WLD = 1497/1497/1729 | No |  | Not valid with the correct ratings.
GD-W2-259 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1557 | 1593.3 | 1630.6 | 102.33 | 104.73 | AEP_P1-2_#695_1681_SRT-A | Single | WSTE=1658 | No |  | Not valid as ComEd criteria allows flow up to short-term emergency rating, but must return to normal rating post contingency, load shed not allowed.
GD-W2-258 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1557 | 1593.3 | 1630.6 | 102.33 | 104.73 | 765-L11215_-S_SRT-A | Single | WSTE=1658 | No |  | Not valid as ComEd criteria allows flow up to short-term emergency rating, but must return to normal rating post contingency, load shed not allowed.