## Light Load GenDeliv
2027 RTEP PJM Generation Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2022W1-GD-LL24 | 314747 | 6BREMO | 314744 | 3BREMO | 1 | 230/115 | 345/345 | 269.592 | 290.55 | 296.95 | 107.78 | 110.15 | 'DVP_P1-2: LN 2193_SRT-A' | single | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-LL25 | 200741 | 26SEWARD | 200766 | 26FLORENCE | 1 | 115/115 | 226/226 | 172 | 188.03 | 181.41 | 109.32 | 105.47 | 'PN_P1-2_PN-230-037_SRT-A' | single | 232SN/282SE | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
Note on K5: New Rating is used. Original rating is 286.799987793
Note on P5: CONTINGENCY 'DVP_P1-2: LN 2193_SRT-A' OPEN BRANCH FROM BUS 313707 TO BUS 313867 CKT 1 /* 6FORK UNION 230.00 - 6BREMODIST 230.00 OPEN BRANCH FROM BUS 313867 TO BUS 314747 CKT 1 /* 6BREMODIST 230.00 - 6BREMO 230.00 OPEN BUS 313867 /* ISLAND: 6BREMODIST 230.00 END
Note on P6: CONTINGENCY 'PN_P1-2_PN-230-037_SRT-A' /* HOMER CITY - SHELOCTA 230 KV LINE DISCONNECT BRANCH FROM BUS 200767 TO BUS 200795 CKT 1 /* 26HOMER CT 230 26SHELOCTA 230 END