## N-1 Thermal
PJM N-1 Thermal Result (Light Load 2027 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2022W1-N1-LLT1 | 314747 | 6BREMO | 314744 | 3BREMO | 1 | 230/115 | 345/345 | 269.592 | 107.35 | 109.72 | Single | 'DVP_P1-2: LN 2193_SRT-A' | same as basecase | NO | Delayed, pending on immediate need solution in DOM
Note on J5: New Rating is used. Original rating is 286.799987793
Note on N5: CONTINGENCY 'DVP_P1-2: LN 2193_SRT-A' OPEN BRANCH FROM BUS 313707 TO BUS 313867 CKT 1 OPEN BRANCH FROM BUS 313867 TO BUS 314747 CKT 1 OPEN BUS 313867 END

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Light Load 2027 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Comments
2022W1-N1-LLVM1 | 244329 | 05W.BELL_REA | 345 | 205 | 0.8969 | 0.9975 | 0.92 | Line_FB | AEP_P4_#1929_05WBELLA 345_M_SRT-A | YES
2022W1-N1-LLVM2 | 242948 | 05WBELLA | 345 | 205 | 0.897 | 0.9977 | 0.92 | Line_FB | AEP_P4_#1929_05WBELLA 345_M_SRT-A | YES
Note on K6: CONTINGENCY 'AEP_P4_#1929_05WBELLA 345_M_SRT-A' OPEN BRANCH FROM BUS 242937 TO BUS 242948 CKT 1 OPEN BRANCH FROM BUS 242946 TO BUS 242948 CKT 1 END
Note on K7: CONTINGENCY 'AEP_P4_#1929_05WBELLA 345_M_SRT-A' OPEN BRANCH FROM BUS 242937 TO BUS 242948 CKT 1 OPEN BRANCH FROM BUS 242946 TO BUS 242948 CKT 1 END

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Light Load 2027)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Comment
2022W1-N1-LLVD1 | 244329 | 05W.BELL_REA | 345 | 205 | 0.8875 | 0.9975 | 11 | Line_FB | AEP_P4_#1929_05WBELLA 345_M_SRT-A | YES
2022W1-N1-LLVD2 | 242948 | 05WBELLA | 345 | 205 | 0.8877 | 0.9977 | 11 | Line_FB | AEP_P4_#1929_05WBELLA 345_M_SRT-A | YES
Note on K4: CONTINGENCY 'AEP_P4_#1929_05WBELLA 345_M_SRT-A' OPEN BRANCH FROM BUS 242937 TO BUS 242948 CKT 1 OPEN BRANCH FROM BUS 242946 TO BUS 242948 CKT 1 END
Note on K5: CONTINGENCY 'AEP_P4_#1929_05WBELLA 345_M_SRT-A' OPEN BRANCH FROM BUS 242937 TO BUS 242948 CKT 1 OPEN BRANCH FROM BUS 242946 TO BUS 242948 CKT 1 END