## Summary
2027 RTEP Short Circuit Result
Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
2022W1-SC-1 | AEP | 243856 | 05JUG ST 1-6 138.kV | M | S | 40kA | 108.5 | 43399.2 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-2 | AEP | 243856 | 05JUG ST 1-6 138.kV | N | S | 40kA | 108.5 | 43399.2 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-3 | AEP | 243856 | 05JUG ST 1-6 138.kV | BC | S | 40kA | 106.8 | 42724.7 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-4 | AEP | 243856 | 05JUG ST 1-6 138.kV | BF | S | 40kA | 106.8 | 42724.7 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-5 | AEP | 243526 | 05HYATT 138.kV | AD1 | S | 50kA | 105.5 | 52751 | 50000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-6 | AEP | 243856 | 05JUG ST 1-6 138.kV | BD | S | 40kA | 103.1 | 41252.7 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-7 | AEP | 243856 | 05JUG ST 1-6 138.kV | BE | S | 40kA | 103.1 | 41252.7 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-8 | OVEC | 248001 | 06DEARBN 345.kV | DB | S | 50kA | 102.3 | 51151.4 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-9 | OVEC | 248001 | 06DEARBN 345.kV | DC | S | 50kA | 102.3 | 51151.4 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-10 | AEP | 243856 | 05JUG ST 1-6 138.kV | D | S | 40kA | 101.4 | 40575.5 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-11 | AEP | 243856 | 05JUG ST 1-6 138.kV | H | S | 40kA | 101.4 | 40575.5 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-12 | AEP | 243856 | 05JUG ST 1-6 138.kV | J | S | 40kA | 101.4 | 40579.3 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-13 | AEP | 243856 | 05JUG ST 1-6 138.kV | L | S | 40kA | 101.4 | 40579.3 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-14 | AEP | 243275 | 05DELAWR 138.kV | T | S | 16kA | 100.4 | 16063.6 | 16000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-SC-15 | APS | 235707 | WYLIE RG 345.kV | WK-1 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-16 | APS | 235707 | WYLIE RG 345.kV | WK-2 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-17 | APS | 235707 | WYLIE RG 345.kV | WK-3 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-18 | APS | 235707 | WYLIE RG 345.kV | WK-4 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-19 | APS | 235707 | WYLIE RG 345.kV | WK-5 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-20 | APS | 235707 | WYLIE RG 345.kV | WK-6 | S | 50kA | 103.6 | 51794.9 | 50000 | NO | Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-21 | ComEd | 0 | KINCAI021N03 345.kV | 21 1-3 B3 | S | 40kA | 101.5 | 40594.9 | 40000 | NO | Immediate Need Exclusion | Violation found in 2024 case, part of s2350 will solve this
2022W1-SC-22 | ComEd | 0 | KINCAI021N03 345.kV | 21 3-5 B3 | S | 40kA | 101.5 | 40594.9 | 40000 | NO | Immediate Need Exclusion | Violation found in 2024 case, part of s2350 will solve this
2022W1-SC-23 | AEP | 243526 | 05HYATT 138.kV | AB1 | S | 50kA | 100.2 | 50083.6 | 50000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case (B3337 will fix this in 2025 summer)
2022W1-SC-24 | AEP | 243856 | 05JUG ST 1-6 138.kV | BG | S | 40kA | 101.4 | 40384.1 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-25 | AEP | 243856 | 05JUG ST 1-6 138.kV | BH | S | 40kA | 101.4 | 40384.1 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-26 | AEP | 243856 | 05JUG ST 1-6 138.kV | BJ | S | 40kA | 101.4 | 40384.1 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.
2022W1-SC-27 | AEP | 243856 | 05JUG ST 1-6 138.kV | BK | S | 40kA | 101.4 | 40384.1 | 40000 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Immediate Need Exclusion | Violation found in 2024 case also.