## Summer GenDeliv
2027 RTEP PJM Generation Deliverability Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2022W1-GD-S601 | 235161 | 01CHARLR | 235169 | 01DRYRUN | 1 | 138 | 201 | 314 | 329.6 | 332.5 | 104.97 | 105.89 | AP_P2-3_WP-138-363_SRT-A | Breaker | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S943 | 235161 | 01CHARLR | 235169 | 01DRYRUN | 1 | 138 | 201 | 314 | 329.4 | 332.2 | 104.91 | 105.78 | AP_P2-2_WP-138-013_SRT-A | Bus | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S565 | 235453 | 01CHERYR | 235517 | 01HARMNY | 1 | 138 | 201 | 229 | 249.8 | 253.8 | 109.08 | 110.83 | AP_P2-3_WP-138-268_SRT-A | Breaker | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S940 | 235453 | 01CHERYR | 235517 | 01HARMNY | 1 | 138 | 201 | 229 | 243.7 | 248.2 | 106.44 | 108.39 | AP_P2-2_WP-138-073_SRT-A | Bus | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S633 | 235169 | 01DRYRUN | 235124 | 01MITCHL | 1 | 138 | 201 | 314 | 317.4 | 320.6 | 101.08 | 102.1 | AP_P2-3_WP-138-363_SRT-A | Breaker | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S949 | 235169 | 01DRYRUN | 235124 | 01MITCHL | 1 | 138 | 201 | 314 | 317.2 | 320.2 | 101.02 | 101.98 | AP_P2-2_WP-138-013_SRT-A | Bus | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S608 | 235334 | 01GLENFL | 235306 | 01BRIDGP | 1 | 138 | 201 | 209 | 221.2 | 219.8 | 105.86 | 105.18 | AP_P2-3_MP-138-024_SRT-A | Breaker | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S945 | 235334 | 01GLENFL | 235306 | 01BRIDGP | 1 | 138 | 201 | 209 | 219.6 | 218.1 | 105.06 | 104.35 | AP_P2-2_MP-138-013_SRT-A | Bus | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S615 | 235334 | 01GLENFL | 235306 | 01BRIDGP | 1 | 138 | 201 | 209 | 219.6 | 218.1 | 105.06 | 104.34 | AP_P2-3_MP-138-022_SRT-A | Breaker | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S616 | 235334 | 01GLENFL | 235306 | 01BRIDGP | 1 | 138 | 201 | 209 | 219.5 | 218 | 105 | 104.29 | AP_P2-3_MP-138-023_SRT-A | Breaker | 221SN/268SE | NO | Substation Equipment Exclusion
2022W1-GD-S651 | 235187 | 01GRANDP | 235180 | 01FAYETT | 1 | 138 | 201 | 209 | 207 | 210.2 | 99.04 | 100.55 | AP_P2-3_WP-138-390_SRT-A | Breaker | 196SN/258SE | NO |  | Due to suspended generator (AF1-209, AF2-101 and AF2-151 )
2022W1-GD-S553 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 206 | 233.6 | 231 | 113.39 | 112.12 | AP_P2-3_PE-500-018D_SRT-SL | Breaker | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-S554 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 206 | 233.5 | 230.9 | 113.37 | 112.07 | AP_P2-3_PE-500-018C_SRT-SL | Breaker | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-S558 | 235484 | 01MESSCK | 235490 | 01MORGAN | 1 | 138 | 201 | 268 | 298.5 | 298.4 | 111.38 | 111.34 | AP_P2-3_PE-500-018D_SRT-SL | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S559 | 235484 | 01MESSCK | 235490 | 01MORGAN | 1 | 138 | 201 | 268 | 298.4 | 298.1 | 111.34 | 111.24 | AP_P2-3_PE-500-018C_SRT-SL | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S28 | 235246 | 01SHANOR | 235205 | 01KRENDL | 1 | 138 | 201 | 422 | 456.6 | 446.6 | 108.2 | 105.83 | AP_P1-2_WP-500-302T_SRT-A | Single | 370SN/452SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Substation equipment exclusion | B3322 (Deactivation driven baseline) will resolve the issue. This baseline is currently on hold.
2022W1-GD-S1029 | 235277 | 01YUKON | 235270 | 01WESTRV | 1 | 138 | 201 | 314 | 326.1 | 325.5 | 103.85 | 103.65 | AP_P7-1_WPP-138-114_SRT-A | Tower | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S1033 | 235277 | 01YUKON | 235161 | 01CHARLR | 1 | 138 | 201 | 314 | 322.6 | 321.6 | 102.74 | 102.44 | AP_P7-1_WPP-138-114_SRT-A | Tower | 308SN/376SE | NO | Substation Equipment Exclusion
2022W1-GD-S1025 | 238590 | 02BRWELL | 238728 | 02FORD | 1 | 138 | 202 | 230 | 239.1 | 243.4 | 103.95 | 105.83 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 189SN/230SE | NO |  | Due to suspended generator (AB1-107)
2022W1-GD-S1010 | 238768 | 02GRNFLD | 238974 | 02N DEPT | 1 | 138 | 202 | 242 | 242.2 | 246.4 | 100.08 | 101.82 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 200SN/242SE | NO |  | Due to suspended generator (AB1-107)
2022W1-GD-S1030 | 239290 | 02HAYES | 238549 | 02AVERY | 1 | 138 | 202 | 282 | 288.2 | 292.3 | 102.2 | 103.65 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 233SN/288SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S1023 | 238874 | 02LAKVEW | 238768 | 02GRNFLD | 1 | 138 | 202 | 385 | 406.2 | 411 | 105.51 | 106.75 | ATSI_P7-1_TE-345-027A_SRT-A | Tower | 320SN/385SE | NO |  | Due to suspended generator (AB1-107)
2022W1-GD-S617 | 238913 | 02LRCRQ2 | 239046 | 02PN Q-2 | 1 | 138 | 202 | 115 | 118.6 | 119.8 | 103.11 | 104.14 | ATSI_P2-4_CEI-138-102L_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | S2649 will solve this violation
2022W1-GD-S1022 | 238974 | 02N DEPT | 238590 | 02BRWELL | 1 | 138 | 202 | 230 | 241.6 | 245.9 | 105.04 | 106.9 | ATSI_P7-1_TE-345-030_SRT-A | Tower | 189SN/230SE | NO |  | Due to suspended generator (AB1-107)
2022W1-GD-S1041 | 238974 | 02N DEPT | 238590 | 02BRWELL | 1 | 138 | 202 | 230 | 227.2 | 231.1 | 98.79 | 100.47 | ATSI_P7-1_TE-345-031_SRT-A | Tower | 189SN/230SE | NO |  | Due to suspended generator (AB1-107)
2022W1-GD-S619 | 239046 | 02PN Q-2 | 238957 | 02MFLDQ2 | 1 | 138 | 202 | 115 | 118.6 | 119.5 | 103.11 | 103.95 | ATSI_P2-4_CEI-138-102L_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | S2649 will solve this violation
2022W1-GD-S586 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 194.6 | 192.4 | 109.33 | 108.07 | AEP_P4_#14920_05TANNER 345_T_SRT-A | Breaker | (AEP portion) 167SN/245SE; (DEOK Portion) 178SN/178SE | YES
2022W1-GD-S1020 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 194.6 | 192.4 | 109.33 | 108.07 | DEOK_P7_4504MFTANNERS4512EBTANNERS_SRT-A | Tower | (AEP portion) 167SN/245SE; (DEOK Portion) 178SN/178SE | YES
2022W1-GD-S632 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | Z1 | 345 | 205/206 | 2255 | 2333.1 | 2316.5 | 103.46 | 102.73 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker | 2354SN/3211SE | YES
2022W1-GD-S1032 | 243026 | 05KAMMER13 | 243012 | 05G WASHGTON | 1 | 138 | 205 | 621 | 643.2 | 637.4 | 103.57 | 102.64 | AEP_P7-1_#11151___SRT-A | Tower | 446SN/620SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | In M-3: AEP-2021-OH013
2022W1-GD-S539 | 246327 | 05NOTTINGH78 | 246325 | 05NOTTINGH56 | Z6 | 138 | 205 | 747 | 873.4 | 860.5 | 116.92 | 115.2 | AEP_P4_#10001_05NOTTINGH78 138_P7_SRT-A | Breaker | - | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion | Branch is a station tie within the fence.
2022W1-GD-S579 | 246327 | 05NOTTINGH78 | 246325 | 05NOTTINGH56 | Z6 | 138 | 205 | 747 | 830.1 | 815 | 111.13 | 109.1 | AEP_P4_#8862_05NOTTINGH78 138_N7_SRT-A | Breaker | - | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion | Branch is a station tie within the fence.
2022W1-GD-S653 | 243347 | 05TIDD 3-4 | 235363 | 01MAHNSL | 1 | 138 | 201/205 | 205 | 205.9 | 205.9 | 100.45 | 100.42 | AEP_P4_#4743_05TIDD 345_CC_SRT-A | Breaker | (AEP portion)205SN/284SE, (APS portion) 308SN/376SE | YES
2022W1-GD-S1042 | 243347 | 05TIDD 3-4 | 235363 | 01MAHNSL | 1 | 138 | 201/205 | 205 | 205.9 | 205.9 | 100.45 | 100.42 | AEP_P7-1_#10848___SRT-A | Tower | (AEP portion)205SN/284SE, (APS portion) 308SN/376SE | YES
2022W1-GD-S657 | 248001 | 06DEARB1 | 248013 | 06PIERCE | 1 | 345 | 206 | 971 | 972.6 | 971.3 | 100.16 | 100.03 | AEP_P4_#14920_05TANNER 345_T_SRT-A | Breaker | - | NO |  | Pending on the further queue studies and PJM is pending on soliciting a baseline solution for the overload at this point.
2022W1-GD-S1044 | 248001 | 06DEARB1 | 248013 | 06PIERCE | 1 | 345 | 206 | 971 | 972.6 | 971.3 | 100.16 | 100.03 | DEOK_P7_4504MFTANNERS4512EBTANNERS_SRT-A | Tower | - | NO |  | Pending on the further queue studies and PJM is pending on soliciting a baseline solution for the overload at this point.
2022W1-GD-S607 | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 1075 | 1131.2 | 1131.5 | 105.22 | 105.25 | AEP_P4_#2978_05DUMONT 765_B_SRT-A | Breaker | - | NO for this window |  | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-S535 | 200741 | 26SEWARD | 200766 | 26FLORENCE | 1 | 115 | 226 | 172 | 202.6 | 199.7 | 117.76 | 116.12 | PN_P2-3_PN-230-0252-A_SRT-A | Breaker | 232SN/282SE | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S537 | 200741 | 26SEWARD | 200766 | 26FLORENCE | 1 | 115 | 226 | 172 | 202.7 | 199.7 | 117.83 | 116.12 | PN_P2-3_PN-230-0252-B_SRT-A | Breaker | 232SN/282SE | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S536 | 200741 | 26SEWARD | 200766 | 26FLORENCE | 1 | 115 | 226 | 172 | 202.6 | 199.7 | 117.77 | 116.12 | PN_P2-3_PN-230-0252-C_SRT-A | Breaker | 232SN/282SE | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S527 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 196.3 | 193.4 | 122.7 | 120.85 | PN_P2-3_PN-230-0347-16-DRT-029_SRT-SL | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | First Energy EOL candidate
2022W1-GD-S534 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 191.6 | 188 | 119.73 | 117.48 | PL_10_P24_100548_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | First Energy EOL candidate
2022W1-GD-S570 | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 223 | 247.2 | 245.8 | 110.87 | 110.24 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | Same as basecase | YES
2022W1-GD-S10 | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 223 | 246 | 244.4 | 110.32 | 109.58 | PJM_500_BG_P1_5011_SRT-A | Single | Same as basecase | YES
2022W1-GD-S578 | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 208 | 227.2 | 227 | 109.22 | 109.14 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | 184SN/223SE | YES
2022W1-GD-S14 | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 208 | 226 | 225.5 | 108.63 | 108.42 | PJM_500_BG_P1_5011_SRT-A | Single | 184SN/223SE | YES
2022W1-GD-S29 | 200016 | 3 MILE I | 204514 | 27TMI | 1 | 500/230 | 227 | 1070 | 1115.6 | 1124.2 | 104.27 | 105.07 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | Same as basecase | YES |  | Overlap with ME-2022-002 proposed rating 972SN/1100SE MVA. The proposed rating is not enough to mitigate the reliability violation
2022W1-GD-S634 | 200016 | 3 MILE I | 204514 | 27TMI | 1 | 500/230 | 227 | 1070 | 1082.6 | 1089.9 | 101.18 | 101.86 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | Same as basecase | YES |  | Overlap with ME-2022-002 proposed rating 972SN/1100SE MVA. The proposed rating will mitigate the reliability violation
2022W1-GD-S1006 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 280.7 | 273.7 | 171.15 | 166.89 | DVP_P7-1: LN 2058-2181_SRT-A | Tower | - | NO |  | Limited by external Facility
2022W1-GD-S592 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 178.8 | 175.7 | 109.04 | 107.14 | DVP_P4-2: 2058T2167_SRT-A | Breaker | - | NO |  | Limited by external Facility
2022W1-GD-S588 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 354 | 380 | 381.6 | 107.33 | 107.79 | DVP_P4-2: 207T2097_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S1028 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 354 | 360.7 | 367.1 | 101.9 | 103.7 | DVP_P7-1: LN 250-258_SRT-A | Tower | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S622 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 354 | 360.7 | 367.1 | 101.9 | 103.7 | DVP_P4-2: 250T258_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S35 | 313904 | 6GOOSECRK | 314006 | 6ASHBURA | 1 | 230 | 345 | 1478.6 | 1495.8 | 1517.7 | 101.16 | 102.64 | DVP_P1-2: LN 274_SRT-S | Single | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S20 | 237053 | AA2-161 POI | 235277 | 01YUKON | 2 | 138 | 201 | 365 | 397.2 | 393.8 | 108.81 | 107.9 | AP_P1-2_WP-138-AA2-161_1_SRT-A | Single | 297SN/365SE | NO |  | Will be addressed by rescope of B3710
2022W1-GD-S21 | 237053 | AA2-161 POI | 235277 | 01YUKON | 1 | 138 | 201 | 365 | 396.8 | 393.6 | 108.7 | 107.84 | AP_P1-2_WP-138-AA2-161_2_SRT-A | Single | 297SN/365SE | NO |  | Will be addressed by rescope of B3710
2022W1-GD-S523 | 316306 | AC2-079 TAP | 314532 | 3OAKRI23 | 1 | 115 | 345 | 136 | 164.6 | 165.3 | 121.06 | 121.55 | DVP_P4-2: 1552_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S526 | 316306 | AC2-079 TAP | 314532 | 3OAKRI23 | 1 | 115 | 345 | 136 | 164.6 | 165.3 | 121.06 | 121.54 | DVP_P4-5: L552_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S525 | 316306 | AC2-079 TAP | 314532 | 3OAKRI23 | 1 | 115 | 345 | 136 | 164.6 | 165.3 | 121.06 | 121.54 | DVP_P4-5: POE L652_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S524 | 316306 | AC2-079 TAP | 314532 | 3OAKRI23 | 1 | 115 | 345 | 136 | 164.6 | 165.3 | 121.06 | 121.54 | DVP_P4-2: 12152_SRT-A | Breaker | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-GD-S927 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 266.7 | 265.1 | 166.68 | 165.69 | PL_10_P22_100582_SRT-A | Bus | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S928 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 263.1 | 260.6 | 164.46 | 162.9 | PN_P2-2_PN-230-006AT_SRT-A | Bus | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S505 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 223.3 | 223.9 | 139.55 | 139.91 | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S504 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 223.3 | 223.9 | 139.55 | 139.91 | AP-P5-5-PE-138-01BEDNGT_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S506 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 221.3 | 220.5 | 138.33 | 137.8 | PJM_500_BG_P4_5_CNSTN_C_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S4 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 131 | 152 | 152.5 | 116 | 116.4 | Base Case | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S5 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 185.2 | 184.3 | 115.73 | 115.16 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S9 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 174.6 | 175.3 | 109.12 | 109.59 | PJM_500_BG_P1_5011_SRT-A | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S11 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 176.9 | 175.2 | 110.56 | 109.48 | AP_P1-2_WP-500-006_SRT-A | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S12 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 176.9 | 175.2 | 110.56 | 109.48 | AP_P1-2_PE-500-004_SRT-SL | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S13 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 175.9 | 175 | 109.96 | 109.37 | AP_P1-2_PE-500-001_SRT-SL | Single | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-GD-S38 | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 852 | 855.8 | 863.7 | 100.45 | 101.38 | PJM_500_BG_P1_5011_SRT-A | Single | 741SN/ 852SE | YES
2022W1-GD-S36 | 213519 | CONOWG01 | 231006 | COLOR_PE | 1 | 230 | 230/235 | 536 | 554.8 | 545.8 | 103.51 | 101.82 | PECO_P1-2_220-03_SRT-A/* $ CHESCO $ PECO_P1-2_220-03 $ L | Single | Same as basecase | YES
2022W1-GD-S589 | 276670 | GARDEN PR; R | 270883 | SILVER LK; R | 1 | 345 | 222 | 1479 | 1605.7 | 1593.5 | 108.56 | 107.75 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | - | NO |  | The withdrawn queue project U3-021/AB2-096 (GARDEN PR) will lower the Final AC %LD to ~92%.
2022W1-GD-S590 | 276670 | GARDEN PR; R | 270883 | SILVER LK; R | 1 | 345 | 222 | 1479 | 1601.4 | 1593.2 | 108.27 | 107.72 | COMED_P4_144-45-BT6-7___SRT-A | Breaker | - | NO |  | The withdrawn queue project U3-021/AB2-096 (GARDEN PR) will lower the Final AC %LD to ~92%.
2022W1-GD-S595 | 208009 | LACK | 200074 | LACK | 3 | 230/500 | 229 | 1167 | 1235.7 | 1245.9 | 105.88 | 106.76 | PL_02_P42_001057_SRT-A | Breaker | Same as basecase | YES
2022W1-GD-S34 | 218300 | LINDEN | 219046 | TOSCO_3 | 1 | 230 | 231 | 934 | 965.9 | 958.7 | 103.41 | 102.65 | Base Case | Single | Same as basecase | NO |  | Due to suspended generator (Z1-116)
2022W1-GD-S1039 | 218300 | LINDEN | 219046 | TOSCO_3 | 1 | 230 | 231 | 1080 | 1105.4 | 1089.9 | 102.35 | 100.91 | PS_P7-1_H2286+W2249_LT_SRT-A | Tower | Same as basecase | NO |  | Due to suspended generator (Z1-116)
2022W1-GD-S626 | 232131 | N_CHURCH | 232128 | PINEY138 | 1 | 138 | 235 | 226 | 238.8 | 233.6 | 105.64 | 103.35 | DPL_P4-2_DP55_SRT-A | Breaker | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-S1043 | 208069 | PPL-BGE TIE | 220964 | GRACETON | 1 | 230 | 229/232 | 598 | 603.8 | 600.1 | 100.98 | 100.35 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | Same as basecase | YES |  | Limited on BGE side
2022W1-GD-S1031 | 218343 | TOSCO_2 | 218441 | VFT_2 | 1 | 230 | 231 | 1081 | 1128.3 | 1112.7 | 104.37 | 102.93 | PS_P7-1_H2286+W2249_LT_SRT-A | Tower | Same as basecase | NO |  | Due to suspended generator (Z1-116)
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
The flowgate is addressed in a different window
The flowgate will be addressed by changing scope of an existing baseline
The flowgate is addressed by exsiting baseline project(s)
The flowgate is pending on the further queue studies and PJM is pending on soliciting a baseline solution for the overload at this point.
The flowgate is not a violation anymore due to withdrawn queue project(s).
The flowgate is caused by suspended queue project(s).