## N-1-1 Thermal Summer
PJM N-1-1 Thermal Result (2027 Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | Initial AC (%) | SCD AC (%) | Contingency 1 | Contingency 2 | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons For Exclusions | Comments
2022W1-N2-ST1 | 235159 | 01CARB J | 235174 | 01ELKO | 1 | 138 | 201 | 160 | 114.96 | 114.38 | AP_P1-2_WP-230-001_SRT-A | AP_P1-3_WP-138-038_SRT-A | 160SN/192SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion and Substation Equpiment Exclusion
2022W1-N2-ST2 | 253988 | 15CARSON | 253993 | 15OAKLND | 1 | 138 | 215 | 242 | 106.14 | 104.03 | DLC_P12_Z-48_SRT-A | DLC_P13_ARSENAL-138_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST3 | 253988 | 15CARSON | 253993 | 15OAKLND | 1 | 138 | 215 | 242 | 106.13 | 103.91 | DLC_P13_ARSENAL-138_SRT-A | DLC_P12_Z-48_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST4 | 253964 | 15COLLIE | 253980 | 15ELWYN | 1 | 138 | 215 | 220 | 111.22 | 109.12 | DLC_P12_Z-162_SRT-A | AP_P1-2_WP-138-334T_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST5 | 253964 | 15COLLIE | 253980 | 15ELWYN | 1 | 138 | 215 | 220 | 111.22 | 109.12 | AP_P1-2_WP-138-334T_SRT-A | DLC_P12_Z-162_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST6 | 253964 | 15COLLIE | 253980 | 15ELWYN | 2 | 138 | 215 | 220 | 110.16 | 108.68 | DLC_P12_Z-62_SRT-A | AP_P1-2_WP-138-334T_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST7 | 253964 | 15COLLIE | 253980 | 15ELWYN | 2 | 138 | 215 | 220 | 110.16 | 108.08 | AP_P1-2_WP-138-334T_SRT-A | DLC_P12_Z-62_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST8 | 253993 | 15OAKLND | 254065 | 15FORBES | 1 | 138 | 215 | 250 | 106.47 | 103.89 | DLC_P12_Z-47_SRT-A | DLC_P13_ARSENAL-138_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST9 | 253993 | 15OAKLND | 254065 | 15FORBES | 1 | 138 | 215 | 250 | 106.47 | 103.82 | DLC_P13_ARSENAL-138_SRT-A | DLC_P12_Z-47_SRT-A | - | NO |  | Cheswick decativation solution will solve this violation
2022W1-N2-ST10 | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 126 | 110.69 | 106.34 | ME_P1-2_ME-115-006_SRT-A | ME_P1-2_ME-115-064_SRT-A | - | NO |  | Addressed by B3715
2022W1-N2-ST11 | 200504 | 26CARLISLE | 200520 | 26ROXBURY | 1 | 115 | 226 | 126 | 110.69 | 106.34 | ME_P1-2_ME-115-064_SRT-A | ME_P1-2_ME-115-006_SRT-A | - | NO |  | Addressed by B3715
2022W1-N2-ST12 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 109.74 | 112.92 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST13 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 107.1 | 109.84 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2209_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST14 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 112.72 | 108.33 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 274_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST15 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 105.52 | 108.1 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2213_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST16 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 103.19 | 105.53 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2095_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST17 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 109.64 | 102.06 | DVP_P1-2: LN 2209_SRT-A | DVP_P1-2: LN 274_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST18 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 107.92 | 100.26 | DVP_P1-2: LN 2213_SRT-A | DVP_P1-2: LN 274_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST19 | 314004 | 6ASHBURN | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 110.07 | 106.95 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST20 | 314004 | 6ASHBURN | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 110.06 | 105.32 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 227_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST21 | 314004 | 6ASHBURN | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 107.01 | 103.3 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2209_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST22 | 314004 | 6ASHBURN | 314010 | 6BEAMEAD | 1 | 230 | 345 | 1573 | 105.3 | 101.31 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2213_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST23 | 314004 | 6ASHBURN | 314072 | 6PL VIEW | 1 | 230 | 345 | 1573 | 111.54 | 108.36 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST24 | 314004 | 6ASHBURN | 314072 | 6PL VIEW | 1 | 230 | 345 | 1573 | 111.53 | 106.71 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 227_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST25 | 314004 | 6ASHBURN | 314072 | 6PL VIEW | 1 | 230 | 345 | 1573 | 108.55 | 104.79 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2209_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST26 | 314004 | 6ASHBURN | 314072 | 6PL VIEW | 1 | 230 | 345 | 1573 | 106.85 | 102.82 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2213_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST27 | 314004 | 6ASHBURN | 314072 | 6PL VIEW | 1 | 230 | 345 | 1573 | 107.09 | 101.03 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2098_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST28 | 314009 | 6BRADOCK | 314054 | 6KEENE M | 1 | 230 | 345 | 629 | 103.77 | 100.84 | DVP_P1-2: LN 2097_SRT-A | DVP_P1-2: LN 281_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST29 | 314054 | 6KEENE M | 314068 | 6OX | 1 | 230 | 345 | 605 | 107.2 | 102.82 | DVP_P1-2: LN 2097_SRT-A | DVP_P1-2: LN 281_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST30 | 314054 | 6KEENE M | 314068 | 6OX | 1 | 230 | 345 | 605 | 107.2 | 102.81 | DVP_P1-2: LN 281_SRT-A | DVP_P1-2: LN 2097_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST31 | 314054 | 6KEENE M | 314068 | 6OX | 1 | 230 | 345 | 605 | 108.53 | 102.75 | DVP_P1-2: LN 2097_SRT-A | DVP_P1-2: LN 2022_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST32 | 314054 | 6KEENE M | 314068 | 6OX | 1 | 230 | 345 | 605 | 108.53 | 102.06 | DVP_P1-2: LN 2022_SRT-A | DVP_P1-2: LN 2097_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST33 | 314054 | 6KEENE M | 314068 | 6OX | 1 | 230 | 345 | 605 | 102.35 | 100.71 | DVP_P1-2: LN 248_SRT-A | DVP_P1-2: LN 2097_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST34 | 314119 | 6NOKESVL | 314130 | 6BRISTER | 1 | 230 | 345 | 1047 | 122.25 | 107.7 | DVP_P1-2: LN 539_SRT-A | DVP_P1-2: LN 569_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST35 | 314119 | 6NOKESVL | 314130 | 6BRISTER | 1 | 230 | 345 | 1047 | 122.26 | 101.83 | DVP_P1-2: LN 569_SRT-S | DVP_P1-2: LN 539_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST36 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 107.13 | 106.27 | DVP_P1-2: LN 2008_SRT-A | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST37 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 102.16 | 104.82 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST38 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 106.17 | 104.31 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 2172_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST39 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 107.13 | 104.16 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 2008_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST40 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 99.82 | 103.87 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 227_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST41 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 103.64 | 103.08 | DVP_P1-2: LN 227_SRT-A | DVP_P1-2: LN 274_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST42 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 104.7 | 102.59 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 274_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST43 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 106.17 | 102.47 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 227_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST44 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 102.54 | 101.45 | DVP_P1-2: LN 2008_SRT-A | DVP_P1-2: LN 2209_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST45 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 102.54 | 100.41 | DVP_P1-2: LN 2209_SRT-A | DVP_P1-2: LN 2008_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST46 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 97.96 | 100.22 | DVP_P1-2: LN 274_SRT-S | DVP_P1-2: LN 2209_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST47 | 313864 | 6POLAND RD | 314171 | 6BRAMBL | 1 | 230 | 345 | 1047 | 101.73 | 100.43 | DVP_P1-2: LN 2209_SRT-A | DVP_P1-2: LN 227_SRT-A | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST48 | 313712 | 6VINTHIL TP | 314119 | 6NOKESVL | 1 | 230 | 345 | 1047 | 120.96 | 106.43 | DVP_P1-2: LN 539_SRT-A | DVP_P1-2: LN 569_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST49 | 313712 | 6VINTHIL TP | 314125 | 6VINTHIL | 1 | 230 | 345 | 1047 | 120.71 | 106.16 | DVP_P1-2: LN 539_SRT-A | DVP_P1-2: LN 569_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST50 | 314913 | 8LOUDOUN | 314061 | 6LOUDOUN | 1 | 500/230 | 345 | 893.1 | 114.37 | 100.05 | DVP_P1-2: LN 502_SRT-S | DVP_P1-2: LN 584_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-ST51 | 314913 | 8LOUDOUN | 314061 | 6LOUDOUN | 1 | 500/230 | 345 | 893.1 | 114.37 | 100.05 | DVP_P1-2: LN 584_SRT-S | DVP_P1-2: LN 502_SRT-S | same as basecase | NO | Delayed, pending on immediate need solution in DOM
Note:
The flowgate is addressed by exsiting baseline project(s).
The flowgate will be addressed by generation deacitivation studies.

## Summer N-1-1 Volt Drop
PJM N-1-1 Voltage Drop Results (2027 Summer)
FG # | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Reasons For Exclusions | Comment
2022W1-N2-SVD1 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-026_SRT-SL | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0099 | 5.01 | YES
2022W1-N2-SVD2 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-511T_SRT-SL | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0055 | 5.453 | YES
2022W1-N2-SVD3 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-511T_SRT-SL | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0055 | 5.453 | YES
2022W1-N2-SVD4 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-003_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0099 | 5.01 | YES
2022W1-N2-SVD5 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-400T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0092 | 5.08 | YES
2022W1-N2-SVD6 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 0.9917 | 6.825 | YES
2022W1-N2-SVD7 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 0.9918 | 6.825 | YES
2022W1-N2-SVD8 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 0.9963 | 6.367 | YES
2022W1-N2-SVD9 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 0.9963 | 6.367 | YES
2022W1-N2-SVD10 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-403T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0055 | 5.453 | YES
2022W1-N2-SVD11 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-403T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0055 | 5.453 | YES
2022W1-N2-SVD12 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-404T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0038 | 5.618 | YES
2022W1-N2-SVD13 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-003_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0087 | 5.13 | YES
2022W1-N2-SVD14 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-003_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0087 | 5.13 | YES
2022W1-N2-SVD15 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-005B_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0072 | 5.28 | YES
2022W1-N2-SVD16 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-005B_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0072 | 5.28 | YES
2022W1-N2-SVD17 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-304T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.007 | 5.3 | YES
2022W1-N2-SVD18 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT19_SRT-SL | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0072 | 5.28 | YES
2022W1-N2-SVD19 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT19_SRT-SL | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0072 | 5.28 | YES
2022W1-N2-SVD20 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT5_SRT-SL | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0087 | 5.13 | YES
2022W1-N2-SVD21 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT5_SRT-SL | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0087 | 5.13 | YES
2022W1-N2-SVD22 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-4_PE-500-006A_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0098 | 5.021 | YES
2022W1-N2-SVD23 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-4_PE-500-006A_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0098 | 5.021 | YES
2022W1-N2-SVD24 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 535_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0038 | 5.618 | YES
2022W1-N2-SVD25 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 541_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0075 | 5.247 | YES
2022W1-N2-SVD26 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 553_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0072 | 5.28 | YES
2022W1-N2-SVD27 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 568_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0096 | 5.038 | YES
2022W1-N2-SVD28 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 569_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0094 | 5.057 | YES
2022W1-N2-SVD29 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 574_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.01 | 5.002 | YES
2022W1-N2-SVD30 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 583_SRT-S | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 0.9917 | 6.825 | YES
2022W1-N2-SVD31 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 583_SRT-S | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 0.9918 | 6.825 | YES
2022W1-N2-SVD32 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-4: 6BELMONT_6X4-039GAS_1_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0054 | 5.46 | YES
2022W1-N2-SVD33 | 235103 | 01BLACKO | 500 | 201 | 5 | ME_P1-2_ME-500-004T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0072 | 5.282 | YES
2022W1-N2-SVD34 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0064 | 5.356 | YES
2022W1-N2-SVD35 | 235103 | 01BLACKO | 500 | 201 | 5 | PEPCO_X4-035_TAP_X035_GSU_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0093 | 5.071 | YES
2022W1-N2-SVD36 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_5011_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0042 | 5.585 | YES
2022W1-N2-SVD37 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_5011_SRT-A | AP_P1-3_WP-500-DRT16_SRT-SL | 1.06 | 1.0041 | 5.585 | YES
2022W1-N2-SVD38 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG1_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0084 | 5.165 | YES
2022W1-N2-SVD39 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG2_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0084 | 5.162 | YES
2022W1-N2-SVD40 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-006T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0087 | 5.13 | YES
2022W1-N2-SVD41 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-010T_SRT-A | AP_P1-3_PE-500-024_SRT-SL | 1.06 | 1.0067 | 5.332 | YES

## Summer N-1-1 Load Drop
N-1-1 Analysis Load Drop Summary (Summer 2027 Case)
FG # | First Cont Name | Second Cont Name | TotalLoadLoss | PJM Accepting Proposals | Reasons For Exclusions | Comment
2022W1-N2-SLD1 | DVP_P1-2: LN 2062_SRT-A | DVP_P1-2: LN 2150_SRT-A | 316.67 | NO | Delayed, pending on immediate need solution in DOM | Overlap with DOM-2021-0032 . Dominion Immediate Need
2022W1-N2-SLD2 | DVP_P1-2: LN 2150_SRT-A | DVP_P1-2: LN 2062_SRT-A | 316.67 | NO | Delayed, pending on immediate need solution in DOM | Overlap with DOM-2021-0032. Dominion Immediate Need
2022W1-N2-SLD3 | DVP_P1-2: LN 2095_SRT-A | DVP_P1-2: LN 2172_SRT-A | 316.55 | NO | Delayed, pending on immediate need solution in DOM | Dominion Immediate Need
2022W1-N2-SLD4 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 2095_SRT-A | 316.55 | NO | Delayed, pending on immediate need solution in DOM | Dominion Immediate Need
2022-N2-SLD1 & 2022-N2-SLD2
| Bus# | Bus Name | LoadMW
| 314083 | 6STERL A | 120.1
| 314015 | 6HERNPK | 77.9
| 314026 | 6DRANESV | 118.7
| 314361 | 6DRANE_1 | 0
316.7
2022-N2-SLD3 & 2022-N2-SLD4
| Bus# | Bus Name | LoadMW
| 313730 | 6CABIN_RUN | 111.3
| 313863 | 6YARDLEY | 76.5
| 313827 | 6EVERGR MILL | 128.8
316.6