## N-1 Thermal
PJM N-1 Thermal Result (Summer 2027 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2022W1-N1-ST1 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.5 | 101.93 | Line_FB | 'BG_P21:FROM:200004 CNASTONE 500 200064 PCHBTM1S 500 1_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST2 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.5 | 101.91 | Line_FB | 'BG_P21:TO:200004 CNASTONE 500 200064 PCHBTM1S 500 1_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST3 | 235523 | 01BETHEL+ | 235507 | 01RIVERT | 1 | 138/138 | 201/201 | 153 | 127.5163 | 132.42 | Line_FB | 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' | 160SN/192SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-ST4 | 235523 | 01BETHEL+ | 235507 | 01RIVERT | 1 | 138/138 | 201/201 | 153 | 127.5163 | 132.42 | Line_FB | 'AP-P5-5-PE-138-01MDWBRK_SRT-A' | 160SN/192SE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-ST5 | 235174 | 01ELKO | 235237 | 01RIDGWY | 1 | 138/138 | 201/201 | 133 | 102.7068 | 117.46 | Line_FB | 'AP-P5-5-WP-138-01CARB_SRT-A' | 149SN/179SE | NO | Substation Equipment Exclusion and Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-ST6 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 106.5 | 106.74 | Line_FB | 'AP-P5-5-PE-138-01BEDNGT_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST7 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 106.5 | 106.74 | Line_FB | 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST8 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.5 | 102.03 | Line_FB | 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST9 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.5 | 101.93 | Line_FB | 'PECO_P4_PEACH235_SRT-A/* $ CHESCO $ PECO_P4_PEACH235 $ STBK' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST10 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.5 | 101.93 | Single | 'PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST11 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 102.75 | 101.69 | Line_FB | 'AP-P5-5-PE-138-01BLACKO_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST12 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 101.0625 | 100.01 | Single | 'AP_P1-2_WP-500-006_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST13 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115/115 | 226/226 | 160 | 101.0625 | 100.01 | Single | 'AP_P1-2_PE-500-004_SRT-SL' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST14 | 237062 | AD1-083 TAP | 235523 | 01BETHEL+ | 1 | 138/138 | 201/201 | 192 | 102.4479 | 105.52 | Line_FB | 'AP-P5-5-PE-138-01MDWBRK_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-ST15 | 237062 | AD1-083 TAP | 235523 | 01BETHEL+ | 1 | 138/138 | 201/201 | 192 | 102.4479 | 105.52 | Line_FB | 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-ST16 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230/230 | 345/345 | 354 | 104.0678 | 104.54 | Line_FB | 'DVP_P4-2: 207T2097_SRT-A' | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N1-ST17 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230/230 | 345/345 | 354 | 98.3051 | 100.12 | Tower | 'DVP_P7-1: LN 250-258_SRT-A' | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N1-ST18 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230/230 | 345/345 | 354 | 98.3051 | 100.12 | Line_FB | 'DVP_P4-2: 250T258_SRT-A' | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N1-ST19 | 200520 | 26ROXBURY | 203971 | AE1-071-POI | 1 | 115/115 | 226/226 | 131 | 103.9695 | 104.47 | Single | 'BASE CASE' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | overlap with First Energy EOL candidate
2022W1-N1-ST20 | 314171 | 6BRAMBL | 313864 | 6POLAND RD | 1 | 230/230 | 345/345 | 1047 | 99.7326 | 103.87 | Tower | 'DVP_P7-1: LN 227-274_SRT-S' | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
2022W1-N1-ST21 | 238913 | 02LRCRQ2 | 239046 | 02PN Q-2 | 1 | 138/138 | 202/202 | 115 | 100.2609 | 101.27 | Line_FB | 'ATSI_P2-4_CEI-138-102L_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | S2649 will solve this violation
2022W1-N1-ST22 | 239046 | 02PN Q-2 | 238957 | 02MFLDQ2 | 1 | 138/138 | 202/202 | 115 | 100.2609 | 101.08 | Line_FB | 'ATSI_P2-4_CEI-138-102L_SRT-A' | Same as basecase | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | S2649 will solve this violation
2022W1-N1-ST23 | 313904 | 6GOOSECRK | 314006 | 6ASHBURA | 1 | 230/230 | 345/345 | 1478.62 | 98.4567 | 100.0106 | Single | 'DVP_P1-2: LN 274_SRT-S' | Same as basecase | NO | Delayed, pending on immediate need solution in DOM
Note on N5: CONTINGENCY 'BG_P21:FROM:200004 CNASTONE 500 200064 PCHBTM1S 500 1_SRT-A' OPENFROM BRANCH FROM BUS 200004 TO BUS 200064 CKT 1 END
Note on N6: CONTINGENCY 'BG_P21:TO:200004 CNASTONE 500 200064 PCHBTM1S 500 1_SRT-A' OPENTO BRANCH FROM BUS 200004 TO BUS 200064 CKT 1 END
Note on N7: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on N8: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on N9: CONTINGENCY 'AP-P5-5-WP-138-01CARB_SRT-A' DISCONNECT BRANCH FROM BUS 235158 TO BUS 235175 CKT 1 DISCONNECT BRANCH FROM BUS 235158 TO BUS 236776 CKT 82 DISCONNECT BRANCH FROM BUS 235158 TO BUS 235157 CKT 1 DISCONNECT BUS 235158 DISCONNECT BRANCH FROM BUS 235229 TO BUS 235286 CKT 1 DISCONNECT BRANCH FROM BUS 235229 TO BUS 236763 CKT 2 DISCONNECT BRANCH FROM BUS 235286 TO BUS 235159 CKT 1 DISCONNECT BRANCH FROM BUS 235159 TO BUS 235174 CKT 1 DISCONNECT BRANCH FROM BUS 235159 TO BUS 235157 CKT 1 DISCONNECT BRANCH FROM BUS 235157 TO BUS 236776 CKT 71 DISCONNECT BUS 235286 DISCONNECT BUS 235157 END
Note on N10: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on N11: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on N12: CONTINGENCY 'PJM_500_BG_P4_5_CNSTN_C_SRT-A' OPEN BRANCH FROM BUS 200004 TO BUS 200064 CKT 1 OPEN BRANCH FROM BUS 200004 TO BUS 200100 CKT ZC END
Note on N13: CONTINGENCY 'PECO_P4_PEACH235_SRT-A/* $ CHESCO $ PECO_P4_PEACH235 $ STBK' TRIP BRANCH FROM BUS 200065 TO BUS 200066 CKT 1 TRIP BRANCH FROM BUS 200064 TO BUS 200065 CKT Z1 TRIP BRANCH FROM BUS 200013 TO BUS 200066 CKT Z1 TRIP BRANCH FROM BUS 200064 TO BUS 200004 CKT 1 END/* $ CHESCO $ PECO_P4_PEACH235 $ STBK
Note on N14: CONTINGENCY 'PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L' TRIP BRANCH FROM BUS 200064 TO BUS 200004 CKT 1 END/* $ CHESCO $ PECO_P1-2_5012 $ L
Note on N15: CONTINGENCY 'AP-P5-5-PE-138-01BLACKO_SRT-A' DISCONNECT BRANCH FROM BUS 235446 TO BUS 235479 CKT 1 DISCONNECT BRANCH FROM BUS 235446 TO BUS 235558 CKT 1 DISCONNECT BRANCH FROM BUS 235446 TO BUS 237506 CKT 1 DISCONNECT BRANCH FROM BUS 235446 TO BUS 235103 CKT 3 REDUCE BUS 235446 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235108 TO BUS 235103 CKT 1 DISCONNECT BUS 235130 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 END
Note on N16: CONTINGENCY 'AP_P1-2_WP-500-006_SRT-A' DISCONNECT BRANCH FROM BUS 235108 TO BUS 235103 CKT 1 END
Note on N17: CONTINGENCY 'AP_P1-2_PE-500-004_SRT-SL' DISCONNECT BRANCH FROM BUS 235108 TO BUS 235103 CKT 1 SET PRECONTRATING 2707 BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 SET POSTCONTRATING 2771 BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 END
Note on N18: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on N19: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on N20: CONTINGENCY 'DVP_P4-2: 207T2097_SRT-A' OPEN BRANCH FROM BUS 314009 TO BUS 314052 CKT 1 OPEN BRANCH FROM BUS 314039 TO BUS 314052 CKT 1 OPEN BRANCH FROM BUS 314039 TO BUS 314068 CKT 1 OPEN BUS 314039 END
Note on N21: CONTINGENCY 'DVP_P7-1: LN 250-258_SRT-A' OPEN BRANCH FROM BUS 314003 TO BUS 314041 CKT 1 OPEN BRANCH FROM BUS 314003 TO BUS 314041 CKT 2 END
Note on N22: CONTINGENCY 'DVP_P4-2: 250T258_SRT-A' OPEN BRANCH FROM BUS 314003 TO BUS 314041 CKT 1 OPEN BRANCH FROM BUS 314003 TO BUS 314041 CKT 2 END
Note on N24: CONTINGENCY 'DVP_P7-1: LN 227-274_SRT-S' OPEN BRANCH FROM BUS 313904 TO BUS 314006 CKT 1 OPEN BRANCH FROM BUS 314006 TO BUS 314010 CKT 1 OPEN BUS 314006 OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 OPEN BUS 314004 OPEN BUS 314354 OPEN BUS 314359 SET PRECONTRATING 1174 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1302 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END
Note on N25: CONTINGENCY 'ATSI_P2-4_CEI-138-102L_SRT-A' DISCONNECT BRANCH FROM BUS 241924 TO BUS 238950 CKT 1 DISCONNECT BRANCH FROM BUS 238950 TO BUS 238879 CKT 1 DISCONNECT BRANCH FROM BUS 238879 TO BUS 238935 CKT 1 DISCONNECT BRANCH FROM BUS 238935 TO BUS 238930 CKT 3 DISCONNECT BRANCH FROM BUS 239283 TO BUS 238879 CKT 1 DISCONNECT BRANCH FROM BUS 239283 TO BUS 238877 CKT 1 DISCONNECT BRANCH FROM BUS 238868 TO BUS 238877 CKT 1 DISCONNECT BRANCH FROM BUS 238868 TO BUS 238870 CKT 1 CLOSE LINE FROM BUS 238950 TO BUS 238951 CKT ZB CLOSE LINE FROM BUS 238876 TO BUS 238877 CKT ZB CLOSE LINE FROM BUS 238867 TO BUS 238868 CKT ZB CLOSE LINE FROM BUS 238869 TO BUS 238870 CKT ZB DISCONNECT BUS 238682 DISCONNECT BUS 241924 DISCONNECT BUS 238685 END
Note on N26: CONTINGENCY 'ATSI_P2-4_CEI-138-102L_SRT-A' DISCONNECT BRANCH FROM BUS 241924 TO BUS 238950 CKT 1 DISCONNECT BRANCH FROM BUS 238950 TO BUS 238879 CKT 1 DISCONNECT BRANCH FROM BUS 238879 TO BUS 238935 CKT 1 DISCONNECT BRANCH FROM BUS 238935 TO BUS 238930 CKT 3 DISCONNECT BRANCH FROM BUS 239283 TO BUS 238879 CKT 1 DISCONNECT BRANCH FROM BUS 239283 TO BUS 238877 CKT 1 DISCONNECT BRANCH FROM BUS 238868 TO BUS 238877 CKT 1 DISCONNECT BRANCH FROM BUS 238868 TO BUS 238870 CKT 1 CLOSE LINE FROM BUS 238950 TO BUS 238951 CKT ZB CLOSE LINE FROM BUS 238876 TO BUS 238877 CKT ZB CLOSE LINE FROM BUS 238867 TO BUS 238868 CKT ZB CLOSE LINE FROM BUS 238869 TO BUS 238870 CKT ZB DISCONNECT BUS 238682 DISCONNECT BUS 241924 DISCONNECT BUS 238685 END
Note on J27: New Rating is used. Original rating is 1573.0
Note on N27: CONTINGENCY 'DVP_P1-2: LN 274_SRT-S' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 OPEN BUS 314004 OPEN BUS 314354 OPEN BUS 314359 SET PRECONTRATING 1174 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE A OF LN 203 IS DE-RATED! SET POSTCONTRATING 1302 BRANCH FROM BUS 314072 TO BUS 314290 CKT 1/* RATE B OF LN 203 IS DE-RATED! END

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2027 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
2022W1-N1-SVM1 | 237062 | AD1-083 TAP | 138 | 201 | 0.9136 | 1.0094 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM2 | 237062 | AD1-083 TAP | 138 | 201 | 0.9136 | 1.0094 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM3 | 235540 | 01KEARNY | 138 | 201 | 0.895 | 0.9886 | 0.92 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM4 | 235540 | 01KEARNY | 138 | 201 | 0.895 | 0.9886 | 0.92 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM5 | 235523 | 01BETHEL+ | 138 | 201 | 0.8257 | 1.0069 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM6 | 235523 | 01BETHEL+ | 138 | 201 | 0.8257 | 1.0069 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM7 | 235507 | 01RIVERT | 138 | 201 | 0.8149 | 1.0067 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM8 | 235507 | 01RIVERT | 138 | 201 | 0.8149 | 1.0067 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM9 | 235500 | 01PAGE | 138 | 201 | 0.9165 | 1.008 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM10 | 235500 | 01PAGE | 138 | 201 | 0.9165 | 1.008 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM11 | 235499 | 01OPEQUN | 138 | 201 | 0.8892 | 0.9914 | 0.92 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM12 | 235499 | 01OPEQUN | 138 | 201 | 0.8892 | 0.9914 | 0.92 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM13 | 235498 | 01OCHAPL | 138 | 201 | 0.8596 | 1.0012 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM14 | 235498 | 01OCHAPL | 138 | 201 | 0.8596 | 1.0012 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM15 | 235457 | 01DTG | 138 | 201 | 0.8092 | 1.0048 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVM16 | 235457 | 01DTG | 138 | 201 | 0.8092 | 1.0048 | 0.92 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Note on K6: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K7: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K8: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on K9: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on K10: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K11: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K12: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K13: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K14: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K15: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K16: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on K17: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on K18: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K19: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K20: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on K21: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Summer 2027)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
2022W1-N1-SVD1 | 237320 | 01VANVL | 138 | 201 | 0.8572 | 0.9884 | 13.12 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD2 | 237320 | 01VANVL | 138 | 201 | 0.8572 | 0.9884 | 13.12 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD3 | 237062 | AD1-083 TAP | 138 | 201 | 0.888 | 1.0094 | 12.14 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD4 | 237062 | AD1-083 TAP | 138 | 201 | 0.888 | 1.0094 | 12.14 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD5 | 235540 | 01KEARNY | 138 | 201 | 0.8466 | 0.9886 | 14.2 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD6 | 235540 | 01KEARNY | 138 | 201 | 0.8466 | 0.9886 | 14.2 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD7 | 235523 | 01BETHEL+ | 138 | 201 | 0.8058 | 1.0069 | 20.11 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD8 | 235523 | 01BETHEL+ | 138 | 201 | 0.8058 | 1.0069 | 20.11 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD9 | 235507 | 01RIVERT | 138 | 201 | 0.7959 | 1.0067 | 21.08 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD10 | 235507 | 01RIVERT | 138 | 201 | 0.7959 | 1.0067 | 21.08 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD11 | 235500 | 01PAGE | 138 | 201 | 0.8899 | 1.008 | 11.81 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD12 | 235500 | 01PAGE | 138 | 201 | 0.8899 | 1.008 | 11.81 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD13 | 235499 | 01OPEQUN | 138 | 201 | 0.8377 | 0.9914 | 15.37 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD14 | 235499 | 01OPEQUN | 138 | 201 | 0.8377 | 0.9914 | 15.37 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD15 | 235498 | 01OCHAPL | 138 | 201 | 0.8437 | 1.0012 | 15.75 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD16 | 235498 | 01OCHAPL | 138 | 201 | 0.8437 | 1.0012 | 15.75 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD17 | 235477 | 01INWOOD | 138 | 201 | 0.881 | 0.9919 | 11.09 | Line_FB | AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD18 | 235477 | 01INWOOD | 138 | 201 | 0.881 | 0.9919 | 11.09 | Line_FB | AP-P5-5-PE-138-01BEDNGT_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD19 | 235457 | 01DTG | 138 | 201 | 0.792 | 1.0048 | 21.28 | Line_FB | AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N1-SVD20 | 235457 | 01DTG | 138 | 201 | 0.792 | 1.0048 | 21.28 | Line_FB | AP-P5-5-PE-138-01MDWBRK_SRT-A | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Note on L3: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L4: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L5: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L6: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L7: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L8: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L9: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L10: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L11: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L12: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L13: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L14: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L15: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L16: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L17: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L18: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L19: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_CAP_SRT-A' REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L20: CONTINGENCY 'AP-P5-5-PE-138-01BEDNGT_SRT-A' DISCONNECT BRANCH FROM BUS 235123 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235453 TO BUS 235517 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235499 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235508 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235546 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235561 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 1 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 2 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 3 DISCONNECT BRANCH FROM BUS 235445 TO BUS 235101 CKT 4 REDUCE BUS 235445 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 1 DISCONNECT BRANCH FROM BUS 235123 TO BUS 235445 CKT 2 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235103 CKT 1 DISCONNECT BRANCH FROM BUS 235101 TO BUS 235105 CKT 1 END
Note on L21: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_CAP_SRT-A' REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END
Note on L22: CONTINGENCY 'AP-P5-5-PE-138-01MDWBRK_SRT-A' DISCONNECT BRANCH FROM BUS 235483 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235504 TO BUS 235593 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235507 TO BUS 235548 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235519 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 1 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 2 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 3 DISCONNECT BRANCH FROM BUS 235483 TO BUS 235110 CKT 4 REDUCE BUS 235483 SHUNT BY 100 PERCENT DISCONNECT BRANCH FROM BUS 235444 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 1 DISCONNECT BRANCH FROM BUS 235457 TO BUS 235483 CKT 2 END