## Winter GenDeliv
2027 RTEP PJM Generation Deliverability Result (Winter)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2022W1-GD-W9 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1913.6 | 1980.7 | 122.9 | 127.21 | AEP_P1-2_#695_1681_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W10 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1913.6 | 1979.7 | 122.9 | 127.15 | 765-L11215__-S_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W362 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1761.9 | 1794 | 113.16 | 115.22 | COMED_P4_112-65-BT4-5___SRT-A | Breaker | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W363 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1761.8 | 1793.8 | 113.15 | 115.21 | COMED_P4_112-65-BT3-4___SRT-A | Breaker | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W364 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1760.9 | 1793.1 | 113.1 | 115.16 | AEP_P4_#2978_05DUMONT 765_B_SRT-A | Breaker | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W25 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1557 | 1744.7 | 1787.6 | 112.06 | 114.81 | AEP_P1-2_#695_1681_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W28 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1557 | 1744.7 | 1786.7 | 112.06 | 114.75 | 765-L11215__-S_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W29 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1310 | 1445.7 | 1492.8 | 110.36 | 113.95 | Base Case | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W32 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1646.8 | 1702.9 | 105.77 | 109.37 | COMED_P1-2_345-L17703_R-S_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W34 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1557 | 1624.7 | 1672.1 | 104.35 | 107.39 | 765-L11216__-S_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W51 | 274804 | UNIV PK N;RP | 243229 | 05OLIVE | 1 | 345 | 205/222 | 1234 | 1223.6 | 1255.3 | 99.16 | 101.73 | AEP_P1-2_#695_1681_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W52 | 274804 | UNIV PK N;RP | 243229 | 05OLIVE | 1 | 345 | 205/222 | 1234 | 1223.6 | 1254.7 | 99.16 | 101.68 | 765-L11215__-S_SRT-A | Single | - | NO for this window | Addressed in 2027 Multi-Driver Proposal Window 1
2022W1-GD-W1 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 225.3 | 225.6 | 140.83 | 140.99 | PL_10_P13_100618_SRT-A | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W2 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 222.5 | 223.1 | 139.04 | 139.41 | PN_P1-2_PN-230-103BT_SRT-A | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W3 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 219.1 | 222.4 | 136.95 | 139.01 | PL_10_P13_100618_SRT-A | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W5 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 216.3 | 219.7 | 135.16 | 137.32 | PN_P1-2_PN-230-103BT_SRT-A | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W15 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 131 | 157 | 162.5 | 119.82 | 124.05 | Base Case | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W16 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 193.8 | 197.3 | 121.15 | 123.28 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W17 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 188.9 | 193.7 | 118.08 | 121.05 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W18 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 131 | 150.7 | 156.4 | 115.05 | 119.4 | Base Case | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W21 | 237053 | AA2-161 POI | 235277 | 01YUKON | 2 | 138 | 201 | 365 | 437.4 | 434.2 | 119.82 | 118.96 | AP_P1-2_WP-138-AA2-161_1_SRT-A | Single | - | NO |  | Will be addressed by rescope of B???
2022W1-GD-W22 | 237053 | AA2-161 POI | 235277 | 01YUKON | 1 | 138 | 201 | 365 | 436.9 | 433.9 | 119.7 | 118.88 | AP_P1-2_WP-138-AA2-161_2_SRT-A | Single | - | NO |  | Will be addressed by rescope of B???
2022W1-GD-W23 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 183.2 | 188 | 114.48 | 117.51 | PJM_500_BG_P1_5011_SRT-A | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W24 | 203971 | AE1-071-POI | 200520 | 26ROXBURY | 1 | 115 | 226 | 160 | 183.8 | 187.9 | 114.88 | 117.43 | AP_P1-2_PE-500-001_SRT-W | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W360 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 229 | 265.1 | 266.5 | 115.76 | 116.39 | AP_P2-3_PE-500-018D_SRT-W | Breaker | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-W361 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 229 | 265 | 266.4 | 115.73 | 116.35 | AP_P2-3_PE-500-018C_SRT-W | Breaker | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-W26 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 177.6 | 183.6 | 110.98 | 114.76 | AP_P1-2_PE-500-001_SRT-W | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W27 | 200522 | 26SHADE GP | 203971 | AE1-071-POI | 1 | 115 | 226 | 160 | 177.6 | 183.6 | 110.98 | 114.76 | AP_P1-2_WP-500-DRT17_SRT-W | Single | 150WN/190WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion | Overlap with First Energy EOL candidate
2022W1-GD-W31 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 229 | 253.9 | 254.8 | 110.89 | 111.28 | AP_P1-2_WP-500-DRT17_SRT-W | Single | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-W30 | 235479 | 01JUNCTN | 235467 | 01FRNCHM | 1 | 138 | 201 | 229 | 253.9 | 254.8 | 110.89 | 111.28 | AP_P1-2_PE-500-001_SRT-W | Single | - | NO | Addressed by exsiting baseline project(s) | Sovled by B3701
2022W1-GD-W33 | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 238 | 258.3 | 260 | 108.51 | 109.26 | PJM_500_BG_P1_5011_SRT-A | Single | 208WN/264WE | YES
2022W1-GD-W371 | 270737 | ELWOOD ; R | 270769 | GOODINGS ;2R | 1 | 345 | 222 | 1781 | 1934.5 | 1927.3 | 108.62 | 108.22 | COMED_P4_116-45-L11613__SRT-A | Breaker | 1602WN/2325WSTE | NO | Substation Equipment Exclusion
2022W1-GD-W376 | 204538 | 27STRABAN | 204529 | 27GERMANTN | 1 | 115 | 227 | 238 | 253.9 | 255.5 | 106.68 | 107.37 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | 208WN/264WE | YES
2022W1-GD-W35 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 4039.6 | 3968.7 | 109.18 | 107.26 | ME_P1-2_ME-500-004T_SRT-A | Single | 3592WN/4290WE | NO | Substation Equipment Exclusion
2022W1-GD-W377 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 224 | 238.6 | 239.5 | 106.5 | 106.91 | AEP_P4_#14920_05TANNER 345_T_SRT-A | Breaker | (AEP portion)210WN/271WE;(DEOK portion)224WN/224WE | YES
2022W1-GD-W618 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 224 | 238.6 | 239.5 | 106.5 | 106.91 | DEOK_P7_4504MFTANNERS4512EBTANNERS_SRT-A | Tower | (AEP portion)210WN/271WE;(DEOK portion)224WN/224WE | YES
2022W1-GD-W36 | 200016 | 3 MILE I | 204514 | 27TMI | 1 | 500/230 | 227 | 1219 | 1281.6 | 1289 | 105.14 | 105.75 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | Transformer | YES |  | Overlap with ME-2021-002 proposed rating 1182WN/1364WE. The proposed rating mitigates the winter reliability violation, however doesn't address the summer violation
2022W1-GD-W37 | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 262 | 276.5 | 276.4 | 105.55 | 105.49 | PJM_500_BG_P1_5011_SRT-A | Single | 208WN/264WE | YES
2022W1-GD-W39 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 3947.7 | 3858.6 | 106.7 | 104.29 | PN_P1-2_PN-500-010T_SRT-A | Single | 3592WN/4290WE | NO | Substation Equipment Exclusion
2022W1-GD-W387 | 235484 | 01MESSCK | 235490 | 01MORGAN | 1 | 138 | 201 | 317 | 322.2 | 330.4 | 101.63 | 104.22 | AP_P2-3_PE-500-018D_SRT-W | Breaker | 250WN/317WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-W388 | 235484 | 01MESSCK | 235490 | 01MORGAN | 1 | 138 | 201 | 317 | 322 | 330.2 | 101.58 | 104.16 | AP_P2-3_PE-500-018C_SRT-W | Breaker | 250WN/317WE | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-GD-W391 | 204544 | 27LINCOLN | 204538 | 27STRABAN | 1 | 115 | 227 | 262 | 272.2 | 271.9 | 103.88 | 103.79 | PJM_500_BG_P4_5_CNSTN_J_SRT-A | Breaker | 208WN/264WE | YES
2022W1-GD-W42 | 220963 | CONASTON | 220961 | NWEST326 | 1 | 230 | 232 | 912 | 931.6 | 944.7 | 102.14 | 103.59 | PJM_500_BG_P1_5011_SRT-A | Single | Same as basecase | YES
2022W1-GD-W623 | 208069 | PPL-BGE TIE | 220964 | GRACETON | 1 | 230 | 229/232 | 652 | 668.1 | 665 | 102.47 | 102 | BG_P7_GRCTN_CNSTN_SRT-A | Tower | Same as basecase | YES |  | limited by BGE side
2022W1-GD-W53 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 3815.8 | 3753 | 103.13 | 101.43 | ME_P1-2_ME-500-003AT_SRT-A | Single | 3592WN/4290WE | NO | Substation Equipment Exclusion
2022W1-GD-W411 | 208069 | PPL-BGE TIE | 220964 | GRACETON | 1 | 230 | 229/232 | 652 | 666.4 | 659.4 | 102.21 | 101.14 | PJM_500_BG_P4_5_CNSTN_B_SRT-A | Breaker | Same as basecase | YES |  | limited by BGE side
2022W1-GD-W55 | 208069 | PPL-BGE TIE | 220964 | GRACETON | 1 | 230 | 229/232 | 652 | 664 | 656 | 101.85 | 100.61 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | Single | Same as basecase | YES |  | limited by BGE side
2022W1-GD-W57 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3464 | 3546.4 | 3483.5 | 102.38 | 100.56 | Base Case | Single | 3592WN/4290WE | NO | Substation Equipment Exclusion
2022W1-GD-W60 | 200064 | PCHBTM1S | 200004 | CNASTONE | 1 | 500 | 232/230 | 3700 | 3757.8 | 3700.8 | 101.56 | 100.02 | DVP_P1-2: LN 596_SRT-A | Single | 3592WN/4290WE | NO | Substation Equipment Exclusion
Note
The circuit is limited by Non PJM facility, and should be addressed by coordinating with the neihboring RTO/ISO
The flowgate is addressed in a different window
The flowgate will be addressed by changing scope of an existing baseline
The flowgate is addressed by exsiting baseline project(s)