## Winter N-1-1 Volt Mag
PJM N-1-1 Voltage Magnitude Results (2027 Winter)
FG # | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | PJM Accepting Proposals | Reasons For Exclusions | Comments
2022W1-N2-VM1 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-001_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.9421 | 0.9072 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM2 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-001_SRT-A | AP_P1-2_WP-138-110B_SRT-A | 0.9421 | 0.9184 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM3 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-001_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.9421 | 0.9072 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM4 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-001_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.942 | 0.9065 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM5 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-001_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.942 | 0.9065 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM6 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-018_SRT-A | AP_P1-2_PE-138-020_SRT-A | 0.963 | 0.9154 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM7 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-018_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.963 | 0.9162 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM8 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-018_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.963 | 0.9162 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM9 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-018_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.9626 | 0.917 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM10 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-018_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.9626 | 0.917 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM11 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-138-020_SRT-A | AP_P1-2_PE-138-018_SRT-A | 0.9626 | 0.9146 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM12 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-138-001_SRT-A | 0.9515 | 0.9076 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM13 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-138-018_SRT-A | 0.9472 | 0.9168 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM14 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-138-018_SRT-A | 0.9477 | 0.9178 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM15 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-138-001_SRT-A | 0.9372 | 0.9069 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM16 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-500-002T_SRT-W | 0.9372 | 0.9092 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM17 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-500-402AT_SRT-A | 0.9372 | 0.9157 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM18 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-001_SRT-W | AP_P1-2_PE-500-402BT_SRT-A | 0.9372 | 0.9169 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM19 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-002T_SRT-W | AP_P1-2_PE-500-001_SRT-W | 0.9636 | 0.909 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM20 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-002T_SRT-W | AP_P1-2_WP-500-DRT17_SRT-W | 0.9636 | 0.909 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM21 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.9615 | 0.9164 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM22 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.9615 | 0.9164 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM23 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-2_PE-500-001_SRT-W | 0.9642 | 0.9169 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM24 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-2_WP-500-DRT17_SRT-W | 0.9642 | 0.9169 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM25 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-110B_SRT-A | AP_P1-2_PE-138-001_SRT-A | 0.9734 | 0.9025 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM26 | 235217 | 01MCCONL | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-110B_SRT-A | AP_P1-2_PE-138-001_SRT-A | 0.9694 | 0.8973 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM27 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-110B_SRT-A | AP_P1-2_PE-138-001_SRT-A | 0.9672 | 0.9088 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM28 | 235267 | 01WARFOR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-138-110B_SRT-A | AP_P1-2_PE-138-001_SRT-A | 0.9684 | 0.8963 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM29 | 235453 | 01CHERYR | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-138-001_SRT-A | 0.9515 | 0.9076 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM30 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-138-018_SRT-A | 0.9472 | 0.9168 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM31 | 235592 | 01HAMPS1 | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-138-018_SRT-A | 0.9477 | 0.9178 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM32 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-138-001_SRT-A | 0.9372 | 0.9069 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM33 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-500-002T_SRT-W | 0.9372 | 0.9092 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM34 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-500-402AT_SRT-A | 0.9372 | 0.9157 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2022W1-N2-VM35 | 235490 | 01MORGAN | 138 | 201 | 0.92 | 1.05 | AP_P1-2_WP-500-DRT17_SRT-W | AP_P1-2_PE-500-402BT_SRT-A | 0.9372 | 0.9169 | NO | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## Winter N-1-1 Volt Drop
PJM N-1-1 Voltage Drop Results (2027 Winter)
FG # | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Reasons For Exclusions | Comment
2022W1-N2-VD1 | 235103 | 01BLACKO | 500 | 201 | 5 | 200038 SUSQ 2 24.0_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9979 | 6.214 | YES
2022W1-N2-VD2 | 235103 | 01BLACKO | 500 | 201 | 5 | 200038 SUSQ 2 24.0_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9979 | 6.214 | YES
2022W1-N2-VD3 | 235103 | 01BLACKO | 500 | 201 | 5 | 208918 SUSQ 1 24.0_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9979 | 6.211 | YES
2022W1-N2-VD4 | 235103 | 01BLACKO | 500 | 201 | 5 | 208918 SUSQ 1 24.0_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9979 | 6.211 | YES
2022W1-N2-VD5 | 235103 | 01BLACKO | 500 | 201 | 5 | 213742 LIMERCK1 22.0_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.997 | 6.302 | YES
2022W1-N2-VD6 | 235103 | 01BLACKO | 500 | 201 | 5 | 213742 LIMERCK1 22.0_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.997 | 6.302 | YES
2022W1-N2-VD7 | 235103 | 01BLACKO | 500 | 201 | 5 | AEP_P1-2_#311_5_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9965 | 6.354 | YES
2022W1-N2-VD8 | 235103 | 01BLACKO | 500 | 201 | 5 | AEP_P1-2_#311_5_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9965 | 6.354 | YES
2022W1-N2-VD9 | 235103 | 01BLACKO | 500 | 201 | 5 | AEP_P1-2_#312_8_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9969 | 6.31 | YES
2022W1-N2-VD10 | 235103 | 01BLACKO | 500 | 201 | 5 | AEP_P1-2_#312_8_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9969 | 6.31 | YES
2022W1-N2-VD11 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-004A_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9975 | 6.249 | YES
2022W1-N2-VD12 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-004A_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9975 | 6.249 | YES
2022W1-N2-VD13 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-026_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD14 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-026_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD15 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-026T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD16 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-026T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD17 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-027T_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD18 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-027T_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD19 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-511T_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9878 | 7.223 | YES
2022W1-N2-VD20 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_MP-500-511T_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9878 | 7.223 | YES
2022W1-N2-VD21 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-010A_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9974 | 6.258 | YES
2022W1-N2-VD22 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-010A_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9974 | 6.258 | YES
2022W1-N2-VD23 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-018_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9972 | 6.284 | YES
2022W1-N2-VD24 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-018_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9972 | 6.284 | YES
2022W1-N2-VD25 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-052_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9967 | 6.327 | YES
2022W1-N2-VD26 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-052_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9967 | 6.327 | YES
2022W1-N2-VD27 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-057_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD28 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-138-057_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD29 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-002T_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9899 | 7.014 | YES
2022W1-N2-VD30 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-002T_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9899 | 7.014 | YES
2022W1-N2-VD31 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-003_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD32 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-003_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9932 | 6.683 | YES
2022W1-N2-VD33 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-400T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.992 | 6.805 | YES
2022W1-N2-VD34 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-400T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.992 | 6.805 | YES
2022W1-N2-VD35 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-401T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD36 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-401T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD37 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9712 | 8.88 | YES
2022W1-N2-VD38 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402AT_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9712 | 8.88 | YES
2022W1-N2-VD39 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9788 | 8.123 | YES
2022W1-N2-VD40 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-402BT_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9788 | 8.121 | YES
2022W1-N2-VD41 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-403T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9878 | 7.223 | YES
2022W1-N2-VD42 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-403T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9878 | 7.223 | YES
2022W1-N2-VD43 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-404T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9862 | 7.382 | YES
2022W1-N2-VD44 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_PE-500-404T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9862 | 7.382 | YES
2022W1-N2-VD45 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-003_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9953 | 6.466 | YES
2022W1-N2-VD46 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-003_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9953 | 6.466 | YES
2022W1-N2-VD47 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-005B_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9973 | 6.268 | YES
2022W1-N2-VD48 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-005B_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9973 | 6.268 | YES
2022W1-N2-VD49 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-304T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.99 | 7 | YES
2022W1-N2-VD50 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-304T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.99 | 7 | YES
2022W1-N2-VD51 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT19_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9973 | 6.268 | YES
2022W1-N2-VD52 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT19_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9973 | 6.268 | YES
2022W1-N2-VD53 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT5_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9953 | 6.466 | YES
2022W1-N2-VD54 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-2_WP-500-DRT5_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9953 | 6.466 | YES
2022W1-N2-VD55 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-4_PE-500-006A_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9948 | 6.516 | YES
2022W1-N2-VD56 | 235103 | 01BLACKO | 500 | 201 | 5 | AP_P1-4_PE-500-006A_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9948 | 6.516 | YES
2022W1-N2-VD57 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_BRANDON1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD58 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_BRANDON1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD59 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_BRANDON2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.573 | YES
2022W1-N2-VD60 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_BRANDON2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.574 | YES
2022W1-N2-VD61 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_WAGNER3_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9977 | 6.232 | YES
2022W1-N2-VD62 | 235103 | 01BLACKO | 500 | 201 | 5 | BG_P1_WAGNER3_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9977 | 6.232 | YES
2022W1-N2-VD63 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1 1N_ANNA1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.57 | YES
2022W1-N2-VD64 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1 1N_ANNA1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.57 | YES
2022W1-N2-VD65 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1 1SURRY_1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9964 | 6.355 | YES
2022W1-N2-VD66 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1 1SURRY_1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9964 | 6.355 | YES
2022W1-N2-VD67 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1A 1X4-039_GT1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9975 | 6.253 | YES
2022W1-N2-VD68 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1A 1X4-039_GT1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9975 | 6.253 | YES
2022W1-N2-VD69 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1B 1X4-039_GT2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9975 | 6.252 | YES
2022W1-N2-VD70 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1B 1X4-039_GT2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9975 | 6.252 | YES
2022W1-N2-VD71 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1S 1WARREN_S1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.215 | YES
2022W1-N2-VD72 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1S 1WARREN_S1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.215 | YES
2022W1-N2-VD73 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1S 1X4-039_ST_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9957 | 6.426 | YES
2022W1-N2-VD74 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-1S 1X4-039_ST_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9957 | 6.426 | YES
2022W1-N2-VD75 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-2 1N_ANNA2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9944 | 6.557 | YES
2022W1-N2-VD76 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-2 1N_ANNA2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9944 | 6.557 | YES
2022W1-N2-VD77 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-2 1SURRY_2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9964 | 6.361 | YES
2022W1-N2-VD78 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-2 1SURRY_2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9964 | 6.361 | YES
2022W1-N2-VD79 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-S1 1Z1-086_ST_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.218 | YES
2022W1-N2-VD80 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-1: G-S1 1Z1-086_ST_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.217 | YES
2022W1-N2-VD81 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 509_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9948 | 6.523 | YES
2022W1-N2-VD82 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 509_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9948 | 6.523 | YES
2022W1-N2-VD83 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 534_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9946 | 6.536 | YES
2022W1-N2-VD84 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 534_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9946 | 6.536 | YES
2022W1-N2-VD85 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 535_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9862 | 7.382 | YES
2022W1-N2-VD86 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 535_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9862 | 7.382 | YES
2022W1-N2-VD87 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 539_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9953 | 6.469 | YES
2022W1-N2-VD88 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 539_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9953 | 6.469 | YES
2022W1-N2-VD89 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 541_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.989 | 7.1 | YES
2022W1-N2-VD90 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 541_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.989 | 7.1 | YES
2022W1-N2-VD91 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 553_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9864 | 7.365 | YES
2022W1-N2-VD92 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 553_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9863 | 7.366 | YES
2022W1-N2-VD93 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 558_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.995 | 6.504 | YES
2022W1-N2-VD94 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 558_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.995 | 6.505 | YES
2022W1-N2-VD95 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 563_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9979 | 6.208 | YES
2022W1-N2-VD96 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 563_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9979 | 6.209 | YES
2022W1-N2-VD97 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 568_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.571 | YES
2022W1-N2-VD98 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 568_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.571 | YES
2022W1-N2-VD99 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 569_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9945 | 6.554 | YES
2022W1-N2-VD100 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 569_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9945 | 6.554 | YES
2022W1-N2-VD101 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 574_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9961 | 6.39 | YES
2022W1-N2-VD102 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 574_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9961 | 6.39 | YES
2022W1-N2-VD103 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 592_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9929 | 6.712 | YES
2022W1-N2-VD104 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 592_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9929 | 6.712 | YES
2022W1-N2-VD105 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 596_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9936 | 6.645 | YES
2022W1-N2-VD106 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 596_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9936 | 6.645 | YES
2022W1-N2-VD107 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7130_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9971 | 6.285 | YES
2022W1-N2-VD108 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7130_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9971 | 6.285 | YES
2022W1-N2-VD109 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7135_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.216 | YES
2022W1-N2-VD110 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7135_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.216 | YES
2022W1-N2-VD111 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7154_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9979 | 6.214 | YES
2022W1-N2-VD112 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-2: LN 7154_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9979 | 6.214 | YES
2022W1-N2-VD113 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 6SURRY-GSU-1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9964 | 6.361 | YES
2022W1-N2-VD114 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 6SURRY-GSU-1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9964 | 6.361 | YES
2022W1-N2-VD115 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8NO ANNA-GSU-1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9942 | 6.584 | YES
2022W1-N2-VD116 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8NO ANNA-GSU-1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9942 | 6.584 | YES
2022W1-N2-VD117 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8NO ANNA-GSU-2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD118 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8NO ANNA-GSU-2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9943 | 6.569 | YES
2022W1-N2-VD119 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8SURRY-GSU-2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9963 | 6.367 | YES
2022W1-N2-VD120 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-3: 8SURRY-GSU-2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9963 | 6.367 | YES
2022W1-N2-VD121 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-4: 6BELMONT_6X4-039GAS_1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9854 | 7.46 | YES
2022W1-N2-VD122 | 235103 | 01BLACKO | 500 | 201 | 5 | DVP_P1-4: 6BELMONT_6X4-039GAS_1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9854 | 7.46 | YES
2022W1-N2-VD123 | 235103 | 01BLACKO | 500 | 201 | 5 | ME_P1-2_ME-500-001T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9971 | 6.294 | YES
2022W1-N2-VD124 | 235103 | 01BLACKO | 500 | 201 | 5 | ME_P1-2_ME-500-001T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9971 | 6.294 | YES
2022W1-N2-VD125 | 235103 | 01BLACKO | 500 | 201 | 5 | ME_P1-2_ME-500-004T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9909 | 6.911 | YES
2022W1-N2-VD126 | 235103 | 01BLACKO | 500 | 201 | 5 | ME_P1-2_ME-500-004T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9909 | 6.911 | YES
2022W1-N2-VD127 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD128 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_LIMER-U1_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U1 $ U | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD129 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_LIMER-U2_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U2 $ U | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.997 | 6.3 | YES
2022W1-N2-VD130 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_LIMER-U2_SRT-A/* $ MONTCO $ PECO_P1-1_LIMER-U2 $ U | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.997 | 6.3 | YES
2022W1-N2-VD131 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_PEACH-U2_SRT-A/* $ CHESCO $ PECO_P1-1_PEACH-U2 $ U | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9957 | 6.434 | YES
2022W1-N2-VD132 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_PEACH-U2_SRT-A/* $ CHESCO $ PECO_P1-1_PEACH-U2 $ U | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9957 | 6.433 | YES
2022W1-N2-VD133 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_PEACH-U3_SRT-A/* $ CHESCO $ PECO_P1-1_PEACH-U3 $ U | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9956 | 6.435 | YES
2022W1-N2-VD134 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-1_PEACH-U3_SRT-A/* $ CHESCO $ PECO_P1-1_PEACH-U3 $ U | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9956 | 6.435 | YES
2022W1-N2-VD135 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.988 | 7.204 | YES
2022W1-N2-VD136 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-2_5012_SRT-A/* $ CHESCO $ PECO_P1-2_5012 $ L | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9879 | 7.207 | YES
2022W1-N2-VD137 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-2_5034_SRT-A/* $ CHESCO $ PECO_P1-2_5034 $ L | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.244 | YES
2022W1-N2-VD138 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-2_5034_SRT-A/* $ CHESCO $ PECO_P1-2_5034 $ L | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.244 | YES
2022W1-N2-VD139 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD140 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_LIMER-GSU1_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU1 $ T | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9969 | 6.313 | YES
2022W1-N2-VD141 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_LIMER-GSU2_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU2 $ T | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9969 | 6.311 | YES
2022W1-N2-VD142 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_LIMER-GSU2_SRT-A/* $ MONTCO $ PECO_P1-3_LIMER-GSU2 $ T | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9969 | 6.311 | YES
2022W1-N2-VD143 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_PEACH-GSU2_SRT-A/* $ CHESCO $ PECO_P1-3_PEACH-GSU2 $ T | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9955 | 6.449 | YES
2022W1-N2-VD144 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_PEACH-GSU2_SRT-A/* $ CHESCO $ PECO_P1-3_PEACH-GSU2 $ T | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9955 | 6.449 | YES
2022W1-N2-VD145 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_PEACH-GSU3_SRT-A/* $ CHESCO $ PECO_P1-3_PEACH-GSU3 $ T | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9954 | 6.456 | YES
2022W1-N2-VD146 | 235103 | 01BLACKO | 500 | 201 | 5 | PECO_P1-3_PEACH-GSU3_SRT-A/* $ CHESCO $ PECO_P1-3_PEACH-GSU3 $ T | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9954 | 6.456 | YES
2022W1-N2-VD147 | 235103 | 01BLACKO | 500 | 201 | 5 | PEPCO_P1_5070_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9975 | 6.254 | YES
2022W1-N2-VD148 | 235103 | 01BLACKO | 500 | 201 | 5 | PEPCO_P1_5070_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9975 | 6.254 | YES
2022W1-N2-VD149 | 235103 | 01BLACKO | 500 | 201 | 5 | PEPCO_X4-035_TAP_X035_GSU_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.995 | 6.5 | YES
2022W1-N2-VD150 | 235103 | 01BLACKO | 500 | 201 | 5 | PEPCO_X4-035_TAP_X035_GSU_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.995 | 6.5 | YES
2022W1-N2-VD151 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_5011_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9844 | 7.56 | YES
2022W1-N2-VD152 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_5011_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9844 | 7.56 | YES
2022W1-N2-VD153 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9894 | 7.063 | YES
2022W1-N2-VD154 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9894 | 7.063 | YES
2022W1-N2-VD155 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9896 | 7.042 | YES
2022W1-N2-VD156 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM_500_BG_P1_CCLFG2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9896 | 7.042 | YES
2022W1-N2-VD157 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_HOPC_G1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9966 | 6.344 | YES
2022W1-N2-VD158 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_HOPC_G1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9966 | 6.344 | YES
2022W1-N2-VD159 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_SALM_G1_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9967 | 6.33 | YES
2022W1-N2-VD160 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_SALM_G1_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9967 | 6.33 | YES
2022W1-N2-VD161 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_SALM_G2_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9967 | 6.33 | YES
2022W1-N2-VD162 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-1_SALM_G2_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9967 | 6.33 | YES
2022W1-N2-VD163 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN1-GSA_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9966 | 6.343 | YES
2022W1-N2-VD164 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN1-GSA_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9966 | 6.343 | YES
2022W1-N2-VD165 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN2-GSA_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9966 | 6.339 | YES
2022W1-N2-VD166 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN2-GSA_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9966 | 6.339 | YES
2022W1-N2-VD167 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN2-GSA-WIN_SRT-W | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9966 | 6.339 | YES
2022W1-N2-VD168 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GEN2-GSA-WIN_SRT-W | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9966 | 6.339 | YES
2022W1-N2-VD169 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GHC-GSA-SUM_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9964 | 6.357 | YES
2022W1-N2-VD170 | 235103 | 01BLACKO | 500 | 201 | 5 | PJM500_PS_P1-2_GHC-GSA-SUM_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9964 | 6.36 | YES
2022W1-N2-VD171 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_000793_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.24 | YES
2022W1-N2-VD172 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_000793_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.241 | YES
2022W1-N2-VD173 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_001446_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.241 | YES
2022W1-N2-VD174 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_001446_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.241 | YES
2022W1-N2-VD175 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_001447_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.24 | YES
2022W1-N2-VD176 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_08_P11_001447_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.241 | YES
2022W1-N2-VD177 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_10_P11_000806_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.22 | YES
2022W1-N2-VD178 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_10_P11_000806_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.22 | YES
2022W1-N2-VD179 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_10_P12_100616_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.224 | YES
2022W1-N2-VD180 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_10_P12_100616_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.224 | YES
2022W1-N2-VD181 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_40_P11_001448_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.238 | YES
2022W1-N2-VD182 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_40_P11_001448_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.238 | YES
2022W1-N2-VD183 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_40_P11_001449_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9976 | 6.238 | YES
2022W1-N2-VD184 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_40_P11_001449_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9976 | 6.238 | YES
2022W1-N2-VD185 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_48_P11_000840_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.218 | YES
2022W1-N2-VD186 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_48_P11_000840_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.219 | YES
2022W1-N2-VD187 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_48_P12_000189_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9978 | 6.219 | YES
2022W1-N2-VD188 | 235103 | 01BLACKO | 500 | 201 | 5 | PL_48_P12_000189_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9978 | 6.219 | YES
2022W1-N2-VD189 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-005T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9949 | 6.506 | YES
2022W1-N2-VD190 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-005T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9949 | 6.507 | YES
2022W1-N2-VD191 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-006T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9924 | 6.762 | YES
2022W1-N2-VD192 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-006T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9924 | 6.762 | YES
2022W1-N2-VD193 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-007_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.995 | 6.495 | YES
2022W1-N2-VD194 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-007_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.995 | 6.495 | YES
2022W1-N2-VD195 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-010T_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9882 | 7.183 | YES
2022W1-N2-VD196 | 235103 | 01BLACKO | 500 | 201 | 5 | PN_P1-2_PN-500-010T_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9882 | 7.183 | YES
2022W1-N2-VD197 | 235103 | 01BLACKO | 500 | 201 | 5 | V3-017-ST-GEN_SRT-A | AP_P1-3_PE-500-024_SRT-W | 1.06 | 0.9974 | 6.256 | YES
2022W1-N2-VD198 | 235103 | 01BLACKO | 500 | 201 | 5 | V3-017-ST-GEN_SRT-A | AP_P1-3_WP-500-DRT16_SRT-W | 1.06 | 0.9974 | 6.256 | YES

## Winter N-1-1 Load Drop
N-1-1 Analysis Load Drop Summary (2027 Winter)
FG # | First Cont Name | Second Cont Name | TotalLoadLoss | PJM Accepting Proposals | Reasons For Exclusions | Comment
2022W1-N2-WLD1 | DVP_P1-2: LN 2062_SRT-A | DVP_P1-2: LN 2150_SRT-A | 339.97 | NO | Delayed, pending on immediate need solution in DOM | Overlap with DOM-2021-0032
2022W1-N2-WLD2 | DVP_P1-2: LN 2150_SRT-A | DVP_P1-2: LN 2062_SRT-A | 339.97 | NO | Delayed, pending on immediate need solution in DOM | Overlap with DOM-2021-0032
2022W1-N2-WLD3 | DVP_P1-2: LN 2095_SRT-A | DVP_P1-2: LN 2172_SRT-A | 308.58 | NO | Delayed, pending on immediate need solution in DOM
2022W1-N2-WLD4 | DVP_P1-2: LN 2172_SRT-A | DVP_P1-2: LN 2095_SRT-A | 308.58 | NO | Delayed, pending on immediate need solution in DOM
2022-N2-WLD1 & 2022-N2-WLD2
| Bus# | Bus Name | LoadMW
| 314083 | 6STERL A | 129.7
| 314015 | 6HERNPK | 95
| 314026 | 6DRANESV | 115.3
| 314361 | 6DRANE_1 | 0
340
2022-N2-WLD3 & 2022-N2-WLD4
| Bus# | Bus Name | LoadMW
| 313730 | 6CABIN_RUN | 114.9
| 313863 | 6YARDLEY | 56.2
| 313827 | 6EVERGR MILL | 137.5
308.6