## Light Load GenDeliv
2027 RTEP PJM Generation Deliverability Result (Light Load)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2022W2-GD-LL1 | 314747 | 6BREMO | 314744 | 3BREMO | 1 | 230/115 | 345/345 | 269.592 | 290.65 | 297.1 | 107.81 | 110.2 | 'DVP_P1-2: LN 2193_SRT-A' | single | same as basecase | YES |  | Listed as flowgate 2022W1-GD-LL24 from Window 1
Note on K5: New Rating is used. Original rating is 286.799987793
Note on P5: CONTINGENCY 'DVP_P1-2: LN 2193_SRT-A' OPEN BRANCH FROM BUS 313707 TO BUS 313867 CKT 1 /* 6FORK UNION 230.00 - 6BREMODIST 230.00 OPEN BRANCH FROM BUS 313867 TO BUS 314747 CKT 1 /* 6BREMODIST 230.00 - 6BREMO 230.00 OPEN BUS 313867 /* ISLAND: 6BREMODIST 230.00 END