## N-1 Thermal
PJM N-1 Thermal Result (Light Load 2027 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2022W2-N1-LLT1 | 314747 | 6BREMO | 314744 | 3BREMO | 1 | 230/115 | 345/345 | 269.592 | 107.38 | 109.78 | Single | 'DVP_P1-2: LN 2193_SRT-A' | same as basecase | YES |  | Listed as flowgate 2022W1-N1-LLT1 from Window 1
Note on J5: New Rating is used. Original rating is 286.799987793
Note on N5: CONTINGENCY 'DVP_P1-2: LN 2193_SRT-A' OPEN BRANCH FROM BUS 313707 TO BUS 313867 CKT 1 OPEN BRANCH FROM BUS 313867 TO BUS 314747 CKT 1 OPEN BUS 313867 END