## Thermal
2023 W2 Summer Baseline Analysis Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | PreFlow | ContFlow(MVA) | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2023W2-N1-ST1 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206 | 112.7989 | 114.43 | Single | 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST2 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206 | 112.7989 | 114.43 | Line_FB | 'AEP_P4_05VASSEL_345_H018K5_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST3 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206 | 112.7989 | 114.43 | Line_FB | 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST4 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206 | 112.7989 | 114.43 | Line_FB | 'AEP_P4_05VASSEL_345_H018K8_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST5 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.533 | 111.01 | Single | 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST6 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.533 | 111.01 | Line_FB | 'AEP_P4_05VASSEL_345_H018K8_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST7 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.533 | 111.01 | Line_FB | 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST8 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.533 | 111.01 | Line_FB | 'AEP_P4_05VASSEL_345_H018K5_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST9 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4231 | 110.62 | Single | 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST10 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4231 | 110.62 | Line_FB | 'AEP_P4_05VASSEL_345_H018K8_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST11 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4231 | 110.62 | Line_FB | 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST12 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4231 | 110.62 | Line_FB | 'AEP_P4_05VASSEL_345_H018K5_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST13 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138/138 | 205/205 | 310 | 192.1 | 335.5 | 105.9677 | 108.22 | Line_FB | 'AEP_P4_#9732_05MALIS 138_M2_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST14 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138/138 | 205/205 | 310 | 192.1 | 316.2 | 99.5161 | 101.99 | Line_FB | 'AEP_P4_#9733_05MALIS 138_M_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST15 | 243590 | 05WESTAR | 243513 | 05GENOA | 1 | 138/138 | 205/205 | 274 | 150.7 | 291.3 | 100.4745 | 106.32 | Line_FB | 'AEP_P4_#9732_05MALIS 138_M2_SRT-A' | Sag limited conductor rating: 223/274/281/317 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N1-ST16 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206.1 | 112.8368 | 114.43 | Line_FB | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST17 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206.1 | 112.8368 | 114.43 | Line_FB | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST18 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.5604 | 111.01 | Line_FB | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST19 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.5604 | 111.01 | Line_FB | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST20 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4505 | 110.62 | Line_FB | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST21 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4505 | 110.62 | Line_FB | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST22 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206.1 | 112.8368 | 114.43 | Single | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST23 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138/138 | 205/205 | 1054 | 742.6 | 1206.1 | 112.8368 | 114.43 | Single | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | - | Yes |  | This is a series reactor bypass
2023W2-N1-ST24 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.5604 | 111.01 | Single | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST25 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 752.6 | 1212.2 | 109.5604 | 111.01 | Single | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST26 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4505 | 110.62 | Single | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-ST27 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 752.6 | 1208 | 109.4505 | 110.62 | Single | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
Note on O4: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O5: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K5_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O6: CONTINGENCY 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O7: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K8_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O8: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O9: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K8_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O10: CONTINGENCY 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O11: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K5_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O12: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O13: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K8_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O14: CONTINGENCY 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O15: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K5_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on O16: CONTINGENCY 'AEP_P4_#9732_05MALIS 138_M2_SRT-A' OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 OPEN BRANCH FROM BUS 243526 TO BUS 243537 CKT 2 END
Note on O17: CONTINGENCY 'AEP_P4_#9733_05MALIS 138_M_SRT-A' OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 OPEN BRANCH FROM BUS 243526 TO BUS 243537 CKT 1 END
Note on O18: CONTINGENCY 'AEP_P4_#9732_05MALIS 138_M2_SRT-A' OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 OPEN BRANCH FROM BUS 243526 TO BUS 243537 CKT 2 END
Note on O19: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O20: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on O21: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on O22: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O23: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O24: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on O25: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O26: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on O27: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on O28: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O29: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on O30: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END