## Summary
2023 Window 2 Summer Generator Deliverability Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Cont Name | ContType | Rating | Final DC %LD | Final AC %LD | DC Final Flow | AC Final Flow | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W2-GD-S116 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1054 | 113.68 | 115.3 | 1198.2 | 1215.3 | - | Yes |  | This is a series reactor bypass
2023W2-GD-S3 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1054 | 113.68 | 115.3 | 1198.2 | 1215.3 | - | Yes |  | This is a series reactor bypass
2023W2-GD-S115 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1054 | 113.68 | 115.3 | 1198.2 | 1215.3 | - | Yes |  | This is a series reactor bypass
2023W2-GD-S114 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1054 | 113.68 | 115.3 | 1198.2 | 1215.3 | - | Yes |  | This is a series reactor bypass
2023W2-GD-S122 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1092 | 110.38 | 111.86 | 1205.4 | 1221.5 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S121 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1092 | 110.38 | 111.86 | 1205.4 | 1221.5 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S4 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1092 | 110.38 | 111.86 | 1205.4 | 1221.5 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S123 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1092 | 110.38 | 111.86 | 1205.4 | 1221.5 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S6 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1092 | 110.27 | 111.47 | 1204.2 | 1217.2 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S127 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1092 | 110.27 | 111.47 | 1204.2 | 1217.2 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S125 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1092 | 110.27 | 111.47 | 1204.2 | 1217.2 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S126 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1092 | 110.27 | 111.47 | 1204.2 | 1217.2 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-S135 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | AEP_P4_#9732_05MALIS 138_M2_SRT-A | Breaker | 310 | 106.6 | 108.86 | 330.5 | 337.5 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-GD-S141 | 243590 | 05WESTAR | 243513 | 05GENOA | 1 | 138 | 205 | AEP_P4_#9732_05MALIS 138_M2_SRT-A | Breaker | 274 | 101.18 | 107.04 | 277.2 | 293.3 | sag limited conductor rating: 223/274/281/317 (SN/SE/WN/WE), Conductor design rating:223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-GD-S142 | 242933 | 05RPMONE | 246929 | 05MADDOX | 1 | 345 | 205 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 1301 | 106.79 | 106.97 | 1389.3 | 1391.6 | 897/1301/1138/1452 (SN/SE/WN/WE) | Yes
2023W2-GD-S165 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | AEP_P4_#9733_05MALIS 138_M_SRT-A | Breaker | 310 | 100.16 | 102.62 | 310.5 | 318.1 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-GD-S170 | 242933 | 05RPMONE | 246929 | 05MADDOX | 1 | 345 | 205 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker | 1301 | 101.86 | 101.47 | 1325.2 | 1320.2 | 897/1301/1138/1452 (SN/SE/WN/WE) | Yes
2023W2-GD-S186 | 243590 | 05WESTAR | 243513 | 05GENOA | 1 | 138 | 205 | AEP_P4_#9733_05MALIS 138_M_SRT-A | Breaker | 274 | 93.89 | 100.4 | 257.3 | 275.1 | sag limited conductor rating: 223/274/281/317 (SN/SE/WN/WE), Conductor design rating:223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-GD-S108 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | AEP_P4_#8975_05KAMMER 765_MM2_SRT-A | Breaker | 2492 | 123.16 | 123.7 | 3069.2 | 3082.7 | - | No | Addressed by existing baseline B3796
2023W2-GD-S109 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | AP_P2-3_WP-500-DRT7A_SRT-SL | Breaker | 2492 | 123.15 | 123.7 | 3068.8 | 3082.5 | - | No | Addressed by existing baseline B3796
2023W2-GD-S110 | 242920 | 05BELMON | 235102 | 01BELMNT | 5 | 765/500 | 201/205 | AP_P2-3_WP-500-DRT10A_SRT-SL | Breaker | 2492 | 123.1 | 123.67 | 3067.7 | 3081.8 | - | No | Addressed by existing baseline B3796
2023W2-GD-S112 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 897 | 116.14 | 118.11 | 1041.7 | 1059.5 | - | No | Addressed by N8169.1
2023W2-GD-S113 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker | 1204 | 115.65 | 117.5 | 1392.4 | 1414.7 | - | No | Addressed by existing baseline B3788
2023W2-GD-S118 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | AEP_P4_#1558_05BAKER 765_Q_SRT-A | Breaker | 1204 | 110.36 | 112.01 | 1328.7 | 1348.6 | - | No | Addressed by existing baseline B3788
2023W2-GD-S120 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | AEP_P4_#309_05HANG R 765_B2_SRT-A | Breaker | 1204 | 110.02 | 111.89 | 1324.7 | 1347.1 | - | No | Addressed by existing baseline B3788
2023W2-GD-S124 | 248005 | 06KYGER | 242528 | 05SPORN | 1 | 345 | 205/206 | AEP_P4_#1560_05BAKER 765_Q2_SRT-A | Breaker | 1204 | 109.77 | 111.64 | 1321.7 | 1344.1 | - | No | Addressed by existing baseline B3788
2023W2-GD-S130 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | Breaker | 4571 | 109.63 | 110.07 | 5011.3 | 5031.3 | - | No | Addressed by existing baseline B3785
2023W2-GD-S131 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P4_#8980_05KAMMER 765_QQ2_SRT-A | Breaker | 4571 | 109.01 | 109.39 | 4983.1 | 5000.2 | - | No | Addressed by existing baseline B3785
2023W2-GD-S138 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker | 897 | 106.33 | 107.4 | 953.8 | 963.3 | - | No | Addressed by N8169.1
2023W2-GD-S157 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker | 897 | 102.69 | 103.73 | 921.1 | 930.4 | - | No | Addressed by N8169.1
2023W2-GD-S159 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker | 4571 | 103.2 | 103.64 | 4717.1 | 4737.5 | - | No | Addressed by existing baseline B3785
2023W2-GD-S166 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 4571 | 101.89 | 102.42 | 4657.3 | 4681.6 | - | No | Addressed by existing baseline B3785
2023W2-GD-S184 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P4_#9728_05MALIS 138_L1_SRT-A | Breaker | 4571 | 100.55 | 100.79 | 4596 | 4607.2 | - | No | Addressed by existing baseline B3785
2023W2-GD-S332 | 242516 | 05MOUNTN | 242920 | 05BELMON | 1 | 765 | 205 | AEP_P2-2_#7222_05MALIS 765_1_SRT-A | Bus | 4571 | 100.52 | 100.76 | 4594.7 | 4605.7 | - | No | Addressed by existing baseline B3785
The flowgate is addressed by exsiting baseline or network project(s)