## Thermal
2023 Window 2 Summer N-1-1 Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons For Exclusions | Comments
2023W2-N2-ST1 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-2_#5832_6228_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 158.06 | 141.81 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST2 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 155.6 | 140.49 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST3 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-2_#5832_6228_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 154.48 | 140.16 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST4 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 158.07 | 139.86 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST5 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 152.37 | 139.08 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST6 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 154.49 | 138.55 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST7 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 155.61 | 137.49 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST8 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 152.38 | 136.53 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST9 | 243513 | 05GENOA | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 144.39 | 133.12 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST10 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 310 | AEP_P1-2_#5832_6228_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 143.23 | 128.88 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST11 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 310 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 141.06 | 127.73 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST12 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 143.24 | 127.18 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST13 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Base Case | 139.16 | 125.21 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST14 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 141.07 | 125.1 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST15 | 243547 | 05MORSE | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 136.27 | 124.95 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST16 | 243513 | 05GENOA | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5800_676_SRT-A | 144.4 | 124.39 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST17 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 223 | AEP_P1-2_#5832_6228_SRT-A | Base Case | 132.6 | 119.93 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST18 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 223 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | Base Case | 129.01 | 117.74 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST19 | 243547 | 05MORSE | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5800_676_SRT-A | 136.28 | 116.09 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST20 | 243513 | 05GENOA | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5828_6225_SRT-A | 125.31 | 112.02 | Sag limited conductor rating 338/453/427/517 (SN/SE/WN/WE), Conductor design rating 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST21 | 243526 | 05HYATT | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | 126.01 | 110.52 | 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST22 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 121.55 | 110.2 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST23 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Base Case | 123.87 | 109.73 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST24 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | 121.56 | 109.57 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST25 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#7207_9700575_SRT-A | 120.32 | 109.02 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST26 | 243513 | 05GENOA | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#12192_05POLARS 138_SRT-A | 122.27 | 108.94 | Sag limited conductor rating 338/453/427/517 (SN/SE/WN/WE), Conductor design rating 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST27 | 243526 | 05HYATT | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 126 | 108.15 | 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST28 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 120.99 | 108.04 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST29 | 243513 | 05GENOA | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5861_14217_SRT-A | 120.64 | 107.3 | Sag limited conductor rating 338/453/427/517 (SN/SE/WN/WE), Conductor design rating 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST30 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | 121.01 | 107.19 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST31 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#7207_9700575_SRT-A | 119.26 | 106.33 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST32 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#739_05BEATTY 345_3_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 110.13 | 106.28 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST33 | 243458 | 05HYATT | 246752 | 05VASSEL | 1 | 345 | 205 | 1409 | AEP_P1-2_#15953_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 109.03 | 105.95 | Sag limited conductor rating: 1409/1409/1781/1781 (SN/SE/WN/WE); Conductor design Rating: 1409/1887/1781/2144 (SN/SE/WN/WE) | Yes
2023W2-N2-ST34 | 243513 | 05GENOA | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 107.64 | 105.85 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST35 | 243513 | 05GENOA | 243537 | 05MALIS | 2 | 138 | 205 | 407 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5860_14218_SRT-A | 119.14 | 105.79 | Sag limited conductor rating 338/453/427/517 (SN/SE/WN/WE), Conductor design rating 338/456/427/517 (SN/SE/WN/WE) | Yes
2023W2-N2-ST36 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 223 | AEP_P1-2_#5832_6228_SRT-A | Base Case | 118.06 | 105.42 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST37 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Base Case | 119.09 | 104.9 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST38 | 243458 | 05HYATT | 246752 | 05VASSEL | 1 | 345 | 205 | 1409 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#15953_SRT-A | 109.03 | 104.64 | Sag limited conductor rating: 1409/1409/1781/1781 (SN/SE/WN/WE); Conductor design Rating: 1409/1887/1781/2144 (SN/SE/WN/WE) | Yes
2023W2-N2-ST39 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-3_#739_05BEATTY 345_3_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 108.3 | 103.96 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST40 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-2_#15953_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 108.96 | 103.23 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST41 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 223 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | Base Case | 114.39 | 103.1 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST42 | 242939 | 05MARYSV | 243458 | 05HYATT | 1 | 345 | 205 | 1335 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | ATSI_P1-2_OES-345-935T_SRT-A | 119.37 | 102.23 | 1166/1335/1481/1591 (SN/SE/WN/WE) | Yes |  | S3006 addresses this issue
2023W2-N2-ST43 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 117.7 | 102.03 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST44 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5831_6227_SRT-A | 114 | 101.97 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST45 | 243513 | 05GENOA | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-3_#739_05BEATTY 345_3_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 105 | 100.98 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST46 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 223 | AEP_P1-2_#5832_6228_SRT-A | Base Case | 113.5 | 100.87 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST47 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#739_05BEATTY 345_3_SRT-A | 110.13 | 100.63 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST48 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 274 | AEP_P1-2_#15953_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 106.69 | 100.2 | Sag limited conductor rating 223/274/281/317 (SN/SE/WN/WE), conductor design rating 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST49 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 310 | AEP_P1-3_#739_05BEATTY 345_3_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 102.95 | 100.11 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-ST50 | 243513 | 05GENOA | 243591 | 05SPRNGR | 1 | 138 | 205 | 223 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#9655_14218_SRT-A | 116.88 | 100.02 | Sag limited conductor rating: 223/223/281/281 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes