## Thermal
2023 W2 Winter Baseline Analysis Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | PreFlow | ContFlow(MVA) | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2023W2-N1-WT1 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.533 | 110.8 | Single | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT2 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.533 | 110.8 | Single | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT3 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.4231 | 109.95 | Single | '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT4 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.4231 | 109.95 | Single | '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT5 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210.5 | 109.5513 | 110.86 | Line_FB | 'AEP_P4_#7245_05VASSEL 345_G_2_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT6 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.5055 | 110.8 | Line_FB | 'AEP_P4_05VASSEL_345_H018K8_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT7 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.5055 | 110.8 | Line_FB | 'AEP_P4_05VASSEL_345_H018K5_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT8 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.5055 | 110.8 | Line_FB | 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT9 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205/205 | 1092 | 736.7 | 1210 | 109.5055 | 110.8 | Single | 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT10 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1201.2 | 109.4414 | 110 | Line_FB | 'AEP_P4_#7245_05VASSEL 345_G_2_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT11 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.3956 | 109.95 | Line_FB | 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT12 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.3956 | 109.95 | Line_FB | 'AEP_P4_05VASSEL_345_H018K5_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT13 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.3956 | 109.95 | Line_FB | 'AEP_P4_05VASSEL_345_H018K8_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-N1-WT14 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205/205 | 1092 | 736.7 | 1200.7 | 109.3956 | 109.95 | Single | 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
Note on P6: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on P7: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P8: CONTINGENCY '246752 05VASSEL 345 247728 05VASSEL_XFL 345 Z1_SRT-A' OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P9: CONTINGENCY '246751 05VASSEL 765 247728 05VASSEL_XFL 345 1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 END
Note on P10: CONTINGENCY 'AEP_P4_#7245_05VASSEL 345_G_2_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 243456 TO BUS 246752 CKT 2 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P11: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K8_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on P12: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K5_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on P13: CONTINGENCY 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P14: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P15: CONTINGENCY 'AEP_P4_#7245_05VASSEL 345_G_2_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 243456 TO BUS 246752 CKT 2 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P16: CONTINGENCY 'AEP_P4_#7218_05VASSEL 765_D1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END
Note on P17: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K5_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on P18: CONTINGENCY 'AEP_P4_05VASSEL_345_H018K8_SRT-A' OPEN BRANCH FROM BUS 247728 TO BUS 246751 CKT 1 OPEN BRANCH FROM BUS 247728 TO BUS 246752 CKT Z1 END
Note on P19: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1_SRT-A' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 OPEN BRANCH FROM BUS 246752 TO BUS 247728 CKT Z1 END