## Summary
2023 Window 2 Winter Generator Deliverability Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Cont Name | ContType | Rating | Final DC %LD | Final AC %LD | DC Final Flow | AC Final Flow | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2023W2-GD-W12 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P1-2_#7441_100545_SRT-A | Single | 1138 | 118.96 | 119.82 | 1353.8 | 1363.6 | With N8169.1, sag limited conductor rating 897/1154/1138/1330 (SN/SE/WN/WE), Conductor design rating: 897/1300/1138/1452 (SN/SE/WN/WE) | Yes
2023W2-GD-W153 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_#7245_05VASSEL 345_G_2_SRT-A | Breaker | 1092 | 110.72 | 112.02 | 1209 | 1223.2 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W155 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1092 | 110.67 | 111.96 | 1208.5 | 1222.6 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W156 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1092 | 110.67 | 111.96 | 1208.5 | 1222.6 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W154 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1092 | 110.67 | 111.96 | 1208.5 | 1222.6 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W19 | 242926 | 05MALIS | 290237 | 05MALIS 1EQ | 1 | 765/999 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1092 | 110.67 | 111.96 | 1208.5 | 1222.6 | 990/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W162 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_#7245_05VASSEL 345_G_2_SRT-A | Breaker | 1092 | 110.61 | 111.16 | 1207.8 | 1213.8 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W25 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1092 | 110.56 | 111.11 | 1207.3 | 1213.4 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W163 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1092 | 110.56 | 111.11 | 1207.3 | 1213.4 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W164 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1092 | 110.56 | 111.11 | 1207.3 | 1213.4 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W165 | 290237 | 05MALIS 1EQ | 243538 | 05MALISX | 1 | 999/138 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1092 | 110.56 | 111.11 | 1207.3 | 1213.4 | 946/1092/1092/1092 (SN/SE/WN/WE) | Yes
2023W2-GD-W168 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 1138 | 110.57 | 110.91 | 1258.3 | 1262.1 |  |  |  | Addressed by N8169.1
2023W2-GD-W176 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker | 1138 | 107.32 | 107.28 | 1221.3 | 1220.9 |  |  |  | Addressed by N8169.1
2023W2-GD-W177 | 243211 | 05ALLEN | 242933 | 05RPMONE | 1 | 345 | 205 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker | 1138 | 106.52 | 106.72 | 1212.2 | 1214.4 |  |  |  | Addressed by N8169.1
2023W2-GD-W58 | 242933 | 05RPMONE | 246929 | 05MADDOX | 1 | 345 | 205 | AEP_P1-2_#7441_100545_SRT-A | Single | 1452 | 99.49 | 100.2 | 1444.7 | 1455 | 897/1301/1138/1452 (SN/SE/WN/WE) | Yes
2023W2-GD-W213 | 242933 | 05RPMONE | 246929 | 05MADDOX | 1 | 345 | 205 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 1452 | 99.59 | 100.18 | 1446 | 1454.6 | 897/1301/1138/1452 (SN/SE/WN/WE) | Yes
2023W2-GD-W214 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_#7245_05VASSEL 345_G_2_SRT-A | Breaker | 1218 | 98.67 | 100.16 | 1201.8 | 1219.9 | - | Yes
2023W2-GD-W217 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_05VASSEL_345_H018K5_SRT-A | Breaker | 1218 | 98.63 | 100.11 | 1201.3 | 1219.3 | - | Yes
2023W2-GD-W216 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_05VASSEL_345_H018K8_SRT-A | Breaker | 1218 | 98.63 | 100.11 | 1201.3 | 1219.3 | - | Yes
2023W2-GD-W215 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P4_#7218_05VASSEL 765_D1_SRT-A | Breaker | 1218 | 98.63 | 100.11 | 1201.3 | 1219.3 | - | Yes
2023W2-GD-W59 | 243538 | 05MALISX | 243537 | 05MALIS | ZB | 138 | 205 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | Single | 1218 | 98.63 | 100.11 | 1201.3 | 1219.3 | - | Yes
The flowgate is addressed by exsiting baseline or network project(s)