## Thermal
2023 Window 2 Winter N-1-1 Results
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons For Exclusions | Comments
2023W2-N2-WT1 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 317 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 130.5 | 112.65 | Sag limited conductor rating: 223/274/281/317 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/SE) | Yes
2023W2-N2-WT2 | 243537 | 05MALIS | 243538 | 05MALISX | ZB | 138 | 205 | 1218 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | 134.16 | 112.2 | - | Yes |  | This is a series reactor bypass
2023W2-N2-WT3 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 349 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 127.76 | 111.54 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-WT4 | 243513 | 05GENOA | 243590 | 05WESTAR | 1 | 138 | 205 | 317 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 128.68 | 111.01 | Sag limited conductor rating: 223/274/281/317 (SN/SE/WN/WE); Conductor design rating: 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-WT5 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 349 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 126.11 | 110.06 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-WT6 | 243537 | 05MALIS | 243538 | 05MALISX | ZB | 138 | 205 | 1218 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | 134.17 | 110.04 | - | Yes |  | This is a series reactor bypass
2023W2-N2-WT7 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 349 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-2_#5832_6228_SRT-A | 120.7 | 104.49 | 223/310/281/349 (SN/SE/WN/WE) | Yes
2023W2-N2-WT8 | 243553 | 05POLARS | 243590 | 05WESTAR | 1 | 138 | 205 | 349 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | 119.04 | 103.01 | 223/310/281/349 (SN/SE/WN/WE) | Yes