## Reactive Interfaces
PJM Market Efficiency Base Case - PJM Reactive Interface Limit Values - Summer/Winter MW
2024-2039
Interface | Type* | Summer/Winter Rating
BLABED Interface | Base | 2238/2361
EAST Interface | Base | 9350/9292
WEST Interface | Base | 5805/5805
BC_PEP Interface | Base | 9263/8574
CLEVELAND Interface | Base | 3992/3992
AEP-DOM Interface | Base | 4576/4000
AP SOUTH Interface | Base | 7668/8662
AP SOUTH Contingency | Contingency | 8645/9661
CENTRAL Contingency | Contingency | 5173/5173
50045005 Contingency | Contingency | 4488/4488
*See the specific transmission lines that comprise the Interfaces and Contingencies within the posted event file.

## Load DR
PJM Market Efficiency Base Case - PJM Peak Load and Energy Forecast
Load | 2025 | 2029 | 2032 | 2035 | 2039
Peak (MW) | 153493 | 165681 | 172109 | 179622 | 190752
Energy (GWh) | 829683 | 933146 | 991188 | 1041217 | 1120928
Notes: 1.) Peak and energy values from the February 2024 PJM Load Forecast Report Table B-1 and Table E-1, respectively.
2.) Model inputs are at the zonal level. To the extent zonal load shapes create different diversity, modeled PJM peak load may vary.
PJM Market Efficiency Base Case - Demand Resource Forecast
Demand Resource | 2025 | 2029 | 2032 | 2035 | 2039
Demand Resource (MW) | 7814 | 8265 | 8500 | 8772 | 9210
Note: 1.) Values from the February 2024 PJM Load Forecast Report Table B-7.

## Fuel-Emissions
PJM Market Efficiency Base Case - Fuel Prices*- ($/MMBtu)
| 2025 | 2029 | 2032 | 2035 | 2039
Coal | 2.7768 | 3.0952 | 3.3864 | 3.6531 | 3.9661
Gas | 3.4265 | 5.4513 | 6.3444 | 7.0005 | 7.4962
OIL-H | 13.1808 | 15.3066 | 16.7171 | 17.9309 | 19.7004
OIL-L | 16.6345 | 19.5433 | 21.2233 | 22.6682 | 24.7752
*Average Annual Values
PJM Market Efficiency Base Case - Emission Prices ($/Ton)
| 2025 | 2029 | 2032 | 2035 | 2039
SO2 | 2.0808 | 2.2523 | 2.3902 | 2.5365 | 2.7456
NOx Annual | 2.5625 | 2.7602 | 2.9291 | 3.1084 | 3.3647
NOx Seasonal | 1460.625 | 1754.4534 | 1465.7991 | 1568.7711 | 1721.4566
National CO2 | 0 | 0 | 0 | 0 | 0
RGGI CO2 - MD,DE,NJ | 16.3255 | 19.4579 | 22.2483 | 23.9706 | 28.7503

## Reserve Margin
PJM Market Efficiency Base Case - Reserve Margin
| 2025 | 2029 | 2032 | 2035 | 2039
Forecasted Summer Peak Net Internal Demand (MW) | 145679 | 157416 | 163609 | 170850 | 181542
Reserve Requirement (MW) - (assumed 17.8% IRM) | 171609.862 | 185436.048 | 192731.402 | 201261.3 | 213856.476
Existing + ISA Level Generation - Retirement (MW of Capacity) | 185037.8867 | 188773.0907 | 188887.4907 | 188887.4907 | 188887.4907
Non-ISA Level Generation Needed to Meet Reserve Margin (MW of Capacity) | - | - | 3843.9113 | 12373.8093 | 24968.9853
Notes: Generation includes existing and projected PJM internal capacity resources.
Unit level solar and wind resource capacity at 38% and 13% of maximum capability, respectively.
Model informed by the 2029 RTEP Powerflow and the Generation Interconnection Queue (Queue status as of 5/14/24)
Non-ISA level units include SusISAs, FSAs, SAA units with pre-FSA queue status.

## Area Summer Capability by Type
PJM Market Efficiency Base Case - 2029 Summer Capability by Generation Type (MW)
Area | Battery Storage | Combined Cycle | Conventional Hydro | CT Gas | CT Oil | CT Other | Fuel Cell | IC Gas | IC Oil | IC Renewable | Nuclear | Pumped Storage Hydro | Solar PV | ST Coal | ST Gas | ST Other | ST Renewable | Wind | Total
Allegheny Power | 81.2 | 3450.6 | 138 | 1408.6 |  |  |  | 29.5 |  | 21 |  |  | 1828.4 | 5125.7 |  |  |  | 1169.6 | 13252.6
American Electric Power | 806 | 9511.5 | 790 | 3710.6 |  |  |  |  | 7.47 | 37.56 | 2200.5 | 244 | 7923.6 | 13565.6 | 756.7 | 54.8 | 63 | 3935.7 | 43607.03
Atlantic Electric |  | 740.5 |  | 386.4 |  |  |  |  | 8 | 3 |  |  | 337.7 |  |  |  |  | 1517.5 | 2993.1
Baltimore Gas & Electric Company | 2.5 |  |  | 263.4 | 216 |  |  |  |  | 8.1 | 1707.8 |  | 31.1 |  |  |  | 52 |  | 2280.9
Commonwealth Edison Co. | 71.56 | 4725.4 |  | 7407.4 | 100 | 169.6 |  | 51 |  | 10.1 | 10531.2 |  | 374.9 | 2650 |  |  |  | 7429 | 33520.16
Dayton Power & Light Co. |  |  |  | 1413.5 |  |  |  |  | 34 |  |  |  | 963.7 | [5 empty] | 2411.2
Delmarva Power & Light Company | 43 | 2485.7 |  | 969.4 | 452.5 |  | 26.4 |  | 88.9 | 16.8 |  |  | 1383.35 |  | 698.9 | 71.3 |  | 247.8 | 6484.05
Duke Energy Ohio/Kentucky | 70.2 | 470.1 |  | 580.7 | 82 |  |  |  |  | 4.5 |  |  | 447.4 | 1620 |  | 50.5 |  |  | 3325.4
Duquesne Light Company | 5.625 | 341.7 | 38.3 |  | 18.1 |  |  | 14.4 |  |  | 1790.5 |  | 63.4 | [5 empty] | 2272.025
East Kentucky Power Coop. | 55 |  | 175.9 | 760.9 | [8 empty] | 825 | 1687 |  |  |  |  | 3503.8
FirstEnergy ATSI | 12 | 5350.8 |  | 1417.6 | 163.6 |  |  |  | 2.5 | 10.1 | 2143 |  | 811.1 | 136 | 330.3 |  |  | 69.1 | 10446.1
Jersey Central Power & Light Company | 180.8 | 1641.3 |  | 554.2 | [5 empty] | 13.7 |  | 420 | 519.87 | [5 empty] | 3329.87
Metropolitan Edison Company | 20 | 2640.3 | 19 |  | 417.4 | 3.8 |  |  |  | 11.1 |  |  | 300 | 115 |  |  | 60 |  | 3586.6
Ohio Valley Electric Corporation | [13 empty] | 2157.2 |  |  |  |  | 2157.2
PECO Energy Company |  | 4180.2 | 498 | 66 | 828 |  |  |  | 10 |  | 4822 | 1070 | 3.1 |  |  |  | 103 |  | 11580.3
Pennsylvania Electric Company | 44 | 1887.5 | 90.4 | 307 | 62 |  |  | 204.6 | 17 | 13.7 |  | 483 | 523.8 | 4174.8 | 598 |  | 78.3 | 1344.6 | 9828.7
Potomac Electric Power Company | 1 | 2560.3 |  | 412.2 | 432.4 |  |  |  |  | 4.6 |  |  | 53.8 |  | 1180.3 |  | 52 |  | 4696.6
PPL Electric Utilities | 50 | 6398.6 | 700.9 | 193.799 | 36 | 51.7 |  | 12 | 5 | 13.6 | 2505 |  | 373.2 | 354.6 | 4640.9 |  | 36.7 | 308 | 15679.999
Public Service Electric & Gas Company | 4.5 | 4951.2 | 5.5 | 1159.6 | 38.4 |  |  | 2.2 |  | 12.72 | 3463 |  | 263.2 |  |  |  | 176.8 |  | 10077.12
Virginia Power Company | 476 | 9475.4 | 603.9 | 3915.3 | 239.8 | 20.6 |  |  | 4 | 125.3 | 3585.5 | 3015 | 9962.787 | 2498.1 | 11 |  | 370.6 | 2344.9 | 36648.187
Total | 1923.385 | 60811.1 | 3059.9 | 24926.599 | 3086.2 | 245.7 | 26.4 | 313.7 | 176.87 | 305.88 | 32748.5 | 5232 | 26989.407 | 34084 | 8216.1 | 176.6 | 992.4 | 18366.2 | 221680.941
PJM Market Efficiency Base Case - 2032 Summer Capability by Generation Type (MW)
Area | Battery Storage | Combined Cycle | Conventional Hydro | CT Gas | CT Oil | CT Other | Fuel Cell | IC Gas | IC Oil | IC Renewable | Nuclear | Pumped Storage Hydro | Solar PV | ST Coal | ST Gas | ST Other | ST Renewable | Wind | Total
Allegheny Power | 81.2 | 3450.6 | 138 | 1408.6 |  |  |  | 29.5 |  | 21 |  |  | 1898.4 | 5125.7 |  |  |  | 1169.6 | 13322.6
American Electric Power | 806 | 9511.5 | 790 | 3710.6 |  |  |  |  | 7.47 | 37.56 | 2200.5 | 244 | 9326.1 | 13565.6 | 756.7 | 54.8 | 63 | 3935.7 | 45009.53
Atlantic Electric |  | 740.5 |  | 386.4 |  |  |  |  | 8 | 3 |  |  | 337.7 |  |  |  |  | 1949.5 | 3425.1
Baltimore Gas & Electric Company | 2.5 |  |  | 263.4 | 216 |  |  |  |  | 8.1 | 1707.8 |  | 31.1 |  |  |  | 52 |  | 2280.9
Commonwealth Edison Co. | 71.56 | 4725.4 |  | 7407.4 | 100 | 169.6 |  | 51 |  | 10.1 | 10531.2 |  | 374.9 | 2650 |  |  |  | 7429 | 33520.16
Dayton Power & Light Co. |  |  |  | 1413.5 |  |  |  |  | 34 |  |  |  | 1005.7 | [5 empty] | 2453.2
Delmarva Power & Light Company | 43 | 2485.7 |  | 969.4 | 452.5 |  | 26.4 |  | 88.9 | 16.8 |  |  | 1469.35 |  | 698.9 | 71.3 |  | 247.8 | 6570.05
Duke Energy Ohio/Kentucky | 70.2 | 470.1 |  | 580.7 | 82 |  |  |  |  | 4.5 |  |  | 447.4 | 1620 |  | 50.5 |  |  | 3325.4
Duquesne Light Company | 5.625 | 341.7 | 38.3 |  | 18.1 |  |  | 14.4 |  |  | 1790.5 |  | 63.4 | [5 empty] | 2272.025
East Kentucky Power Coop. | 55 |  | 175.9 | 760.9 | [8 empty] | 825 | 1687 |  |  |  |  | 3503.8
FirstEnergy ATSI | 12 | 5350.8 |  | 1417.6 | 163.6 |  |  |  | 2.5 | 10.1 | 2143 |  | 811.1 | 136 | 330.3 |  |  | 69.1 | 10446.1
Jersey Central Power & Light Company | 180.8 | 1641.3 |  | 554.2 | [5 empty] | 13.7 |  | 420 | 519.87 |  |  |  |  | 4558 | 7887.87
Metropolitan Edison Company | 20 | 2640.3 | 19 |  | 417.4 | 3.8 |  |  |  | 11.1 |  |  | 300 | 115 |  |  | 60 |  | 3586.6
Ohio Valley Electric Corporation | [13 empty] | 2157.2 |  |  |  |  | 2157.2
PECO Energy Company |  | 4180.2 | 498 | 66 | 828 |  |  |  | 10 |  | 4822 | 1070 | 3.1 |  |  |  | 103 |  | 11580.3
Pennsylvania Electric Company | 44 | 1887.5 | 90.4 | 307 | 62 |  |  | 204.6 | 17 | 13.7 |  | 483 | 523.8 | 4174.8 | 598 |  | 78.3 | 1344.6 | 9828.7
Potomac Electric Power Company | 521.9 | 2560.3 |  | 412.2 | 432.4 |  |  |  |  | 4.6 |  |  | 89.8 |  | 1180.3 |  | 52 |  | 5253.5
PPL Electric Utilities | 50 | 6398.6 | 700.9 | 193.799 | 36 | 51.7 |  | 12 | 5 | 13.6 | 2505 |  | 373.2 | 354.6 | 4640.9 |  | 36.7 | 308 | 15679.999
Public Service Electric & Gas Company | 4.5 | 4951.2 | 5.5 | 1159.6 | 38.4 |  |  | 2.2 |  | 12.72 | 3463 |  | 263.2 |  |  |  | 176.8 | 1148 | 11225.12
Virginia Power Company | 770.9 | 9475.4 | 603.9 | 3915.3 | 239.8 | 20.6 |  |  | 4 | 125.3 | 3585.5 | 3015 | 14235.787 | 2498.1 | 11 |  | 370.6 | 3224.9 | 42096.087
Total | 2739.185 | 60811.1 | 3059.9 | 24926.599 | 3086.2 | 245.7 | 26.4 | 313.7 | 176.87 | 305.88 | 32748.5 | 5232 | 32898.907 | 34084 | 8216.1 | 176.6 | 992.4 | 25384.2 | 235424.241

## FSA Level Added Though 2032
FSA Level Units Added to the Market Efficiency Base Case to Meet PJM Projected Reserve Margin Through 2032
PROMOD Unit | Unit Type | Area | Maximum Capability (MW) | Activation Date
Q_AE1-044 | Solar PV | Virginia Power Company | 200 | 2031-01-01
Q_AC2-112 | Solar PV | Virginia Power Company | 150 | 2031-01-01
Q_AD1-151 | Solar PV | Virginia Power Company | 150 | 2031-01-01
Q_AE1-153 | Solar PV | Virginia Power Company | 149 | 2031-01-01
Q_AE2-033 | Solar PV | Virginia Power Company | 149 | 2031-01-01
Waller Solar:PV1 | Solar PV | Virginia Power Company | 131 | 2031-01-01
Q_AF2-065 | Solar PV | Virginia Power Company | 150 | 2031-01-01
Q_AF1-069B | Battery Storage | Virginia Power Company | 67.7 | 2031-01-01
Q_AF1-069S | Solar PV | Virginia Power Company | 94 | 2031-01-01
Q_AG1-147 | Solar PV | Virginia Power Company | 70 | 2031-01-01
Q_AG1-533 | Solar PV | Allegheny Power | 40 | 2031-01-01
Red Brick Solar:PV1 | Solar PV | Virginia Power Company | 130 | 2031-01-01
Q_AE1-157 | Solar PV | Virginia Power Company | 120 | 2031-01-01
Q_AG1-038 | Solar PV | Virginia Power Company | 45 | 2031-01-01
Q_AF2-115 | Solar PV | Virginia Power Company | 25 | 2031-01-01
Q_AF2-091 | Solar PV | Virginia Power Company | 34 | 2031-01-01
Q_AF2-300 | Solar PV | Virginia Power Company | 20 | 2031-01-01
Q_AF2-302 | Solar PV | American Electric Power | 20 | 2031-01-01
Q_AG1-021 | Solar PV | Virginia Power Company | 20 | 2031-01-01
Q_AG1-022 | Solar PV | American Electric Power | 20 | 2031-01-01
Q_AG1-031 | Solar PV | Virginia Power Company | 20 | 2031-01-01
Carver Solar I:PV1 | Solar PV | Virginia Power Company | 91 | 2031-01-01
Blue Jay Solar VA:PV1 | Solar PV | American Electric Power | 100 | 2031-01-01
Q_AC1-191 | Solar PV | Virginia Power Company | 80 | 2031-01-01
Q_AE1-084 | Solar PV | Virginia Power Company | 83 | 2031-01-01
Q_AF1-075 | Solar PV | Virginia Power Company | 73 | 2031-01-01
Q_AE1-173 | Solar PV | Virginia Power Company | 800 | 2031-01-01
Q_AC1-143 | Solar PV | Virginia Power Company | 60 | 2032-01-01
Q_AC1-120 | Solar PV | Virginia Power Company | 60 | 2032-01-01
Q_AE1-056 | Solar PV | Virginia Power Company | 60 | 2032-01-01
Q_AF2-403 | Battery Storage | Virginia Power Company | 20 | 2032-01-01
Q_AC2-079 | Solar PV | Virginia Power Company | 85 | 2032-01-01
Concho Solar I:PV2 | Solar PV | Delmarva Power & Light Company | 86 | 2032-01-01
Q_AG1-034 | Solar PV | American Electric Power | 127.5 | 2032-01-01
Q_AF1-275 | Solar PV | American Electric Power | 50 | 2032-01-01
Q_AG1-483B | Battery Storage | Potomac Electric Power Company | 520.9 | 2032-01-01
Q_AG1-483S | Solar PV | Potomac Electric Power Company | 36 | 2032-01-01
Q_AG1-024 | Solar PV | American Electric Power | 85 | 2032-01-01
Q_AF2-084 | Solar PV | Dayton Power & Light Co. | 42 | 2032-01-01
Q_AE2-073 | Solar PV | American Electric Power | 50 | 2032-01-01
Q_AD2-067 | Solar PV | American Electric Power | 150 | 2032-01-01
Q_AG1-125 | Solar PV | American Electric Power | 400 | 2032-01-01
Q_AG1-126 | Solar PV | American Electric Power | 400 | 2032-01-01
Q_AF2-042 | Solar PV | Virginia Power Company | 500 | 2032-01-01
Q_AE2-190 | Solar PV | Virginia Power Company | 70 | 2032-01-01
Q_AE2-094B | Battery Storage | Virginia Power Company | 207.2 | 2032-01-01
Q_AE2-094S | Solar PV | Virginia Power Company | 300 | 2032-01-01
Q_AE2-313 | Solar PV | Virginia Power Company | 314 | 2032-01-01
Redbud Gaylord 345 kV:PV1 | Solar PV | Allegheny Power | 30 | 2032-01-01
Ho Fel Solar:PV1 | Solar PV | Virginia Power Company | 40 | 2032-01-01
Notes:
Unit selection determined by 1.) Locational consideration [State, datacenter growth proximity] 2.) Evaluation of commercial probability.
Unit level solar and wind resource capacity at 38% and 13% of maximum capability, respectively.
Model informed by the RTEP Powerflow and the Generation Interconnection Queue (Queue status as of 5/14/24).
FSA level units include SusISAs and FSAs.

## NJ SAA 1.0
NJ SAA Units in the Market Efficiency Base Case Through 2032
PROMOD Unit | Unit Type | Area | Maximum Capability (MW) | Activation Date
Atlantic Shores Offshore Wind Project 1:WT1 | Wind | Atlantic Electric | 300 | 2029-09-01
Atlantic Shores Offshore Wind Project 1:WT2 | Wind | Atlantic Electric | 605 | 2029-09-01
Atlantic Shores Offshore Wind Project 1:WT3 | Wind | Atlantic Electric | 605 | 2029-09-01
Ocean Wind:WS1 98 | Wind | Atlantic Electric | 432 | 2031-01-01
Q_AE1-020 | Wind | Jersey Central Power & Light Company | 816 | 2031-01-01
Q_AG2-055 | Wind | Public Service Electric & Gas Company | 1148 | 2031-01-01
LCS-Atlantic | Wind | Jersey Central Power & Light Company | 1200 | 2032-01-01
LCS-Larrabee | Wind | Jersey Central Power & Light Company | 1200 | 2032-01-01
LCS-Smithburg | Wind | Jersey Central Power & Light Company | 1342 | 2032-01-01
Notes:
Model informed by the RTEP Powerflow and the Generation Interconnection Queue (Queue status as of 5/14/24).

## Financial Parameters
Carrying Charge Rate and Discount Rate
Discount Rate | 7.11%
Levelized Annual Carrying Charge Rate | 11.94%